## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
4b9b78fc-d027-47c7-935b-f05d4d46ce4f | checklist | ITP-ME-01 Piling | itp | ITP-ME-01 Piling
f1f6dd3a-fd38-4571-83c0-a4b1d382b3b5 | section | Preconstruction
d4f48775-da58-43a9-89b0-daa65376fab6 | checkpoint | 1.1 - Permits and Approvals
68c21a25-b43b-569c-a140-06b4b145186e | note | PROCEDURE / INSTRUCTION - Ensure Permits are in place including, but not limited to:
a367affb-54b3-5459-8c79-50bfda2cb389 | note | ○ Excavation Permits
90a0e4da-8460-5ac0-a15b-51fd0f0a1eec | note | ACCEPTANCE CRITERIA - Excavation Permit
5fef6a65-4092-5c2a-95f0-131d05224fa2 | note | VERIFYING DOCUMENT - Working Party to have access and sign onto permits where required.
13cae7c5-d377-566d-8aa9-c74b660f4bd0 | note | VERIFICATION: EPC - H
1d4adc12-717e-5bfb-b5c0-6cf3a418d100 | note | VERIFICATION: CLIENT - R
60cf63fc-851d-4ca5-8d0e-71e4fe328d31 | signoff | HOLD POINT
e315cc1b-33c5-4bfe-84ee-df00d9c78409 | checkpoint | 1.2 - Identification of underground services
9c5ae628-a55e-5ce1-9741-e0999398a87f | note | PROCEDURE / INSTRUCTION - Use of DBYD and other methods to positively identify underground services.
6d9a028d-8cd8-54e9-a16f-c731a365221d | note | ACCEPTANCE CRITERIA - Engineer to verify DBYD
84f61aaa-4337-5016-95ba-2f7d8961ad5a | note | VERIFYING DOCUMENT - DBYD / Excavation Permit Survey (if required)
2659a055-fe78-52ba-bba8-e42be70e409c | note | VERIFICATION: EPC - H
957250bc-f800-5b27-bc70-c2027f158b65 | note | VERIFICATION: CLIENT - R
f7e4c7b8-8a27-4c5b-8704-f61de71c57db | signoff | HOLD POINT
13561204-2f46-43a7-819b-6d798b458fc7 | checkpoint | 1.3 - Approval of SWMS
b110dd53-9c3b-5ca7-9e8c-046f4db24bc3 | note | PROCEDURE / INSTRUCTION - Submission, review, and approval of all SWMS for the works
99bbdca0-2aed-54f9-b0a7-dd0639addb04 | note | ACCEPTANCE CRITERIA - SWMS Approved
7105a703-6720-520e-9e33-ff103032768e | note | VERIFICATION: EPC - H
392dbbfb-644a-5c65-ba44-9831b88ef443 | note | VERIFICATION: CLIENT - NA
2bd3376f-89ec-48ae-935c-165c6163a77f | signoff | HOLD POINT
19436585-9cdd-41a4-8707-84b87f495287 | checkpoint | 1.4 - Conformance of Materials
263a35f8-6d0c-5f70-a5ae-4bb2ef9b3d66 | note | PROCEDURE / INSTRUCTION - All delivered materials and procured items conform to project specifications and IFC drawings.
4346a48f-1316-5d06-8bb6-fbfb4be29a6d | note | ACCEPTANCE CRITERIA - As per Drawings and specifications
6866baaf-34bf-5eed-9093-492846bfdbec | note | VERIFYING DOCUMENT - Delivery Docket
2cdd975b-8c9a-512c-bd64-0022db3bfb83 | note | VERIFICATION: EPC - R
a2fa3676-416a-5a5c-b461-4c74abfa8a34 | note | VERIFICATION: CLIENT - S
04003e2f-4375-47e3-8cfa-d67a5d4d8b6c | checkpoint | 1.5 - Inspection Measuring and Test Equipment (IMTE) Registers
d6a7945c-d5a8-5378-ab89-e09d9be923fa | note | PROCEDURE / INSTRUCTION - Supply of all calibration certificates to the engineer including but not limited to:
f7ac41f8-bdbb-51a9-a0c5-d0133133fa73 | note | ○ Survey Equipment
7e911653-6a69-56b3-ac0f-730521fb8d20 | note | ACCEPTANCE CRITERIA - Visual
69462b8c-58ff-5c8b-8884-a9e61b0ea45d | note | VERIFYING DOCUMENT - Calibration Certificates
c97a4032-2e25-5785-9055-b1edeaeb5198 | note | VERIFICATION: EPC - R
a6efa2d4-b5c5-55f1-a3bb-740718b79d11 | note | VERIFICATION: CLIENT - S
5a9c0f7a-5335-4843-a7ee-e7ddde15daaa | section | Construction
87667074-de50-423b-849b-ff654d439723 | checkpoint | 2.1 - Survey and set out of piles
086a94e3-3c21-59bd-9f80-6b845be9d89a | note | PROCEDURE / INSTRUCTION - Mark the ground in accordance with Schletter pile location
55c24336-1b5d-550e-9263-6fd765a99928 | note | ACCEPTANCE CRITERIA - Visual as per Schletter pile location spreadsheet.
d146bf10-66f9-5ef2-aa81-e0243569deff | note | VERIFYING DOCUMENT - Survey As Constructed record
ae4058d5-b1b6-5e58-9066-8b0529b27eb2 | note | ○ Pile location spreadsheet
13319ba2-5dbf-5578-ad8e-b91a11296d2d | note | VERIFICATION: EPC - H
c276b3bf-2cee-5871-a316-087afd77d0bc | note | VERIFICATION: CLIENT - S
11589932-964f-41e0-807e-36e211e574db | signoff | HOLD POINT
77d1bca3-56a3-4123-8d42-c5b86865ea1d | checkpoint | 2.2 - Pile distribution to respective blocks
58ba4ccf-bafc-5395-9430-782defa16b22 | note | PROCEDURE / INSTRUCTION - Distribute colour coded piles, dimensions, and length into allocated location
87d8a8b0-3684-533c-a7b0-683480ed92b8 | note | ACCEPTANCE CRITERIA - Visual. Piles distributed as per Schletter drawings i.e., correct colour code, dimensions, and length.
864df3c1-7a63-5f1e-a36d-4d3a11b54b49 | note | ○ Pile location CSV file
539797a1-f898-5063-9a74-5cfe5278d27d | note | VERIFYING DOCUMENT - Survey As Constructed record
9641b483-0b3b-5add-9349-09b6cccf5e5c | note | VERIFICATION: EPC - R
ddc1681b-5bd1-5225-a27b-58ddeef13f28 | note | VERIFICATION: CLIENT - S
45f71390-c053-47fe-9121-725a976272a3 | checkpoint | 2.3 - Pile refusal
c4845592-6f5a-522b-8e5b-7b5443eea42c | note | PROCEDURE / INSTRUCTION - Drive piles to depth until it reached point of refusal.
aac74056-618e-53b0-840e-cc209079b799 | note | ACCEPTANCE CRITERIA - Record pile location and mark on the drawing
8ae81f6a-fda7-5ba7-af0a-c6d2db67c940 | note | ○ Record actual pile embedment depth
d3d8de2f-c25c-56fc-85ab-0e2dcd213411 | note | ○ Pile refusal in accordance with Pile Refusal Procedure
e8127dc4-1a12-5762-8dee-954db7c57ca6 | note | ○ Pile Testing Procedure
88524ba8-1a4f-5a54-9a49-c8c05b942da8 | note | ○ Piles cut and holes drilled as per Schletter documentation
37f7ab20-4d4c-5061-9edb-a85f1437a194 | note | VERIFYING DOCUMENT - Survey record
0e00d10a-396a-5cea-8e9a-8ab29bfc67e0 | note | ○ Pile marked on the drawing
7dc790e2-26b8-5afe-82d4-aacfad82b293 | note | ○ 1. Schletter - ITC – Piling
60f1881a-7c92-56a9-9120-6a8b7c6dfbde | note | ○ ITC Data Tracker Excel Pile Monitoring Sheet
c76e5f1c-1c25-5638-9333-9787c0a6f13c | note | – Embedment Depth
df4f47f4-0183-5625-ace4-1e9d5482d8bd | note | – Reveal Height
39988fbb-76a9-517d-b7ef-68a907c84aa7 | note | ○ Pile test result documentation
a936c7c4-4152-51a9-a3f5-22a055395fa1 | note | VERIFICATION: EPC - S
bf708f35-1d04-5c05-91d5-bc9f43f65e4f | note | VERIFICATION: CLIENT - S
210921ab-a1a0-4717-b1bb-a3c73ac5a510 | checkpoint | 2.4 - Piles installation
7be008ba-efcf-5cf5-b83c-ab21fe497099 | note | PROCEDURE / INSTRUCTION - Install pile on correct location as per Schletter drawing
cb46ef63-b4ba-58bb-884b-f4710ba04829 | note | ○ Install pile within the design tolerances
e3372d61-9514-581f-b241-2ee33452e691 | note | ○ Piles should have no damage or deformation and in correct orientation
0557ebd8-aeea-5422-9255-a6985375fbf4 | note | ACCEPTANCE CRITERIA - Tolerances as per Schletter Installation Manual Section 7.2 Installation Tolerances:
79603673-d58f-5546-afef-bc85382c7833 | note | ○ North-South 3°
c4baa657-7046-55a1-891b-448d6d8e668c | note | ○ East-West ± 3°
6d7fe3ed-15f2-54a1-a932-43386f392127 | note | ○ Pile Twisting from axis:± 5°
d698a0e9-575a-5372-982f-3735833dbba5 | note | ○ Distance E/W: ±100mm
488f05fb-76b0-59c6-bcc9-551fd918d4e6 | note | ○ N/S: ±50mm
7bff60e1-fd15-5e2a-9b20-b9210710c413 | note | ○ Reveal Height: ±100mm
29ce2282-1dea-5ac7-a675-6f9f1daeba70 | note | ○ Height difference foundation posts within one row: ±50mm
b547a5b4-0ac5-59a5-91ef-a9a139b3f4b7 | note | ○ Piles have no damage deformation and in correct orientation.
7ee2e5fc-07dd-57c9-80f9-c6cc28c4203f | note | VERIFYING DOCUMENT - Schletter - ITC – Piling
06b8882f-c76f-5dca-87c3-bfa8d6492463 | note | ○ Surveyset-out data
edf775c5-5d04-5e0f-bbc0-3a10684231d1 | note | ○ ITC Data Tracker Excel Pile Monitoring Sheet
6bf0dc7e-842b-595f-9c03-6f5cc7b5bf96 | note | ○ Pile(s) marked on the As- Constructed drawing/Red Line Mark-up
4f490877-8bfb-5d94-8ed4-14d452866f22 | note | ○ Punchlist
0e4c0add-9714-58dc-960b-c1916dbb3ea6 | note | ○ Survey record
c112cdd4-4e74-5783-989c-416b76565ce9 | note | VERIFICATION: EPC - R
3934943b-87d5-55a0-abdf-00735b78874c | note | VERIFICATION: CLIENT - S
506c802a-dab2-4a69-bef0-f7d49a3506f8 | checkpoint | 2.5 - Cold Galvanising Repair, if required
121fcab3-6426-5fcf-8869-cf920022c953 | note | PROCEDURE / INSTRUCTION - Use two coats of zinc rich galvanising paint on damage, deform, and top of piles
efd8a931-df2f-5391-a8a2-1d28d937544c | note | ACCEPTANCE CRITERIA - Galvanising repaired as per manufacturer’s recommendation and procedure.
642f5e9e-9724-54c6-9c39-629fb1de8a67 | note | ○ Visual
24762c94-8b8a-511a-b9f7-431f0e310a2b | note | VERIFYING DOCUMENT - Schletter - ITC – Piling
c3de3bba-e3e7-572d-b092-b25390a487a7 | note | VERIFICATION: EPC - R
6eee5560-a57e-5515-88fa-e2d36922f0a4 | note | VERIFICATION: CLIENT - S
c3fcd322-51ef-40af-a676-f94d64a242cf | section | Postconstruction
dc791a3b-5d29-4a40-a3aa-d6620283ca8f | checkpoint | 2.6 - As Constructed records – Red Line Mark-Up (RLMU) Drawings
dee27ed9-a372-577c-b105-f15b09018ea6 | note | PROCEDURE / INSTRUCTION - Engineer to compile and record changes on IFC Drawings, to be issued to Client .
73c77b8e-239f-5b06-b6d3-1732ecc25d99 | note | ACCEPTANCE CRITERIA - Visual
e5e0cafc-14a5-500a-bca4-caeb3a510c8b | note | VERIFYING DOCUMENT - RLMU Drawings
d0e61b9d-f037-5409-b3af-5df12b4ab557 | note | VERIFICATION: EPC - R
0096f3b4-2016-5026-b109-eb884402fdac | note | VERIFICATION: CLIENT - S
a479a5e7-5281-42ff-b351-bde5c2cdaef9 | checkpoint | 2.7 - Develop Punchlist
dceefd30-7fc8-5ce1-b8aa-a9d41f7288ea | note | PROCEDURE / INSTRUCTION - Development of punch list with PM/CM and/or Supervisor
6f8445e3-7fb1-554e-b54f-4c98d4ce4a6c | note | ACCEPTANCE CRITERIA - Punchlist closed in a timely manner
fad003e3-03b1-52f7-9172-13b970005784 | note | VERIFYING DOCUMENT - Punchlist
5b461795-e541-5d6a-a188-86122cc8ba64 | note | VERIFICATION: EPC - R
8ee665fe-1cbf-5a4c-8349-81937e432456 | note | VERIFICATION: CLIENT - S
0f5038fe-a50a-4a00-acd0-0656ac9275f5 | checkpoint | 2.8 - Final Walk Down
27d56f2f-5295-50ab-94cd-212e36014cdf | note | PROCEDURE / INSTRUCTION - 100% visual verification required for each pile upon ITP sign off
f7e05e21-e6db-5452-b6af-5f65e70557ac | note | ACCEPTANCE CRITERIA - Visual
c56cb6a9-6450-5edc-b132-8a7ae0301050 | note | VERIFYING DOCUMENT - Punchlist, if required
87a4ec6f-ff11-5504-9ebe-ab79c294df56 | note | VERIFICATION: EPC - H
10319e0e-2f0e-59ec-9192-66b9df0bfe61 | note | VERIFICATION: CLIENT - H
2cf042ef-23f5-4c8e-946a-5fdbd13274bf | signoff | HOLD POINT
47a5883b-25bb-419c-b43b-af23d6611a10 | checklist | Pile Predrilling & Filling ITC |  | Pile Predrilling & Filling ITC
820f2dc1-c839-41c6-815d-e829e3bf4bc9 | section | Details
822b60dc-9114-4145-92da-1e31b86d78d4 | checkpoint | Details
32563daa-1ab7-5b69-8c18-119dffa09cbc | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
d5772d00-ed1b-58a8-8ea1-ea88c53400de | textbox | Row Number
cbd42514-f2ec-5fdb-ad93-90be100094a7 | textbox | Table Number
4c0575c4-2bff-5de7-a919-021cde764dd5 | dropdown | Number of Piles | 8 Pile, 16 Pile, Other
ca25b2b1-54b4-5a1a-9023-e96cd94308ef | textbox | Specify (if other)
6e5a0348-d87d-430b-b534-6f0d9236b7e0 | section | Drilling
be355296-546b-4a34-8aaf-8a931af44f64 | checkpoint | Drilling
6e5a839e-51d4-51c0-b0f2-df4852e97a64 | date | Date
b452b2d3-99a2-5253-8004-33ce579f69c1 | dropdown | Drill Depth | 1.8m, Other
c3499d93-c223-5c0e-b131-6a0d9d33d9f9 | textbox | Specify (if other)
db566456-4ad7-5a34-a7e1-317dfb9c6a91 | dropdown | Drill Width | 300mm, Other
9f2400d4-d1e1-59a7-b2a3-1e458fa8f17a | textbox | Specify (if other)
7762566f-bf3c-4152-8244-cb38a0e4ed24 | checkpoint | North/South Verticality +/- 3deg
b82384e9-cfd3-4ded-930b-98b52e8e23d9 | checkpoint | East/West Verticality +/- 3deg
de788806-e841-4d7e-9856-3ea3c44a11fd | section | Fill
62dd6feb-3063-4611-99b0-a30d2f9788d4 | checkpoint | Fill
af816b8e-e914-5021-b303-be8d045629ec | dropdown | Predrill Fill Mix | 5% Stabilised Sand, Other
b14f36a2-2f66-5ffb-9759-6c062ea64cce | textbox | Specify (if other)
0f08d319-ba70-45f3-ad22-e0a9e62fb0b0 | checkpoint | Attachments
65334946-7ad1-40ae-94fa-2e6946071ac2 | checklist | Upload Attachments |  | Upload Attachments
6da6f498-e18e-4121-84fe-5cd5ddfb8d03 | section | Details
abd1894c-f4ca-4bd7-adb7-c536eb29dab6 | checkpoint-no-value | Upload Attachments