## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Piling ITC-ITR | itp |  |  |  |  | Piling ITC-ITR
section | Preconstruction
checkpoint | Design
label | DETAIL - Issued For Construction Drawings:
label | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
label | ○ Schletter Electronic Design Data
label | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
checkpoint | Survey & Setout
label | DETAIL - Schletter Electronic Design Data
label | – Schletter FS DUO - Fixed-tilt Installation Procedure
label | Survey As Constructed Record
label | – Pile Location Spreadsheet
checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
label | DETAIL - Supply of all calibration certificates
section | Construction
checkpoint | Pile Distribution to respective blocks
label | DETAIL - Survey Data
label | – Schletter pile location data
label | Visual Inspection
label | – Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
checkpoint | Pile Refusal
label | DETAIL - Drive piles to depth until they reach the point of refusal
label | ○ Record Pile location and mark on the drawing
label | ○ Record Actual Pile embedment Depth
label | ○ Pile refusal in accordance with pile refusal procedure
label | ○ Piles cut and holes drilled as per Schletter documentation
label | ○ Survey Record
label | ○ ITC Data Tracker Excel Pile Monitoring Sheet
label | – Embedment Depth
label | – Reveal Height
label | ○ Pile Test Result documentation
checkpoint | Pile Predrill to minimum embedment
label | DETAIL - For Each Pile
label | ○ Pile Predrill ITC
label | ○ Piles are minimum of 1.8m deep
label | ○ Predrill holes are minimum of 300mm dia
label | ○ Backfilled with approved mix as per Schletters Installation Procedure
checkpoint | Pile Installation
label | DETAIL - Schletter FS Duo Fixed-tilt Installation Procedure
label | ○ Install Pile on the correct location as per Schletter drawing
label | ○ Install pile within the design tolerances
label | ○ Piles should have no damage or deformation and in correct orientation
label | – North/South +/- 3°
label | – East/West +/- 3°
label | – Pile Twisting from axis +/- 5°
label | – Distance E/W +/- 100mm
label | – N/S +/- 50mm
label | – Reveal Height +/- 100mm
label | – Height difference foundation posts within one row +/- 50mm
label | ○ Piles have no damage deformation and in correct orientation
checkpoint | Cold Galvanising Repair, if required
label | DETAIL - Schletter FS Duo Fixed-tilt Installation Procedure
label | ○ Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
section | Close-Out
checkpoint | As Constructed - Redline Markup Drawings
label | DETAIL - At completion of the the piling for each area
label | ○ Markup Redline Asbuilts if different from design and identify changes
checkpoint | Non-Conformance-Reports
label | DETAIL - Non-Conformances Closed Out
checkpoint | Punch List
label | DETAIL - Development of Punchlist with PM/CM and or Supervisor
label | ○ Punch List closed out in a timely mannor
checkpoint | Handover
label | DETAIL - At completion of works QA/QC Pack is handed to client
label | ○ Client Verifies Work has been completed correctly and all quality documents are in order
holdpoint | HOLD POINT