## Sheet1
Homai Train Station - Inspection and Test Plan
Project Area |  | Homai Train Station |  |  |  | Rev | 2 |  | Inspection and Test Codes:
Activity Title |  | Lighting |  |  |  | Date | 2025-01-17 |  | [R] Review | Review of reports, records or other evidence of compliance.
Location | [5 empty] | Lot No. |  |  | [I] Inspection | In process check, work proceeds. Record the check if required.
Ref # |  | DN1212-ITP-011 | [6 empty] | [W] Witness | Inspection to be witnessed on site and recorded. Record to be filed.
DNZ Project Manager: |  | Dan Trotman | [6 empty] | [H] Hold | No work to proceed past Hold Point until this is completed, recorded and released
AT Project Manager: |  | Werner Nel
DNZ Project Engineer: |  | Grant Wallace
Drawings/Reference Documents: |  | Drawing Key, Notes & Luminaire Schedule: 3235599-SP03-BE-1000 Electrical Schematics: 3235599-SP03-BE-1001 Electrical Scope of Works: 3235599-SP03-BE-1002 Lighting Layout Sheet 1: 3235599-SP03-BE-1011 Lighting Layout Sheet 2: 3235599-SP03-BE-1012 Lighting Layout Sheet 3: 3235599-SP03-BE-1013
Specifications: |  | AS/NZS 3000 Electricity Act Electrical Codes of Practice Requirements from Auckland Transport, Auckland One Rail and KiwiRail Electrical Safety Regulations 2010 AS/NZS 3008 AS/NZS 1158
ITP Item # | Construction Activity or Material Element |  | Standard, Drawing or Specification Reference | Construction Activity Description, Test Type and Acceptance Criteria |  | Test Frequency |  | QA Record | Verification Method and On Site Responsibilities |  |  | DNZ Rep Sign and Date
[9 empty] | DNZ Engineer | Engineer's Rep | Designer Rep
1 | PRELIMINARY AND GENERAL
1.1 | Method Statement Development & Safety Analysis |  | The Downer Standards (TDS) | Prior to Construction: Document Review Method Statement & JSEA Completed & signed by relevant authority |  | Once |  | Work pack (MS,JSEA,ITP) | H | R | R | Sign | Date
1.2 | IFC Drawings and Specification |  | ACC | A minimum of two weeks prior to construction: document review. DWG’s are for construction or as per instruction Works done in accordance with KiwiRail specification |  | Once |  | N/A | R |  |  | Sign | Date
1.3 | Model |  | ACC | Model reviewed and confirmed with correct location; depth, height and orientation for each light pole. |  | Once |  | N/A | R |  |  | Sign | Date
2 | MATERIAL APPROVALS
2.1 | GAP40 |  | AS/NZS1260 AS/NZS 2053 | General all passing |  | Once |  | Mix Certification InEight Approval .................. | R |  | H | Sign | Date
2.2 | Light Pole |  | AS/NZS 4680 IFC Drawings | Light Pole type, height, outreach arm lengths as per IFC drawings |  | Once |  | MDS InEight Approval ....................... | I |  | R | Sign | Date
2.3 | Cable |  | 3235599-SP03-BE-1000: Note 10 | Cables must meet AS/NZS 3000 & AS/NZS5000 requirements. Supplied by Electrical Subcontractor. Minimum Street Lighting supply cable size shall be 1C 10mm² neutral screen cable. |  | Once |  | MDS InEight Approval ....................... | I |  | R | Sign | Date
2.4 | Luminaires |  | 3235599-SP03-BE-1000: Note 5,7 | Luminaires as per IFC approved drawings and specifications. All Luminaires shall be tilted at an angle of 0 Degrees to Horizontal unless stated otherwise. Each Luminar shall be provided with a 7 - PIN NEMA Socket and a LPC (Light Point Controller) to provide on-off light switching. 10 year Warranty from Supplier. |  | Once |  | MDS Warranty Certificate InEight Approval ....................... | I |  | R | Sign | Date
2.5 | Dali System |  | 3235599-SP03-BE-1002 | Contractor to provide new Dali Control system in controls section of board, Dali to be controlled by Rotary Dimmer for commissioning and adjustment purposes |  | Once |  | MDS InEight Approval ....................... | R |  | R | Sign | Date
3 | CONSTRUCTION ACTIVITIES
3.1 | Survey Setout |  | 3235599-SP03-BE-1000 3235599-SP03-BE-1001 3235599-SP03-BE-1002 3235599-SP03-BE-1011 3235599-SP03-BE-1012 3235599-SP03-BE-1013 | Surveyor to Setout light pole locations as per the model. Where pole is within 2m of the dripline of the trees, assess whether the tree requires trimming to minimise shadowing, and notify the Engineer for further action if required. Permitted Location Tolerance: -0.5m Parallel to The Carriage Way -0.2m Perpendicular to The Carriage Way -0.2m Vertically If the final pole location exceeds the permitted tolerance further lighting design may be required. |  | Every Light Pole |  | As-Builts | H |  | R | Sign | Date
3.2 | Hydro-excavation |  | 3235599-SP03-BE-1012 | Excavate down 1300mm (height) x 300mm wide (Diameter) |  | Every Light Pole |  | As-Builts Photos Checksheet | I |  |  | Sign | Date
3.3 | Pole Installation |  | 3235599-SP03-BE-1000: Note 13 3235599-SP03-BE-1012 | Excavate down 1300mm (height) x 300mm wide (Diameter). . |  | Every Light Pole |  | As-Builts Photos Checksheet | I |  |  | Sign | Date
3.4 | Cable Pulling |  | 3235599-SP03-BE-1012 | Each light pole to be installed as per the requirements of the NZTA and AS/NZS 3000, wiring rules. |  | Every Light Pole |  | MDS | I |  |  | Sign | Date
3.5 | Luminaires Installation |  | 3235599-SP03-BE-1012 | As per IFC drawings and specification, approved luminaires installed. |  | Every Installation |  | MDs Photos | I |  |  | Sign | Date
3.6 | Testing & Commissioning |  | AS/NZS 3000 | COC to be completed by the installer to confirm installation is safe and complies with the design and specifications. ROI to be completed by an independent Electrical Inspector to confirm the above prior to livening. Demonstrate all specific commissioning functions/requirements detailed in electrical specifications are met. |  | Once |  | Certification of Compliance COC/ESC by Installer ROI By Independent Inspector | H |  | I | Sign | Date
3.7 | Earthing Test |  | AS/NZS 3000 NZ Electrical Safety Regulations | Check of earthing of metal columns, outreach arms, and Luminaries. |  | Every Light Pole |  | COC/ESC | H |  | I | Sign | Date
4 | FINAL RECORDS
4.1 | As-Built |  | N/A | Installed as per design drawings. All compliance recorded CAD files |  | Once |  | As-Built | H |  | R | Sign | Date
4.2 | Redline Mark-Up |  | IFC Drawings | IFC Drawings mark-Up on ACC sheets dated and signed. |  | Once |  | IFC Drawings Mark-Up on ACC | H |  | R | Sign | Date
4.3 | Certificate of Compliance |  | Electrical Safety Regulations 2010 | Compliance Certificates, COC, ESC & ROI |  | Once |  | Certification | H |  | R | Sign | Date
4.4 | Producer Statement |  | Schedule 6 3910 | Signed PS3 confirming electrical works completed meets the requirements of the building code and consent plans. |  | Once |  | Signed PS3 | H |  | R | Sign | Date
4.5 | Non-conformances |  | DN1212-DOW-PLA-PM-0005 QMP | Non-conformances reports to be raised when specification not met. All non-conformances within the area under review need to be listed on the NCR report. NCR Reference ….................. |  | Each NCR |  | NCR forms on InEight | H |  | R | Sign | Date
Comments:
ITP APPROVAL PROCESS
Prepared By: Project Engineer |  |  | Grant Wallace |  | Signed: |  | Date:
Reviewed By: Project Manager |  |  | Dan Trotman |  | Signed: |  | Date:
Reviewed by: Quality Mgr./Eng. |  |  | Cordelia Girdler-Brown |  | Signed: |  | Date:
Reviewed By: Design Engineer |  |  | Daniel Cvitanich |  | Signed: |  | Date:
Reviewed By: AT Project Manager |  |  | Werner Nel |  | Signed: |  | Date:
Reviewed By: AT Engineer to Contract |  |  | Mike Robertson |  | Signed: |  | Date:
FINAL ITP CLOSE-OUT
Downer Project/Site Engineer |  |  |  |  | Signed: |  | Date:
QA Mgr./Engineer |  |  |  |  | Signed: |  | Date:
Engineer Rep(Assistant) |  |  |  |  | Signed: |  | Date:
Note on A43: Kelsey Wong: ITP Revision to be signed and approved the Project Lead prior to construction. Final version issued to Quality Engineer / Engineer's Rep for Comment and Acceptance of ITP.