## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1212-ITP-011 Lighting | itp |  |  |  |  | DN1212-ITP-011 Lighting Rev2
section | 1 - PRELIMINARY AND GENERAL
checkpoint | 1.1 - Method Statement Development & Safety Analysis
label | Standard, Drawing or Specification Reference - The Downer Standards (TDS)
label | Construction Activity Description, Test Type and Acceptance Criteria - Prior to Construction: Document Review
label | ○ Method Statement & JSEA
label | ○ Completed & signed by relevant authority
label | Test Frequency - Once
label | QA Record - Work pack (MS,JSEA,ITP)
label | DNZ Engineer - H
label | Engineer's Rep - R
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - IFC Drawings and Specification
label | Standard, Drawing or Specification Reference - ACC
label | Construction Activity Description, Test Type and Acceptance Criteria - A minimum of two weeks prior to construction: document review. DWG’s are for construction or as per instruction
label | ○ Works done in accordance with KiwiRail specification
label | Test Frequency - Once
label | QA Record - N/A
label | DNZ Engineer - R
checkpoint | 1.3 - Model
label | Standard, Drawing or Specification Reference - ACC
label | Construction Activity Description, Test Type and Acceptance Criteria - Model reviewed and confirmed with correct location; depth, height and orientation for each light pole.
label | Test Frequency - Once
label | QA Record - N/A
label | DNZ Engineer - R
section | 2 - MATERIAL APPROVALS
checkpoint | 2.1 - GAP40
label | Standard, Drawing or Specification Reference - AS/NZS1260, AS/NZS 2053
label | Construction Activity Description, Test Type and Acceptance Criteria - General all passing
label | Test Frequency - Once
label | QA Record - Mix Certification
textbox | InEight Approval
label | DNZ Engineer - R
label | Designer Rep - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Light Pole
label | Standard, Drawing or Specification Reference - AS/NZS 4680, IFC Drawings
label | Construction Activity Description, Test Type and Acceptance Criteria - Light Pole type, height, outreach arm lengths as per IFC drawings
label | Test Frequency - Once
label | QA Record - MDS
textbox | InEight Approval
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.3 - Cable
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1000: Note 10
label | Construction Activity Description, Test Type and Acceptance Criteria - Cables must meet AS/NZS 3000 & AS/NZS5000 requirements.
label | ○ Supplied by Electrical Subcontractor.
label | ○ Minimum Street Lighting supply cable size shall be 1C 10mm² neutral screen cable.
label | Test Frequency - Once
label | QA Record - MDS
textbox | InEight Approval
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.4 - Luminaires
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1000: Note 5,7
label | Construction Activity Description, Test Type and Acceptance Criteria - Luminaires as per IFC approved drawings and specifications.
label | ○ All Luminaires shall be tilted at an angle of 0 Degrees to Horizontal unless stated otherwise.
label | ○ Each Luminar shall be provided with a 7 - PIN NEMA Socket and a LPC (Light Point Controller) to provide on-off light switching.
label | ○ 10 year Warranty from Supplier.
label | Test Frequency - Once
label | QA Record - MDS, Warranty Certificate
textbox | InEight Approval
label | DNZ Engineer - I
label | Designer Rep - R
checkpoint | 2.5 - Dali System
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1002
label | Construction Activity Description, Test Type and Acceptance Criteria - Contractor to provide new Dali Control system in controls section of board, Dali to be controlled by Rotary Dimmer for commissioning and adjustment purposes
label | Test Frequency - Once
label | QA Record - MDS
textbox | InEight Approval
label | DNZ Engineer - R
label | Designer Rep - R
section | 3 - CONSTRUCTION ACTIVITIES
checkpoint | 3.1 - Survey Setout
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1000
label | ○ 3235599-SP03-BE-1001
label | ○ 3235599-SP03-BE-1002
label | ○ 3235599-SP03-BE-1011
label | ○ 3235599-SP03-BE-1012
label | ○ 3235599-SP03-BE-1013
label | Construction Activity Description, Test Type and Acceptance Criteria - Surveyor to Setout light pole locations as per the model.
label | ○ Where pole is within 2m of the dripline of the trees, assess whether the tree requires trimming to minimise shadowing, and notify the Engineer for further action if required.
label | ○ Permitted Location Tolerance:
label | -0.5m Parallel to The Carriage Way
label | -0.2m Perpendicular to The Carriage Way
label | -0.2m Vertically
label | ○ If the final pole location exceeds the permitted tolerance further lighting design may be required.
label | Test Frequency - Every Light Pole
label | QA Record - As-Builts
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Hydro-excavation
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1012
label | Construction Activity Description, Test Type and Acceptance Criteria - Excavate down 1300mm (height) x 300mm wide (Diameter)
label | Test Frequency - Every Light Pole
label | QA Record - As-Builts, Photos, Checksheet
label | DNZ Engineer - I
checkpoint | 3.3 - Pole Installation
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1000: Note 13, 3235599-SP03-BE-1012
label | Construction Activity Description, Test Type and Acceptance Criteria - Excavate down 1300mm (height) x 300mm wide (Diameter).
label | Test Frequency - Every Light Pole
label | QA Record - As-Builts, Photos, Checksheet
label | DNZ Engineer - I
checkpoint | 3.4 - Cable Pulling
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1012
label | Construction Activity Description, Test Type and Acceptance Criteria - Each light pole to be installed as per the requirements of the NZTA and AS/NZS 3000, wiring rules.
label | Test Frequency - Every Light Pole
label | QA Record - MDS
label | DNZ Engineer - I
checkpoint | 3.5 - Luminaires Installation
label | Standard, Drawing or Specification Reference - 3235599-SP03-BE-1012
label | Construction Activity Description, Test Type and Acceptance Criteria - As per IFC drawings and specification, approved luminaires installed.
label | Test Frequency - Every Installation
label | QA Record - MDs Photos
label | DNZ Engineer - I
checkpoint | 3.6 - Testing & Commissioning
label | Standard, Drawing or Specification Reference - AS/NZS 3000
label | Construction Activity Description, Test Type and Acceptance Criteria - COC to be completed by the installer to confirm installation is safe and complies with the design and specifications.
label | ○ ROI to be completed by an independent Electrical Inspector to confirm the above prior to livening.
label | ○ Demonstrate all specific commissioning functions/requirements detailed in electrical specifications are met.
label | Test Frequency - Once
label | QA Record - Certification of Compliance, COC/ESC by Installer, ROI By Independent Inspector
label | DNZ Engineer - H
label | Designer Rep - I
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Earthing Test
label | Standard, Drawing or Specification Reference - AS/NZS 3000, NZ Electrical Safety Regulations
label | Construction Activity Description, Test Type and Acceptance Criteria - Check of earthing of metal columns, outreach arms, and Luminaries.
label | Test Frequency - Every Light Pole
label | QA Record - COC/ESC
label | DNZ Engineer - H
label | Designer Rep - I
holdpoint | AUTHORITY HOLDPOINT
section | 4 - FINAL RECORDS
checkpoint | 4.1 - As-Built
label | Standard, Drawing or Specification Reference - N/A
label | Construction Activity Description, Test Type and Acceptance Criteria - Installed as per design drawings. All compliance recorded CAD files
label | Test Frequency - Once
label | QA Record - As-Built
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Redline Mark-Up
label | Standard, Drawing or Specification Reference - IFC Drawings
label | Construction Activity Description, Test Type and Acceptance Criteria - IFC Drawings mark-Up on ACC sheets dated and signed.
label | Test Frequency - Once
label | QA Record - IFC Drawings Mark-Up on ACC
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Certificate of Compliance
label | Standard, Drawing or Specification Reference - Electrical Safety Regulations 2010
label | Construction Activity Description, Test Type and Acceptance Criteria - Compliance Certificates, COC, ESC & ROI
label | Test Frequency - Once
label | QA Record - Certification
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Producer Statement
label | Standard, Drawing or Specification Reference - Schedule 6 3910
label | Construction Activity Description, Test Type and Acceptance Criteria - Signed PS3 confirming electrical works completed meets the requirements of the building code and consent plans.
label | Test Frequency - Once
label | QA Record - Signed PS3
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.5 - Non-conformances
label | Standard, Drawing or Specification Reference - DN1212-DOW-PLA-PM-0005 QMP
label | Construction Activity Description, Test Type and Acceptance Criteria - Non-conformances reports to be raised when specification not met. All non-conformances within the area under review need to be listed on the NCR report.
textbox | NCR Reference
label | Test Frequency - Each NCR
label | QA Record - NCR forms on InEight
label | DNZ Engineer - H
label | Designer Rep - R
holdpoint | AUTHORITY HOLDPOINT
section | ITP APPROVAL PROCESS
checkpoint-no-status | ITP APPROVAL PROCESS
label | Prepared By: Project Engineer - Grant Wallace
label | Reviewed By: Project Manager - Dan Trotman
label | Reviewed by: Quality Mgr./Eng. - Cordelia Girdler-Brown
label | Reviewed By: Design Engineer - Daniel Cvitanich
label | Reviewed By: AT Project Manager - Werner Nel
label | Reviewed By: AT Engineer to Contract - Mike Robertson
date | Date:
section | FINAL ITP CLOSE-OUT
checkpoint | FINAL ITP CLOSE-OUT
textbox | Downer Project/Site Engineer:
textbox | QA Mgr./Engineer:
textbox | Designers Rep(Assistant):
date | Date:
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature