## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | EFPQF01 - Inspection and Test Plan Schedule |  | EFPQF01 - Inspection and Test Plan Schedule | af2ac659-3843-4863-ba4a-c7c4c119e296
| section | Design
| checkpoint | Hydraulic Calculations
75b0fec2-8797-5c0d-a51e-2218c989b967 | note | Works By: Entire
10c13d23-7877-5b0d-b474-36bcdc8e8c34 | note | Entire: Review/Approve & Submitted
ceea1e4a-1a69-506d-b198-aa739a1e7580 | note | Consulting Engineer: Review/Approve
1f1b4b01-b112-51a6-9ce4-90c5e2c93186 | note | Builder: Review/Approve
6ebb1724-728d-54a6-bbec-14d33e07ccda | note | Acceptance Criteria: AS:2118
| checkpoint | Gaseous System Design
4505a533-5b38-53fe-8977-27eeecd1100e | note | Works By: Entire
b764913d-0945-56df-a464-09c3da29b849 | note | Entire: Review/Approve & Submitted
2cf909fe-4c09-5b3f-bbd4-ecaa58e1d5f2 | note | Consulting Engineer: Review/Approve
d6667dd8-7ae7-5e0b-9dce-97d8996e2b4b | note | Builder: Review/Approve
4fd72406-a322-5894-ba70-b3d31bfaec0e | note | Acceptance Criteria: AS:14520
| checkpoint | Fire Electrical
749e53de-d147-54e1-b11f-5c7762931e4a | note | Entire: Review/Approve & Submitted
1580a803-a6ed-50da-9228-bce50045f7b8 | note | Consulting Engineer: Review/Approve
22325bdd-405f-5886-a302-b86ea1e0aa4b | note | Builder: Review/Approve
83ba9794-e8a2-588f-81de-b72fd337c60c | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
| section | Drafting
| checkpoint | Drafting sprinkler
e99ef96e-8fcc-5368-a980-2b7a3a0f42c9 | note | Works By: Entire
24011b33-e818-5f38-908f-fc44bd670935 | note | Entire: Review/Approve & Submitted
86995db1-a39a-594a-9a1c-d150a52a9079 | note | Consulting Engineer: Review/Approve
cc32a978-fa26-545e-b9f4-6d6367158141 | note | Builder: Review/Approve
60b3bfee-26cd-532e-bc6c-f676de1fec42 | note | Statutory Authority: Inspect & Review/Approve
6406d4e9-1e69-54c7-b10a-1f2fe5d509bd | note | Acceptance Criteria: AS:2419, AS:2441
4f2ed4cf-4542-5f4b-96b1-c6dc191ad2a1 | note | QC Form: Drawing Register
| checkpoint | Drafting Gaseous Suppression
e8e93196-48b7-599d-b9c1-a12c7d23f04c | note | Works By: Entire
e591a5be-f428-5aa6-a60d-e99a2d2e2c1e | note | Entire: Review/Approve & Submitted
03320f2e-b605-59b3-ad88-6ebb2d6a2678 | note | Consulting Engineer: Review/Approve
887361f5-b8ee-58e5-a5ca-a2d23c05baeb | note | Builder: Review/Approve
9d0eba3b-da7d-5fb3-b190-93acdc8d9cbe | note | Statutory Authority: Inspect & Review/Approve
4f397939-9562-5428-97d3-ca840602b875 | note | Acceptance Criteria: AS:4214
59a36c3e-d720-5e09-88af-8e6d56d3cf76 | note | QC Form: Drawing Register
| checkpoint | Drafting Fire Electrical
84de714c-ce1e-51fa-b3e6-55c316292f80 | note | Works By: Entire
2ef38739-3dc1-5020-9517-d016c72f1357 | note | Entire: Review/Approve & Submitted
5aed36c8-5b06-59b6-ba0c-74b6a4d6ca30 | note | Consulting Engineer: Review/Approve
8a415d43-0372-52a3-9b57-6838f6a9bc90 | note | Builder: Review/Approve
06663100-cf5c-5e30-a11e-64237703b1f1 | note | Statutory Authority: Inspect & Review/Approve
36b721c3-c590-549c-9aa4-9a7699498f44 | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
a53cb974-793e-5f02-93bf-022f728b8938 | note | QC Form: Drawing Register
| section | Samples
| checkpoint | Sample Tech Data
efccd5ac-f558-551d-a332-63ef566a4ccd | note | Works By: Entire
61e909ac-403c-520b-889d-9b2341623a8a | note | Entire: Review/Approve & Submitted
7ab921c6-9750-5c86-8a8b-33c2450cd1a0 | note | Consulting Engineer: Review/Approve
7f031a56-a58b-5e7c-8a5b-779bf6b2521b | note | Builder: Review/Approve
017047a6-6dc3-58db-8d38-e1e141b224ba | note | Acceptance Criteria: Specification
96a5f55e-ed7f-5ca6-8707-719da3b367f7 | note | QC Form: Sample Register
| section | Off-Site Manufacture
| checkpoint | Fire pumps and tanks
8c2ce02b-2180-529b-921d-bfed7c724f0b | note | Works By: Supplier
12457955-bada-53cf-a9b7-5111a449d300 | note | Entire: Review/Approve & Submitted
3ebff7c9-efd5-5d2f-b75c-2c0d0cd4c6e1 | note | Consulting Engineer: Review/Approve
cc0fa70a-925b-5388-af44-b89c2d07905e | note | Builder: Review/Approve
6758c01c-e784-5ae5-99c6-4383eba58f3c | note | Acceptance Criteria: AS:2941
| checkpoint | Fire Indicator Panel
51c63f04-0078-5590-997c-0b90be5267bd | note | Works By: Supplier
ffed5265-6db3-5b6d-b5e9-7b0ae5c284f3 | note | Entire: Review/Approve & Submitted
e5774df5-7a7b-56f6-9aa3-333b62ea7dc0 | note | Consulting Engineer: Review/Approve
61648154-66f5-56de-bc7d-1ee99b66e562 | note | Builder: Review/Approve
9b502326-3249-5872-85b7-ec007ef4852d | note | Acceptance Criteria: AS:1670, AS3000
| section | Incoming Inspection
| checkpoint | Sprinkler pipe
3c0155a3-9de8-564a-8dc6-6fcfa803fbe1 | note | Works By: Entire
31ac5222-2637-54fd-b351-7b90261423bf | note | Entire: Review/Approve & Submitted
149bad58-7959-5935-b787-8a3329c5245b | note | Consulting Engineer: Review/Approve
bcb1143e-ec3d-5296-a690-a1d44fe6523f | note | Builder: Review/Approve
59ae6391-273c-5bc9-bc21-7a5957a90274 | note | Acceptance Criteria: AS:2118
cdbe1ed7-a399-5fae-87e4-f25b246662a5 | note | QC Form: ENT-006 Hydrants and hosereels
| checkpoint | Fire pumps and tanks
c233c649-e520-5f26-860c-c31d93f26759 | note | Works By: Entire
ad617cfd-0fee-50d8-ba50-813fa6ca3056 | note | Entire: Review/Approve & Submitted
b7ac890a-fe4f-5a22-9927-7e9c322c3747 | note | Consulting Engineer: Review/Approve
ca43d035-242a-5a1b-94f4-74da9067a70f | note | Builder: Review/Approve
8298f35b-e68c-50fe-a6fe-b835a517e174 | note | Acceptance Criteria: AS:2941
| checkpoint | Gaseous Fire Suppression
36ee9cc4-08a7-5e14-ba80-c44066b05c12 | note | Works By: Entire
348bd128-0c11-5a3f-8b9a-dbee9d580a19 | note | Entire: Review/Approve & Submitted
74014bb0-bb45-595e-9ce0-b390b49cae82 | note | Consulting Engineer: Review/Approve
bedc598b-acc9-5559-9941-0fb8fa519aac | note | Builder: Review/Approve
cea76932-a2b6-5ab1-a072-c06c473ce344 | note | Acceptance Criteria: AS:4214
| checkpoint | Fire Electrical
a1ff677b-9880-5224-87ad-0d9778c88416 | note | Works By: Subcontractor
57bd9426-edf1-55cb-a741-9134c864357a | note | Entire: Review/Approve & Submitted
e8a24c04-bf78-57f8-87c5-0807bc3872eb | note | Consulting Engineer: Review/Approve
e3d7538d-4836-536d-aa52-ddc095bf9cf5 | note | Builder: Review/Approve
c6189382-e4b3-547e-b1e2-01fb10bf1dba | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
3c322b78-ea2e-51c4-8d3e-64abca7bb66a | note | QC Form: ENT-013 - Fire Detection
| section | Installation
| checkpoint | Fire Hydrant / Hosereels - Rough-In & Fit-Off
9b87a939-c374-5b9d-93aa-b26712209fa6 | note | Works By: Entire
a60c2e09-a6f8-56a9-b245-b576b654f807 | note | Entire: Review/Approve & Submitted
332c5aa1-c8b3-56bd-844f-7fe0f781bc83 | note | Consulting Engineer: Review/Approve
0b81e9aa-7ba7-50da-b796-dac111cfccfb | note | Builder: Review/Approve
23921bd4-1166-522e-b3f9-abe5884de4ec | note | Statutory Authority: Inspect & Review/Approve
bd0c1149-82ed-51d5-8f37-cebca0c8ebf4 | note | Acceptance Criteria: AS:2419, AS:2441
dacaf819-350c-5cac-964c-816d80cc9fa4 | note | QC Form: ENT-004 - Sprinkler rough in and fit off
| checkpoint | Gaseous Fire Suppression - Rough-In & Fit-Off
c361f832-f72b-5ebb-b146-4cc7fc81347c | note | Works By: Entire
f0c65d00-3f0a-543b-9d45-ed0136dd1c04 | note | Entire: Review/Approve & Submitted
f7b92a5e-579e-5f1a-82d4-386884289d5a | note | Consulting Engineer: Review/Approve
0f43ff82-d9c5-5a07-9a05-7adfe35c717d | note | Builder: Review/Approve
0d287312-1377-5538-b43d-6722ddbbf871 | note | Statutory Authority: Inspect & Review/Approve
7c76f539-4840-55d8-99bd-9b5a81462e01 | note | Acceptance Criteria: AS:4214
| checkpoint | Fire Electrical - Rough-In & Fit-Off
8c514343-643b-5d3f-823c-96da96f0a1a3 | note | Works By: Subcontractor
7bcf0329-23c7-5277-9c75-d8f541f99794 | note | Entire: Review/Approve & Submitted
29fcc741-5ef8-5adc-ade9-6fcfd1de76d6 | note | Consulting Engineer: Review/Approve
d1f41103-1ce6-5561-9b22-12311cf2c08e | note | Builder: Review/Approve
8ff6a21a-b274-5d4d-aa24-a9e9b34ffd5f | note | Statutory Authority: Inspect & Review/Approve
ec7e108f-0c5d-5efe-877a-480178d5d22d | note | Acceptance Criteria: AS:1670, AS:1668, AS:3000
7adcf0d4-59ec-5ac7-8f8d-adb75a28fdfe | note | QC Form: ENT-013 - Fire Detection
| section | Commissioning
| checkpoint | Fire Hydrant / Hosereels
d92f0a97-902e-58aa-a36c-ee2795999383 | note | Works By: Entire
9d5f3517-935a-58bc-945d-577bd86a4705 | note | Entire: Review/Approve & Submitted
86028fbf-efe8-5b23-871f-9623b0b4e2d5 | note | Consulting Engineer: Review/Approve
712a92b9-b6e0-5d6e-a10e-71e1e8b6d483 | note | Builder: Review/Approve
ef373ade-619f-571a-94c2-daa764f70ded | note | Statutory Authority: Inspect & Review/Approve
966236f4-9f7f-5c44-99e9-f0ea11aa6031 | note | Acceptance Criteria: AS:2419, AS:2441
42266b76-0d4d-5e40-853e-496d8bb04785 | note | QC Form: ENT-006 - Hydrants & Hosereels
| checkpoint | Gaseous Fire Suppression
ccc2d51f-150f-58f2-b31d-77cb31fd2b1c | note | Works By: Entire
0b46836e-3b69-54bd-81a4-624509edafed | note | Entire: Review/Approve & Submitted
adf6ceac-8821-57d2-bf5c-d66ecbeaf7d9 | note | Consulting Engineer: Review/Approve
58fff31b-77c1-5c1e-a97a-a4e4e95e5c9b | note | Builder: Review/Approve
401dacab-729c-54b8-969e-48246caf53c8 | note | Statutory Authority: Inspect & Review/Approve
c7402064-dd48-50aa-830d-901f2712f0f4 | note | Acceptance Criteria: AS:4214
| checkpoint | Fire Electrical
b977e9c8-f147-58f8-bcf9-d555aa3f8a39 | note | Works By: Subcontractor
c095aa86-ec00-562a-b14a-2da8bfe0a397 | note | Entire: Review/Approve & Submitted
605ab80f-28a2-52ce-87fe-81dd4de009bb | note | Consulting Engineer: Review/Approve
553e7413-408f-519c-994e-dcfa52d47c36 | note | Builder: Review/Approve
55e166ca-34c0-5005-8439-b704bc466796 | note | Statutory Authority: Inspect & Review/Approve
147654bc-5d36-5c25-ad79-28f456114a93 | note | Acceptance Criteria: AS:1670
b112d656-97bf-5c58-bf7b-1aed4e6f85cb | note | QC Form: ENT-015
| checkpoint | Interface Checks - Mechanical / Fire
d068dcbc-0a1c-5c64-abe1-addf442baae9 | note | Works By: Entire
b0822ff5-2b67-538f-b751-5bf9be0ed53f | note | Entire: Review/Approve & Submitted
8df388c7-f08c-5020-a327-95bfa60163ba | note | Consulting Engineer: Review/Approve
926d3494-32e2-51a1-abed-46c4bf667d6e | note | Builder: Review/Approve
d92b2da0-6135-5b65-884f-8176b63fcb38 | note | Statutory Authority: Inspect & Review/Approve
8cb6a600-06d5-51f7-a9e8-2b0dac20c8b0 | note | Acceptance Criteria: AS:1670, AS:1668
5970fc76-f632-5fba-9460-71e7f22f5df7 | note | QC Form: ENT-015
| checkpoint | As-Installed Drawings and - Manuals (inc. Test Data)
8bb9c300-06e9-5dd8-993e-e08a9047f08e | note | Works By: Entire
9f2b2279-df62-5f49-821f-5b011e9c419f | note | Entire: Submitted
5e91e863-fd5e-51d9-838c-af6967647b69 | note | Consulting Engineer: Inspected & Review/Approve
3cd00bbc-5bf1-5d82-9a39-1eb995c52344 | note | Builder: Inspected & Review/Approve
| checkpoint | Final Defects List
0b5fd0fa-5460-5088-9140-1e894722871f | note | Works By: Entire
bf8195bc-766c-5966-a384-2964351f52f2 | note | Entire: Inspected
bfc8979d-5b1b-5f18-819f-455716c9fed6 | note | Consulting Engineer: Inspected & Review/Approve
15d7e796-5167-598b-90a4-1c40c3006973 | note | Builder: Inspected & Review/Approve
| section | Defects Liability & Warranty
| checkpoint | Entire to Provide Servicing information for Defects Liability Period
66bf7043-657e-5236-b292-08192e0199b3 | note | Works By: Entire Service Department
83ac04fa-45db-5a9f-8047-ea28cdd5e8d2 | note | Entire: Provide
39e93bba-5519-579e-9a03-dfb129574d40 | note | Builder: Review/Approve
ca6ebc63-91e5-5921-9509-9054a7181e4a | note | Acceptance Criteria: AS:1851.3
| checkpoint | Entire to Provide Warranty Information
cb9338de-9596-5778-a3e2-ba3617810ee8 | note | Works By: Entire Service Department
f77c6fee-d2d5-5959-9e3a-8277a857f7d0 | note | Entire: Provide
36e1177c-0595-57e9-8ea4-5fd4a47aa69b | note | Builder: Review/Approve
0876fc6e-b4d3-5b1c-b808-3493b607046c | note | Acceptance Criteria: AS:1851.4
| checklist | EFPQF02 - Fire Service Pump Install |  | EFPQF02 - Fire Service Pump Install | 29976682-cb6e-4a60-9ad2-390f9648c5f1
| section | Documentation
| checkpoint | Confirm correct construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
62205021-1a4a-5d8f-a785-ff244c0e7350 | tickbox | Fire service pumps
39d1c956-1e5b-537c-bdd5-dc6837087b5f | tickbox | Pump control panels
7d6b2848-449f-53f2-85a8-fbd1126ebd2c | tickbox | Valves
| section | Installation
| checkpoint | Plinths positioned. Min height 150mm
| checkpoint | Pumps positioned on plinth
| checkpoint | Minimum 1.0-meter clearance required around perimeter pumpset.
| checkpoint | Suction connected including isolation valves
| checkpoint | Pressure relief valves and drain installed
| checkpoint | Discharge check valves installed upstream of discharge isolation valve
| checkpoint | Discharge connected including isolation valves
| checkpoint | Suction and discharge pressure gauges installed
| checkpoint | Flow test arrangement installed
| checkpoint | Pump start pressure switches installed and wired
| checkpoint | Control panels installed and wired
| checkpoint | Battery trays installed
| checkpoint | Circulation relief piped to drain
| checkpoint | Gland drains installed
| checkpoint | Diesel exhaust and muffler installed discharging to atmosphere
| checkpoint | External bell and strobe installed
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF03 - Wet Pipe Sprinkler Install |  | EFPQF03 - Wet Pipe Sprinkler Install | 3e97b891-f164-40ef-a5fc-d2b368ec7634
| section | Documentation
| checkpoint | Confirm correct construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
02ed2de4-832f-55e6-b77a-231e45640ef0 | tickbox | Fabricated pipework.
94d28301-2e17-51a3-8162-39606a38464a | tickbox | Fittings.
76134ff8-1493-5a11-8aad-fce8106f77c2 | tickbox | Hangers.
1070260d-2773-5b4b-95eb-c9a95cbc7a59 | tickbox | Sprinklers.
9c371e64-0c5c-50cb-a903-5e6ec423b742 | tickbox | Valves.
| section | Installation Rough In / Fit Off
| checkpoint | Confirm hanger spacing.
86b7884a-092c-5496-bf7e-3ee833af6b7a | note | 25mm - max 4m spacing.
a768f9b6-57d4-571f-85ea-9827e82025ca | note | 32 – 100mm - max 5m spacing.
86057916-4c51-5355-8d7b-7389fb1b5520 | note | ≥ 150mm - max 6m spacing.
| checkpoint | Confirm support at change of direction at 1m max.
| checkpoint | Confirm support of pipework no more than 1m from end.
| checkpoint | Confirm support of armpiece exceeding 500mm.
| checkpoint | Confirm first support of range pipe within 2m of mains.
| checkpoint | Confirm pipework installed as per drawing.
| checkpoint | Confirm sprinklers installed/Fit Off
| checkpoint | Confirm sprinkler guards installed.
| section | Pressure Testing
| checkpoint | Confirm all open ends plugged.
| checkpoint | Confirm isolation and drain valves are closed.
| checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
| checkpoint | Record pressure test results on Pressure Test Form.
| section | Pressure Test Report Sheet
| checkpoint | Test Details & Results
755f261d-eb29-526a-a754-dac95380acb2 | textbox | Test number
811749f8-657b-53d6-8519-f84b1e3c25b4 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
8e0fa9bb-c8ff-59ea-a755-877c93853535 | textbox | Start Date
4953b92b-ed7d-5c6d-ab5c-3197d4a4bb5c | textbox | Start Time
f987ec9c-d4cb-5ee5-a901-5f2daafed381 | textbox | Start Pressure
8e830cb1-630d-5764-b09f-ecf6acf47685 | textbox | Finish Time
53b44b15-a45d-5440-923e-e3e912cd2f02 | textbox | Finish Pressure
d4d15f60-2fe0-5217-a619-4afe1caa5815 | textbox | Gauge Reference
| checkpoint | Test completed to specification/drawings & Area left clean/tidy
8319d033-7d2f-5260-ae4d-c107c3c6e06d | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checkpoint | Entire Fire Sign-Off (attach signature)
| checklist | EFPQF04 - Wet Pipe Sprinkler Control Valve |  | EFPQF04 - Wet Pipe Sprinkler Control Valve | 6c503164-b8b9-4ad4-b806-c43e167c088a
| section | Documentation
| checkpoint | Confirm correct construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
972225cf-f7fd-5bd2-90be-f402fa5303f2 | tickbox | Isolation valves.
418e5902-c725-571d-bba4-4906fda42b1f | tickbox | Alarm valves.
92185536-3cb2-5686-88f3-4b997edf44c8 | tickbox | Pressure switches.
7f1926d1-3f4d-58da-bab1-f07f53b1545d | tickbox | Jacking pump
| section | Installation
| checkpoint | Main stop valve installed
| checkpoint | Alarm valve installed
| checkpoint | Drain valve installed
| checkpoint | Alarm pressure switches installed
| checkpoint | Water motor alarm installed
| checkpoint | Pressure gauges installed
| checkpoint | Jacking pump installed
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF05 - Pre Action - Sprinkler |  | EFPQF05 - Pre Action - Sprinkler | 50a50edf-4a7c-4be1-90a2-b29ef25c3a27
| section | Documentation
| checkpoint | Confirm correct construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
aed2d1cd-c6cb-520a-a3ff-d1dcfd68ce4e | tickbox | Fabricated pipework - All pipe galvanised.
4c2ff96e-3726-5566-8402-3c98a05bdada | tickbox | Fittings - All fittings galvanised.
5480b87b-fe99-59fb-ae39-d0e9c99430ba | tickbox | Hangers - All hangers galvanised.
df32e533-1315-513c-ba60-f38fca91b16b | tickbox | Sprinklers.
be30bb18-8ae4-50cd-87f4-a8304525f78e | tickbox | Valves.
| section | Installation Rough In / Fit Off
| checkpoint | Confirm hanger spacing
f43fbe08-c488-51d7-a13c-186daf12e4bd | note | 25mm - max 4m spacing.
beb4a282-e660-5182-b858-70212cc06a68 | note | 32 – 100mm - max 5m spacing.
c0f74a5b-938c-575c-91fb-4023725b9b1e | note | ≥ 150mm - max 6m spacing.
| checkpoint | Confirm support at change of direction at 1m max.
| checkpoint | Confirm support of pipework no more than 1m from end.
| checkpoint | Confirm support of armpiece exceeding 500mm.
| checkpoint | Confirm first support of range pipe within 2m of mains.
| checkpoint | Confirm pipework installed as per drawing.
| checkpoint | Confirm pipework installed fall back to drain
| checkpoint | Mains minimum 2mm per 1m.
| checkpoint | Ranges minimum 4mm per 1m.
| checkpoint | Confirm sprinklers installed.
| checkpoint | Confirm sprinkler guards installed.
| section | Pressure Testing
| checkpoint | Confirm all open ends plugged.
| checkpoint | Confirm isolation and drain valves are closed.
| checkpoint | Fill pipework with air to 50kpa to confirm no open ends.
| checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
| checkpoint | Fill pipework with air to 300kpa. Hold for 30 minutes. Pressure loss of 10% (60kpa) permitted.
| checkpoint | Record pressure test results on Pressure Test Form.
| section | Pressure Test Report Sheet
| checkpoint | Test Details & Results
ca7a993b-cff9-5c9a-ad51-7d72ca7bea24 | textbox | Test number
6ffac8cf-5aea-5966-8a69-abbdf3773b2a | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
306adc11-b849-5662-9900-5b900591f721 | textbox | Start Date
1f88a28e-5d69-57f5-9684-4cfb329c5f1f | textbox | Start Time
7203bc31-50a2-5216-8fad-4174c0e38b1d | textbox | Start Pressure
33ae1bcf-52b7-5c5d-a594-d82e30ba503e | textbox | Finish Time
7d34f504-8177-5ee2-97d0-e08d49f83a6c | textbox | Finish Pressure
e695b86a-8b93-579c-82f1-3fc705cd7398 | textbox | Gauge Reference
| checkpoint | Test completed to specification/drawings & Area left clean/tidy
8cae7bf3-89fc-560b-ac2e-6890e216fe94 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checkpoint | Entire Fire Sign-Off (attach signature)
| checklist | EFPQF06 - Pre Action - Sprinkler Control Valve |  | EFPQF06 - Pre Action - Sprinkler Control Valve | ca67014a-c7e2-469d-ba0d-9b45e8823ecd
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
1cea06c6-5b14-585f-af2d-12da16e4473c | tickbox | Isolation valves.
c7c8c07a-fd60-56c9-a62f-aa2f7ef2f53e | tickbox | Alarm valves.
862a1f2c-f631-5424-9886-5b6706c7e5dc | tickbox | Pressure switches.
6072e851-b13c-53ec-95bb-4a25e2e12bde | tickbox | Nitrogen generator/Air compressor
| section | Installation
| checkpoint | Main stop valve installed
| checkpoint | Alarm valve installed
| checkpoint | Drain valve installed
| checkpoint | Alarm pressure switches installed
| checkpoint | Water motor alarm installed
| checkpoint | Pressure gauges installed
| checkpoint | Nitrogen generator/air compressor installed
| checklist | EFPQF07 - Pressure Test Report Sheet |  | EFPQF07 - Pressure Test Report Sheet | af794b3f-47e8-4807-a2fb-7c0b2c90e8b1
| checkpoint | Test Details & Results
4d5a2ef8-514b-5da9-b061-78800ade67b2 | textbox | Test number
d7e4d6ee-2d6c-589d-abc6-f8fd67229e64 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
6daca6ce-da91-5c22-9c84-4ef1ee8fc23d | textbox | Start Date
f8517976-15f3-5c32-a681-dd267b341de9 | textbox | Start Time
a6c75f98-4ccc-5b2e-a301-c45945d1df3d | textbox | Start Pressure
3efc9e39-50f1-5783-aefb-56bde94ce60d | textbox | Finish Time
790d36db-230a-53c9-aeb9-85dd25112b76 | textbox | Finish Pressure
3e2fc0cc-38aa-5a07-8287-2ff846d0d46a | textbox | Gauge Reference
| checkpoint | Test completed to specification/drawings & Area left clean/tidy
ff1afbc3-9830-5096-a73e-4bfb2aa2850a | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checkpoint | Entire Fire Sign-Off (attach signature)
| checklist | EFPQF08 - Fire Alarms Install |  | EFPQF08 - Fire Alarms Install | 3d66fbb7-198b-4907-8a27-164d31766191
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
f66736f4-2b7f-5983-a236-31b741c540e2 | tickbox | Fire rated cable
d3e539a4-9e05-5178-bb08-fe79811defaf | tickbox | TPS cable
4998b3cc-0374-5eb2-a830-7921ad9a957e | tickbox | Detectors
3e94d5d0-91e1-575c-a600-478fb862bddd | tickbox | Strobes
1dbac755-6b2c-59d0-bd9c-8b7f8cf61e63 | tickbox | Speakers
| section | Installation Rough In / Fit Off
| checkpoint | Confirm correct cable type run
| checkpoint | Confirm cable support/conduit fixings and spacings
| checkpoint | Confirm segregation from other electrical services
| checkpoint | Confirm detector fit off locations
| checkpoint | Confirm speaker fit off locations
| checkpoint | Confirm strobe fit off locations
| checkpoint | Confirm fire interfaces connected to sprinkler installation
| checkpoint | Confirm fire interfaces connected to security
| checkpoint | Confirm fire interfaces connected to mechanical
| checkpoint | Confirm fire interfaces connected to BMS
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF09 - MASDS Install |  | EFPQF09 - MASDS Install | 16489fec-0d14-4aa9-ac87-ac2c045cdf15
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
7fcd075c-dab8-5e7f-a734-c13e038a96af | tickbox | Fire rated cable
b75cc916-0397-558d-bd84-d6f8f57a8d51 | tickbox | TPS cable
d32e9c1b-febc-5d9f-815d-0c50293d8a03 | tickbox | MASDS units
f2eee3bb-cef2-549f-bf88-ecbfa5033e9c | tickbox | MASDS pipework
fdf2825f-56c3-54d2-a5da-bddfbe329e0e | tickbox | MASDS Power supplies
| section | Installation Rough In / Fit Off
| checkpoint | Confirm correct cable type run
| checkpoint | Confirm cable support/conduit fixings and spacings
| checkpoint | Confirm segregation from other electrical services
| checkpoint | Confirm MASDS pipework installed as per drawing
| checkpoint | Confirm MASDS sampling points size & spacing
| checkpoint | Confirm MASDS unit fit off locations
| checkpoint | Confirm MASDS power supply fit off locations
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF10 - FDCIE Install |  | EFPQF10 - FDCIE Install | 9342c5a0-f412-4923-9424-0f8bccf720ec
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
aa439d13-c9e9-5ed7-9353-e68346d4d2d7 | tickbox | Fire rated cable
fda1534a-1006-5e0b-9076-336fcc5cb0ec | tickbox | TPS cable
6ed17c31-5c95-5371-b3f4-d98a584b445a | tickbox | FDCIE Panel
| section | Installation Rough In / Fit Off
| checkpoint | Confirm correct cable type run
| checkpoint | Confirm cable support/conduit fixings and spacings
| checkpoint | Confirm segregation from other electrical services
| checkpoint | Confirm FDCIE mounted in correct location
| checkpoint | Loop cables terminated to correct output
| checkpoint | Confirm OWS cables terminated to correct output.
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF11 - Fire Hydrant & Hosereel Install |  | EFPQF11 - Fire Hydrant & Hosereel Install | 077c2f57-519a-4df3-b958-a59785b408dd
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
e01389dd-80e3-5298-a433-6544a457181b | tickbox | Pipework.
6e707654-53d0-5f87-b923-ed75e29dae79 | tickbox | Fittings.
a03cb07f-d5e7-57cd-926c-3c24a89050c2 | tickbox | Hangers.
64036684-0875-5782-aa2b-10a54624b63d | tickbox | Isolation valves.
c0946354-1914-5cf6-8908-599451ebba33 | tickbox | Hydrant valves.
af868d7e-38f1-5782-a91f-cf84e0e53d81 | tickbox | Hosereels
| section | Installation Rough In / Fit Off
| checkpoint | Confirm hanger spacing.
1b2bcd12-abd2-52bf-b05d-124ea05c3f5c | note | 100mm - max 5m spacing.
de9b2cac-b8e9-58e3-83a7-ba5a30734dfc | note | ≥ 150mm - max 6m spacing.
| checkpoint | Confirm support at change of direction at 1m max.
| checkpoint | Confirm support of pipework no more than 1m from end.
| checkpoint | Confirm support of horizontal branch from vertical riser no more than 300mm from riser
| checkpoint | Confirm pipework installed as per drawing.
| checkpoint | Confirm hydrant height at handle between 750mm and 1200mm
| checkpoint | Confirm minimum clearance around hydrant handle 100mm
| checkpoint | Confirm hydrant valve outlet not inclined more than 35° from horizontal
| checkpoint | Confirm outlet has 300mm clearance for a minimum 225 degrees
| checkpoint | Confirm hosereel mounting height 1400- 2400mm to centre of barrel
| checkpoint | Isolation valve height is 900 – 1100mm
| checkpoint | Maintain 100mm clearance around barrel
| checkpoint | Confirm hydrant cap and chain installed
| checkpoint | Confirm installation pressure gauge installed at top of most remote hydrant
| checkpoint | Confirm pipe identification labels installed
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF12 - Fire Tank Install |  | EFPQF12 - Fire Tank Install | 58ed7254-281d-44d0-a0f5-21ac4be06975
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
d3d376c1-0d4a-54d3-92bf-77c8760b9c8e | tickbox | Tank Panels.
0a235a6e-06ef-5db1-aaf1-74e25b926bed | tickbox | Roof Purlins.
60265ce7-b071-5bbe-9ba1-d8b6823323b6 | tickbox | Roof Sheet.
019dee7d-95fb-5425-a938-4d0cdb0392f9 | tickbox | Access ladder.
6ab9fa14-5490-5fc6-9243-114cdf680dd7 | tickbox | Vortex.
43877af9-c88c-530c-a3d4-8378f072aaa0 | tickbox | Pipe nozzles.
| section | Installation
| checkpoint | Confirm tank slab tolerance within +/- 3mm
| checkpoint | Build first panel ring
| checkpoint | Build roof including access hatch
| checkpoint | Hang tank liner
| checkpoint | Fix tank jacks and lift for next panel install
| checkpoint | Install ladder sections at each lift
| checkpoint | Fix base ring and remove jacks
| checkpoint | Ensure internal tank base free of debris
| checkpoint | Install geo fabric to base
| checkpoint | Stretch tank liner to tank base
| checkpoint | Connect pipe nozzles and vortex
| checkpoint | Confirm tank level indicator installed
| checkpoint | Confirm tank capacity labels installed
| checkpoint | Confirm warning labels installed
| checkpoint | Confirm ladder guards and inspection hatches installed
| checkpoint | Confirm no leaks when tank full
| checkpoint | Copy of Installers statement attached
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF13 - Fire Booster Assembly Install |  | EFPQF13 - Fire Booster Assembly Install | ad350319-e9f8-4d87-a0e0-470f869bddb6
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
7c3b793a-72ed-53b0-a9c6-6d4d5c11401f | tickbox | Fire Boosters
ac9a0216-a4ab-54ad-818e-263a39dbba38 | tickbox | Suction Connections
8918bf17-6ce6-5189-9eee-ab6d6b316b2c | tickbox | Feed Hydrants
1161fa92-d8db-53d3-bfe3-2366664db53c | tickbox | Isolation valves
| section | Installation
| checkpoint | Confirm height of booster outlets between 750mm and 1200mm above standing surface in front of booster
| checkpoint | Confirm height of feed hydrant outlets between 750mm and 1200mm above standing surface in front of booster
| checkpoint | Confirm height of large bore suction connection between 450mm and 600mm above standing surface in front of booster
| checkpoint | Confirm height of small bore suction connection minimum of 400mm above large bore suction connection
| checkpoint | Maintain minimum 450mm centre to centre clearance between outlets
| checkpoint | Confirm front face of all connections within 150mm of the front of cabinet
| checkpoint | Confirm caps and chains installed
| checkpoint | Confirm isolation valves chained and locked
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF14 - Gas Suppression Install |  | EFPQF14 - Gas Suppression Install | 9cb0af2b-bfb3-4512-97ad-f7107944ff62
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
d1a857aa-be6b-56da-8e6f-34e6e6642183 | tickbox | Fabricated pipework.
9a9e34c4-3cb6-569a-aa1e-61db76ae79fe | tickbox | Fittings.
cb0e3fad-2fd9-56af-b2e7-97f846c7d95d | tickbox | Hangers.
0a615a3f-6bcc-5452-b1dc-62c4595f2780 | tickbox | Nozzles
52281e0b-e9ce-5edf-a94b-21abb05c4e2f | tickbox | Cylinders
c8d8244c-aa14-509e-8e6c-f2909c5dbe0b | tickbox | Actuators
c6d09d38-bafb-5fb7-836a-ac26826e89ec | tickbox | Hoses
4f234557-0b66-5fe3-a7d7-b7ec48c927f6 | tickbox | Gauges
| section | Installation Rough In / Fit Off
| checkpoint | Confirm maximum hanger spacing.
cff007c4-5897-576e-bb40-6fd11e1983c5 | note | 25mm - max 4m spacing.
1dce705c-12b9-5658-a34c-a3b19c87e942 | note | 32 – 100mm - max 5m spacing.
10404965-7518-5e57-9635-6422401bd137 | note | ≥ 150mm - max 6m spacing.
8d6b5393-edb3-5174-9608-34daba36a241 | note | Acceptance Criteria - AS:2414
| checkpoint | Confirm support at change of direction at 1m max.
54e0d028-b43b-503b-96e2-f21bcaa42ba2 | note | Acceptance Criteria - AS:2414
| checkpoint | Confirm support of pipework no more than 1m from end.
29905bbc-b911-5dec-bc4f-e24891741892 | note | Acceptance Criteria - AS:2414
| checkpoint | Confirm support of armpiece exceeding 500mm.
fdb0c227-836b-5620-9ebf-d435925bb94d | note | Acceptance Criteria - AS:2414
| checkpoint | Confirm first support of range pipe within 2m of mains.
a0c983c5-a973-500f-88a4-1befd97924f5 | note | Acceptance Criteria - AS:2414
| checkpoint | Confirm pipework installed as per drawing.
| checkpoint | Cap installation and perform pressure test
be076c61-3af6-5bad-a275-94a5aeb08b2e | note | Acceptance Criteria - AS:2414
| checkpoint | Confirm discharge nozzles installed.
| checkpoint | Confirm gas cylinder mounting as per manufacturer instruction
| checkpoint | Confirm cylinder hoses fitted to discharge manifolds
| checkpoint | Confirm cylinder pressure gauges fitted and indicating correctly
| checkpoint | Confirm discharge actuators fitted
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| section | Pressure Test Report Sheet
| checkpoint | Test Details & Results
f1320ad2-e43e-5d6e-83c8-c38a0ef2e056 | textbox | Test number
f791045b-3c0e-5a08-9520-ae9bbc399732 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), PNEUMATIC TEST – 300kpa 10 MINS - PERMITTED LOSS 20% (60kpa)
b47f340c-fd27-58b5-854c-53ecf0626826 | textbox | Start Date
f46e7a5b-2d10-5726-adeb-3b87437290e9 | textbox | Start Time
2234275e-af14-55ed-9178-abf188a4dd5b | textbox | Start Pressure
e8d7fd8d-3b5c-5fb5-be78-7012111372fc | textbox | Finish Time
388e6655-0f0e-5b23-8ca9-e639c135e794 | textbox | Finish Pressure
ecf5ff79-7621-5c8f-b5f3-927b7f953f96 | textbox | Gauge Reference
| checkpoint | Test completed to specification/drawings & Area left clean/tidy
8dc1b016-4058-5d84-a172-2465bb970740 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checkpoint | Entire Fire Sign-Off (attach signature)
| checklist | EFPQF15 - Water Mist Install |  | EFPQF15 - Water Mist Install | 0d270ce7-46ce-466f-a3c1-b5b3d2ad1ee9
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
a1233818-1504-519b-b96c-efcd4b7b8a05 | tickbox | Pipe.
62ff1372-80f0-5e95-99b1-eb89dc2dde41 | tickbox | Fittings.
43ff3743-cd49-5779-bfa1-835a90285708 | tickbox | Hangers.
39dde66f-4ffa-5bb2-a3eb-450c1a310cc2 | tickbox | Nozzles
ce2f5691-d6f0-5626-8f11-97f1d0a210fd | tickbox | Valves
| section | Installation Rough In / Fit Off
| checkpoint | Confirm maximum hanger spacing.
ad2ac105-1c25-533a-b722-420d02bc28f3 | note | ≤25mm - max 4m spacing.
44212eb3-0ea9-58f7-844f-cb863bfd9ebe | note | 32 – 100mm - max 5m spacing.
ada13c92-bb1d-5689-a53a-864a60de67a8 | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm support at change of direction at 1m max.
4f798ecf-7fbe-562b-80c6-59ac974cf5f9 | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm support of pipework no more than 1m from end.
0a831763-0ae8-596c-82f3-08fb96f6f956 | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm support of armpiece exceeding 500mm.
e1363c42-2446-513c-b293-d7ed73d893ab | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm pipework installed as per drawing.
| checkpoint | Confirm isolation and test valves installed
| checkpoint | Cap installation and perform pressure test
e38f84b8-272c-579d-b708-459422c09c7a | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm discharge nozzles installed.
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| section | Pressure Test Report Sheet
| checkpoint | Test Details & Results
11ba0e0b-81c8-5a4e-bc78-d4d05dcccfa3 | textbox | Test number
853789fa-d629-5671-bfe4-74ab8d5e441d | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), HYDRAULIC TEST - 3300kpa 2 HOURS - NO LOSS
1976b4e3-36f5-5b9d-8588-f9d66cdbe73e | textbox | Start Date
bc4a72bb-58bf-5043-8971-46c96189b09d | textbox | Start Time
a60266d0-72f7-5623-8e7c-68217acaf452 | textbox | Start Pressure
ce96801f-9277-5fa9-b33e-1645d1f8293b | textbox | Finish Time
58329df4-cd73-5400-a9d3-0781202f54b7 | textbox | Finish Pressure
037e5971-e62f-55d1-8041-1d54bc376517 | textbox | Gauge Reference
| checkpoint | Test completed to specification/drawings & Area left clean/tidy
fa1d456d-8eac-58b0-bc15-f19b9a2002dc | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checkpoint | Entire Fire Sign-Off (attach signature)
| checklist | EFPQF16 - Fire Extinguisher & Blanket Install |  | EFPQF16 - Fire Extinguisher & Blanket Install | 5a2d1e2b-31c1-46a1-8c0c-111b0679c9ae
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
51684073-1818-5d11-8874-e1d41b3a61e7 | tickbox | Fire Extinguisher.
025605e5-0dae-5cd0-a2da-722009715ecc | tickbox | Fire Blanket.
12a7bf57-88bc-5c40-b9a7-d5990bf6e5f5 | tickbox | Signage.
| section | Installation
| checkpoint | Confirm top of extinguisher handle ≤1200mm above floor level
ae94a543-f3d9-53b6-9a67-c20be628f42f | note | Acceptance Criteria - AS:2444
| checkpoint | Confirm extinguisher type signage located just above handle
c60e85a4-a008-56f8-a086-6cb0f7f9479c | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm extinguisher location signage located at ≥2000mm above floor level
6378b356-4d79-5df3-ba36-0da4878c09c8 | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm fire blanket located in a readily accessible location
7eb383fa-d470-53b0-897c-0972773db562 | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm fire blanket signage provided adjacent to the fire blanket
8e71cc80-4a76-541b-bb27-94d820a41ca1 | note | Acceptance Criteria - AS:4587
| checkpoint | Confirm fire blanket location signage located at ≥2000mm above floor level
8c274b39-65e7-52b8-b508-de8019fc9fad | note | Acceptance Criteria - AS:4587
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF17 - Fire Electrical Commissioning Test Report |  | EFPQF17 - Fire Electrical Commissioning Test Report | aae25a7f-93b8-44f7-ad72-4cba18d11b90
| section | Pre-Start
| checkpoint-no-value | Pre-Start Details
09e00421-fdbe-5ddf-9803-b9776048cc57 | textbox | drawing reference
92e5d0bc-d0ea-5f69-95e7-bd084e910330 | textbox | level and area
| section | Installation
| checkpoint | Secure cabinet
42c56c17-5ed7-527e-a2c9-33329ba39fc2 | note | Specification Ref: drawing
| checkpoint | Extinguishers installed
c5cb6169-1da7-5da2-82f1-e4d3ab9b39aa | note | Specification Ref: drawing & AS:2444
| checkpoint | Signage to meet code compliance
e5e9d815-8f8c-5508-bbb4-892768dc8943 | note | Specification Ref: drawing & AS:2941
| checkpoint | Hangers location and spacing
549b8757-0ea0-547e-853b-d88cb8feebf4 | note | Specification Ref: drawing & AS:2941
| checkpoint | Fire blankets
c0a73829-191a-5638-840a-660a3fe39896 | note | Specification Ref: AS:2444
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
6adb0fa4-e920-5c65-8a1b-90bb4e255ac9 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
a8d0b919-5ec1-5f8e-a5da-469fa7105a71 | button | Entire Fire Signature Sign-Off added below | Yes, No
| checklist | EFPQF18 - Fire Penetrations (x 10) |  | EFPQF18 - Fire Penetrations (x 10) | e33701fc-eeb1-4273-bf63-b18b059fc9b4
| checkpoint | Fire Penetration details
f4386e4e-934e-5934-a52e-35016c884907 | textbox | Location
705fd4fa-84a7-5bff-9c78-c16f6f491d02 | textbox | Diameter
f7f8a173-a558-5923-a7d9-1a162f16beb1 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
a4a35798-688f-5c26-a9f3-171068ce5c56 | textbox | Date
| checkpoint | Fire Penetration details
8260a946-0032-5987-86f0-0c4c4e5b37aa | textbox | Location
24ef7521-171e-54c4-a90a-778bc48fde0d | textbox | Diameter
39535747-9f19-5110-9935-238d9014c2ba | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
ad7f817e-6504-5877-a7e0-7b9c97fe6075 | textbox | Date
| checkpoint | Fire Penetration details
a88edc6f-34e4-5b4e-8a2c-eea2de1a8125 | textbox | Location
7721185e-a6bd-5ffd-b1bb-13fdd110c0a8 | textbox | Diameter
bd1d93ba-caa9-525a-87e0-85a82d41ce51 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
f985323a-92a0-53b3-88b3-5d3100425f12 | textbox | Date
| checkpoint | Fire Penetration details
aad562c2-a09c-55c4-9aaa-59a256388499 | textbox | Location
eb9a4f92-f5ad-5b6e-8db2-cba3c3cf293b | textbox | Diameter
5e7bb020-ab80-5f0f-a850-b3c4ce5de3d2 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
a8174139-c634-5ada-a321-0f1f918fe3dd | textbox | Date
| checkpoint | Fire Penetration details
f9b54cef-7df6-54cd-bf11-4c48942f75d8 | textbox | Location
94240db7-0e3d-5a5f-9efc-77d4385d05fe | textbox | Diameter
eff74528-c76a-57ad-a6a6-55ca110a3068 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
264a2ed7-c6c0-5e6d-9215-d7e0146ca343 | textbox | Date
| checkpoint | Fire Penetration details
4f9b4667-8108-5707-b86d-c9b1dda76b9b | textbox | Location
4024fe02-83f2-565d-884c-fb8328b56ad1 | textbox | Diameter
72b0f3d3-ef17-501a-abb2-f6001f6a3164 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
a38fb32c-9d76-5eb0-a040-b6041111285a | textbox | Date
| checkpoint | Fire Penetration details
0a13f4aa-5226-5761-ab80-b5919d97ff99 | textbox | Location
f4e94659-048d-5f3d-9b7a-4cf095e7cbae | textbox | Diameter
33cb4215-9dcb-5915-af0e-5fc9ef1fdc33 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
31956444-b8ba-5b7f-8f66-fd1b3ad22dec | textbox | Date
| checkpoint | Fire Penetration details
782b5556-0775-505d-82ee-d98e79aca4f8 | textbox | Location
b0b8e99c-3ca8-566e-89c5-b9bafb919153 | textbox | Diameter
f989e132-db1c-5536-83fe-e38543dd4eb1 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
9396afd5-fb1d-5482-9285-6cec02e4875c | textbox | Date
| checkpoint | Fire Penetration details
f2fc4158-d566-54d1-923f-2cfee8d0d58b | textbox | Location
6090861a-b9a5-5f70-9e62-69930ac39e8c | textbox | Diameter
a2fe72b2-a5bb-5c43-86a8-3de8e60167a7 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
12ed6dd5-c278-5f85-83fe-aaaf50bfb8c8 | textbox | Date
| checkpoint | Fire Penetration details
f5833bd9-f7e7-57f9-a280-f67b66f1e611 | textbox | Location
fd3fe880-955b-5c11-9f18-76bb029f50bd | textbox | Diameter
7585653b-cf01-56d4-9f1f-d14c0c4ae692 | textbox | Wall/Slab Thickness
| checkpoint | Sleeve installed satisfactorily
40e8c950-f04a-5319-8272-1d9e8c956498 | textbox | Date
| checklist | EFPQF19 - Occupant Warning System Install |  | EFPQF19 - Occupant Warning System Install | f454b196-dc5e-4b76-9434-bb7d99af6546
| section | Documentation
| checkpoint | Confirm construction drawings approved for use.
| section | Incoming Inspection
| checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
7717478c-2215-55e7-a959-2006de7ae9b7 | tickbox | Fire rated cable
0833b60d-2672-5333-9338-c3dcf956893d | tickbox | TPS cable
6b9f1baa-1c3e-5524-84b9-142e943d0a9a | tickbox | OWS Panel
903b360b-56fb-58cc-a04d-16faecd77649 | tickbox | Speakers
e07d5617-0e4e-561c-9b91-1af9bb3bdf58 | tickbox | Strobes
71a79ba4-280d-5784-a5a3-f683d3150f49 | tickbox | VAD
| section | Installation Rough In / Fit Off
| checkpoint | Confirm correct cable type run
5aba78af-9e34-58fb-9f0f-df8fab4e5488 | note | Acceptance Criteria - AS:1670
| checkpoint | Confirm cable support/conduit fixings and spacings
200c4f99-5990-5e7f-89bd-9c501f31f1a4 | note | Acceptance Criteria - AS:3000
| checkpoint | Confirm segregation from other electrical services
5ca7c27c-915e-54e1-8d7b-5cdcdf7e1a2b | note | Acceptance Criteria - AS:1670
| checkpoint | Confirm OWS mounted in correct location
| checkpoint | Loop cables terminated to correct output
| checkpoint | Confirm FDCIE cables terminated to correct output.
| section | Sign-Off
| checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
| checklist | EFPQF20 - Calibration Record (x5) |  | EFPQF20 - Calibration Record (x5) | 64f58a4a-74b1-432e-95e6-1ab22fb14aaf
| checkpoint | 1.Calibration Details - Pass once entered
79e4c9de-f48e-583b-b099-8b5dacb2a318 | textbox | Equipment
81db5421-0d13-5b7c-b639-cb2e51d0f838 | textbox | ID Number
6723eb3a-148f-53cf-8d62-6f443fca5fcc | textbox | Expiry (If applicable)
9e8c9648-bf20-58a7-bcb6-ad3204ff50c1 | textbox | Record Number
e7ff90bc-f8ca-5aaa-bb68-91956b13df3a | textbox | Date Calibrated
| checkpoint | 1.Calibration Details - Pass once entered
f799a3ba-57f7-5e57-ab4e-d195392659b5 | textbox | Equipment
229a82ee-ef70-5759-9283-18e98ddc95d7 | textbox | ID Number
5ddff110-3cc1-5cdf-88fe-ec009cdd22f1 | textbox | Expiry (If applicable)
1d966014-8696-5f0e-9163-632499f67c19 | textbox | Record Number
bfb4854e-0bcf-505d-b1bc-fbce9c6e0be1 | textbox | Date Calibrated
| checkpoint | 1.Calibration Details - Pass once entered
f309d07e-5704-51e4-9f40-28c04fc68cdf | textbox | Equipment
1ce939e1-e6b5-59ab-a125-ed083c647d7c | textbox | ID Number
88492c2b-bc08-5f6c-84b3-5e5d734257fe | textbox | Expiry (If applicable)
6adcdf90-7292-53ff-8b4d-9c8c515991e3 | textbox | Record Number
0c2a332f-13d2-5d49-ad47-0150c7e5357b | textbox | Date Calibrated
| checkpoint | 1.Calibration Details - Pass once entered
d7239e41-e1c4-5095-bf00-844cbe96f999 | textbox | Equipment
21c8bff4-18c8-534c-8798-b7ef76dd902d | textbox | ID Number
69feddfd-c3aa-5b12-9c40-37865106d8e8 | textbox | Expiry (If applicable)
b90dfbc3-d712-5d17-84d7-08d86e1a7420 | textbox | Record Number
15ad939d-b591-5929-b062-9dce94690cf7 | textbox | Date Calibrated
| checkpoint | 1.Calibration Details - Pass once entered
2686c055-15ef-5bf3-9dd2-64281755f3a7 | textbox | Equipment
dde83b89-5da3-5c66-ac62-cb918b1f7380 | textbox | ID Number
963d21d6-a426-5dd9-bccd-adac01ce2c94 | textbox | Expiry (If applicable)
6d9ce197-5c05-5dcc-af8a-aa45cb3b4210 | textbox | Record Number
9440565e-2cad-5b89-a463-882cfc44a3b2 | textbox | Date Calibrated
| checkpoint | Sign-Off Records completed
113aa84d-0ab2-5802-8584-c32a28eac751 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
ee4c86db-20af-576f-b956-6b5de2b79e7b | button | Entire Fire Signature Sign-Off added below | Yes, No
| checklist | EFPQF21 - Action Request |  | EFPQF21 - Action Request | 63492cc1-11ce-4df8-be02-0d0e1cd69ec5
| checkpoint | Action Request Details - Pass once entered
2d21dd9b-3979-5ff0-90ca-40011c96cea3 | textbox | Action Request Number
0037d75a-4156-5352-bfef-57d2930960ae | note | This action request is a result of (Tick below)
d15f1365-6417-55b3-9b11-c8c31c8743e7 | tickbox | Audit
e2a9f73b-bd40-58f7-8ff8-e1b5586fbe12 | tickbox | Failure
703bef10-3943-58b2-ba11-38d73e808d15 | tickbox | Non-Conformance
588802a2-eb74-5700-ab9a-3173d741caca | tickbox | Process Improvement Idea
9ad70495-5556-57fd-a907-6b9ae25c675d | tickbox | Customer Complaint
70b16f8c-ab53-54ba-93dc-da85ecc768a6 | tickbox | Corrective/Preventative Action
| checkpoint | Description of failure/Non Conformance/Improvement Idea/Customer Complaint
982c97e0-e68c-55c5-a483-a3e3dd37cd61 | note | Send to Quality Manager for allocation of number and passing to appropriate person for action
0a77b28b-c54b-5e56-9ee2-8a5c5208fe1a | textbox | Details
4ab1ff94-6a61-5107-bc81-a93854a89622 | textbox | Reported By
b04caf38-9ef4-52ff-bcea-98a4c8b9f9f9 | textbox | Date
| checkpoint | Investigate cause and list details
75943bce-fd79-55c4-b438-4b4dc1adcae6 | note | State action when and if there is a deeper underlying issue or problem
206740cc-bcb3-5bf9-ade7-759f83612a64 | textbox | Details
2f68059e-e541-56af-8156-89672c189f88 | textbox | Assigned To
d8fb16dc-6865-5ed5-a9a9-485228e03d87 | textbox | Date of Completion
01fd1c07-7710-5b4b-984e-8fe6d2284aa5 | note | Signature Sign-Off attached below
| checkpoint | List details of deeper underlying issue and corrective action
01f06c33-48e4-50c3-b284-e4374d877065 | note | This section only applicable if above indicates the need
649fc024-fe7f-5f26-8a8d-7b64b4a35679 | textbox | Details
23225667-2ef8-5b94-a06d-ce75583aa65f | textbox | Assigned To
e570cebf-3c74-5086-8e10-bcd4b58ff3c6 | textbox | Date of Completion
ad4631a5-bce7-53e2-97e0-96d1c8a6ffab | note | Signature Sign-Off attached below
| checkpoint | Verification/Follow-up
6f5767d6-992a-50ce-9bc7-e2904afdea47 | textbox | Details
0a36e49e-9b90-5c68-845d-635abd37af93 | textbox | Assigned To
77e164e9-4bc2-56c2-98cc-acc66eec5d17 | textbox | Date of Completion
6a9b9539-794a-595a-97c0-c00a499ce856 | note | Signature Sign-Off attached below
| checkpoint | Sign-Off Records completed
643ef8ca-6efb-55d6-b7e4-ed10f19dd126 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
4f139d5f-5b84-5880-833d-b0faef709abd | button | Entire Fire Quality Manager Signature Sign-Off added below | Yes, No
| checklist | EFPQF22 - Register of Non-Conformance Reports x10 |  | EFPQF22 - Register of Non-Conformance Reports x10 | 43cf1152-5243-4728-9b50-9776a0ce72a7
| checkpoint | Item 1. Pass once entered
919c9bb3-7c14-55e6-8945-2c8f3dc5723e | textbox | Report Number
a2685c2f-1aa5-543c-9bc3-f9add0ac13cf | textbox | Description
71a81f11-c77e-56cb-9591-8af3431b42e5 | button | Non-Conformance rectified (Input date below) | Yes, No
92d5fbb5-df15-57b1-ac72-cbe8a873169b | textbox | Date rectified
5ebbd4cc-d04b-5a8b-b1bd-0ae94ecdd7e6 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 2. Pass once entered
74b4245c-f27f-5521-8a4c-8a96a24c92ad | textbox | Report Number
5e35c4b1-a506-59cb-afa7-4604dd2d85ad | textbox | Description
4c1eb2f7-c31d-53a9-9ab2-daca3c6ec2f2 | button | Non-Conformance rectified (Input date below) | Yes, No
182d72b3-853c-5918-9735-8240c1422cc3 | textbox | Date rectified
5af4d784-165d-5c7f-9679-cc9625a6dc70 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 3. Pass once entered
363948ad-a165-5799-81d7-be3978f23002 | textbox | Report Number
946d03ad-965a-5152-b5e7-68ebe0227acf | textbox | Description
b7b5d390-5fbe-53aa-84c0-aa5c4cb6c6b4 | button | Non-Conformance rectified (Input date below) | Yes, No
60939686-1422-54a4-af7c-fd64cd40e772 | textbox | Date rectified
d27e1abd-7e6c-5f94-b707-eee077d09316 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 4. Pass once entered
83e672d5-a521-5b5c-bb56-e935d7729d82 | textbox | Report Number
190f9eff-3077-51bc-9544-2dfd0c77685b | textbox | Description
93475fcf-c88b-52eb-b6f6-cdce9a5bc8b2 | button | Non-Conformance rectified (Input date below) | Yes, No
27cbe609-fe1b-57bb-9cc6-366170cb827a | textbox | Date rectified
feee5666-6b39-5c21-8a5e-e3975bb1160b | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 5. Pass once entered
d96bcd93-ca54-54eb-8aec-b3d1e24e94ab | textbox | Report Number
1560e905-18c8-5090-bd3e-bcbb0ba709ba | textbox | Description
fd47554c-65c4-53f1-9f0c-ce4b46fbac30 | button | Non-Conformance rectified (Input date below) | Yes, No
314a4403-6f88-5634-98a1-fa26210c86b9 | textbox | Date rectified
0b884e92-baa5-5a8a-b78a-bbdd91759230 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 6. Pass once entered
4aabbf7d-3911-5701-a4ec-22bb3ec623a6 | textbox | Report Number
a6b5274f-6aaf-5a00-8344-8abd5bf2e370 | textbox | Description
131387dc-4ced-501c-9ebb-1daa41e86512 | button | Non-Conformance rectified (Input date below) | Yes, No
dc85696f-cd92-5493-a761-8841f880f4b4 | textbox | Date rectified
6e39bd23-a799-50a4-97ac-3e5feb5727ba | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 7. Pass once entered
b6b62ade-aff5-5a4e-be21-5f4c9eee5f53 | textbox | Report Number
61167a07-257c-5454-9eb0-a0ac7cd17f39 | textbox | Description
8a3b1d03-9d88-5a52-873e-837a7de0cb7d | button | Non-Conformance rectified (Input date below) | Yes, No
b8ae8c3c-348d-5cfc-832d-5f4b66b40741 | textbox | Date rectified
9d69f893-ee70-5f33-98e6-f9184edf6617 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 8. Pass once entered
4e8d5868-e349-5a70-8d44-1f3bfa767494 | textbox | Report Number
2a42db29-f143-53e2-89f9-284754aed84b | textbox | Description
03f9a56b-6b55-5dcb-831a-64926e612b46 | button | Non-Conformance rectified (Input date below) | Yes, No
9035b4ba-7e2d-5f00-874f-241f51554305 | textbox | Date rectified
7ac58185-7c66-58c1-9217-613a7a344995 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 9. Pass once entered
24d7f215-2dd9-5cd7-882c-1e899c66e325 | textbox | Report Number
a87524ee-f682-5581-80be-63d4e3994189 | textbox | Description
7cfebf7b-c6d6-507a-815c-9113eb6ea01b | button | Non-Conformance rectified (Input date below) | Yes, No
f3b63c7b-1056-54a9-ac56-f6320a984a7c | textbox | Date rectified
8e0f4921-a92a-5ded-a98e-a73e40787068 | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Item 10. Pass once entered
f083f51f-d6f9-5db4-ba5f-2279725638cc | textbox | Report Number
0227ceb7-40b1-5969-be89-3bb7cb3347a7 | textbox | Description
d336540e-02dd-5b80-868a-52fe0da715d0 | button | Non-Conformance rectified (Input date below) | Yes, No
14350cf8-32ba-54b5-9247-42d89e25992d | textbox | Date rectified
7e1e35a2-6471-5f41-99f5-aebd8a10aead | button | Non-Conformance approved (Input date below) | Yes, No
| checkpoint | Sign-Off Records completed
9068ba78-6149-5e2a-8373-572bcbc974b7 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
cb4d7f85-0188-5a6a-9974-e03bf0b568db | button | Entire Fire Signature Sign-Off added below | Yes, No
| checklist | EFPQF27 - EWIS Commissioning |  | EFPQF27 - EWIS Commissioning | b24d15dc-b23c-4e74-91db-e26fa49eb706
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Download, fill in and upload completed EWIS Commissioning sheet
| checklist | EFPQF28 - Fire Matrix |  | EFPQF28 - Fire Matrix | 12c9e7c0-4d17-4bfa-8f2e-27e924886ad5
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Download, fill in and upload completed EWIS Commissioning sheet