## Project Structure
Folders | [5 empty] | Checklists
Site QA
| Project Maidstone TMF | Admin Building | Ground Floor | Wet Fire | Sprinkler System Rough In & Fit Off | 03
[5 empty] | Sprinkler Pressure Test | 07
[5 empty] | Sprinkler Control Valve | 04
[5 empty] | Fire Extinguisher | 16
|  |  |  | Dry Fire | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
[5 empty] | FDCIE Install | 10
[5 empty] | EWIS Commissioning Sheet | 27
[5 empty] | Fire Matrix | 28
|  |  | First Floor | Wet Fire | Sprinkler System Rough In & Fit Off | 03
[5 empty] | Sprinkler Pressure Test | 07
[5 empty] | Fire Extinguisher | 16
|  |  |  | Dry Fire | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
|  | SMA Building | Warehouse | Wet Fire | Sprinkler System Rough In & Fit Off | 03
[5 empty] | Hydrant System Rough In & Fit Off | 11
[5 empty] | Sprinkler Pressure Test | 07
[5 empty] | Hydrant Pressure Test | 07
[5 empty] | Sprinkler Control Valve | 04
[5 empty] | Fire Extinguisher | 16
|  |  |  | Dry Fire | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
[5 empty] | FDCIE Install | 10
[5 empty] | EWIS Commissioning Sheet | 27
[5 empty] | Fire Matrix | 28
[5 empty] | MASDS Rough In & Fit Off | 09
|  |  | Stores & Offices | Wet Fire | Sprinkler System Rough In & Fit Off | 03
[5 empty] | Sprinkler Pressure Test | 07
[5 empty] | Fire Extinguisher | 16
|  |  |  | Dry Fire | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
|  |  | Paint Booth | Wet Fire | Sprinkler System Rough In & Fit Off | 03
[5 empty] | Sprinkler Pressure Test | 07
[5 empty] | Sprinkler Control Valve | 04
[5 empty] | Fire Extinguisher | 16
|  |  |  | Dry Fire | MASDS Rough In & Fit Off | 09
|  | Wash Down Building | Wash Down Area | Wet | Hose Reel System Rough In & Fit Off | 11
[5 empty] | Hose Reel Pressure Test | 07
[5 empty] | Fire Extinguisher | 16
|  |  |  | Dry | Fire Alarm Install | 08
|  | Yard Hydrants | Yard | Wet | Hydrant System Rough In & Fit Off | 11
[5 empty] | Hydrant Pressure Test | 07
[5 empty] | Fire Extinguisher | 16
|  | Fire Pump Satation | Pump Station | Wet | Fire Water Tank | 12
[5 empty] | Fire Pumps | 02
|  |  |  | Dry | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
[5 empty] | FDCIE Install | 10
[5 empty] | EWIS Commissioning Sheet | 27
[5 empty] | Fire Matrix | 28
|  | Boosters at Street | Boosters | Wet | Fire Boosters | 13
|  |  |  | Dry | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
|  | Project | All | Wet | Fire Penetrations | 18
|  |  |  | Dry | Fire Matrix | 28
[5 empty] | Fire Electrical Commissioning Test Report | 17
|  | Substation |  | Wet Fire | Fire Extinguisher | 16
|  |  |  | Dry Fire | Occupant Warning System Install | 19
[5 empty] | Fire Alarm Install | 08
[5 empty] | FDCIE Install | 10
[5 empty] | EWIS Commissioning Sheet | 27
[5 empty] | Fire Matrix | 28
[5 empty] | MASDS Rough In & Fit Off | 09

## Checklists
type | name | values
checklist-sectioned | EFPQF01 - Fire Service Pump Install
section | Documentation
checkpoint | Confirm correct construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire service pumps
tickbox | Pump control panels
tickbox | Valves
section | Installation
checkpoint | Plinths positioned. Min height 150mm
checkpoint | Pumps positioned on plinth
checkpoint | Minimum 1.0-meter clearance required around perimeter pumpset.
checkpoint | Suction connected including isolation valves
checkpoint | Pressure relief valves and drain installed
checkpoint | Discharge check valves installed upstream of discharge isolation valve
checkpoint | Discharge connected including isolation valves
checkpoint | Suction and discharge pressure gauges installed
checkpoint | Flow test arrangement installed
checkpoint | Pump start pressure switches installed and wired
checkpoint | Control panels installed and wired
checkpoint | Battery trays installed
checkpoint | Circulation relief piped to drain
checkpoint | Gland drains installed
checkpoint | Diesel exhaust and muffler installed discharging to atmosphere
checkpoint | External bell and strobe installed
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF02 - Wet Pipe Sprinkler Install
section | Documentation
checkpoint | Confirm correct construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fabricated pipework.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Sprinklers.
tickbox | Valves.
section | Installation Rough In / Fit Off
checkpoint | Confirm hanger spacing.
label | 25mm - max 4m spacing.
label | 32 – 100mm - max 5m spacing.
label | ≥ 150mm - max 6m spacing.
checkpoint | Confirm support at change of direction at 1m max.
checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint | Confirm support of armpiece exceeding 500mm.
checkpoint | Confirm first support of range pipe within 2m of mains.
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Confirm sprinklers installed/Fit Off
checkpoint | Confirm sprinkler guards installed.
section | Pressure Testing
checkpoint | Confirm all open ends plugged.
checkpoint | Confirm isolation and drain valves are closed.
checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
checkpoint | Record pressure test results on Pressure Test Form.
section | Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned | EFPQF03 - Wet Pipe Sprinkler Control Valve
section | Documentation
checkpoint | Confirm correct construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Isolation valves.
tickbox | Alarm valves.
tickbox | Pressure switches.
tickbox | Jacking pump
section | Installation
checkpoint | Main stop valve installed
checkpoint | Alarm valve installed
checkpoint | Drain valve installed
checkpoint | Alarm pressure switches installed
checkpoint | Water motor alarm installed
checkpoint | Pressure gauges installed
checkpoint | Jacking pump installed
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF04 - Pre Action - Sprinkler
section | Documentation
checkpoint | Confirm correct construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fabricated pipework - All pipe galvanised.
tickbox | Fittings - All fittings galvanised.
tickbox | Hangers - All hangers galvanised.
tickbox | Sprinklers.
tickbox | Valves.
section | Installation Rough In / Fit Off
checkpoint | Confirm hanger spacing
label | 25mm - max 4m spacing.
label | 32 – 100mm - max 5m spacing.
label | ≥ 150mm - max 6m spacing.
checkpoint | Confirm support at change of direction at 1m max.
checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint | Confirm support of armpiece exceeding 500mm.
checkpoint | Confirm first support of range pipe within 2m of mains.
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Confirm pipework installed fall back to drain
checkpoint | Mains minimum 2mm per 1m.
checkpoint | Ranges minimum 4mm per 1m.
checkpoint | Confirm sprinklers installed.
checkpoint | Confirm sprinkler guards installed.
section | Pressure Testing
checkpoint | Confirm all open ends plugged.
checkpoint | Confirm isolation and drain valves are closed.
checkpoint | Fill pipework with air to 50kpa to confirm no open ends.
checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
checkpoint | Fill pipework with air to 300kpa. Hold for 30 minutes. Pressure loss of 10% (60kpa) permitted.
checkpoint | Record pressure test results on Pressure Test Form.
section | Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned | EFPQF05 - Pre Action - Sprinkler Control Valve
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Isolation valves.
tickbox | Alarm valves.
tickbox | Pressure switches.
tickbox | Nitrogen generator/Air compressor
section | Installation
checkpoint | Main stop valve installed
checkpoint | Alarm valve installed
checkpoint | Drain valve installed
checkpoint | Alarm pressure switches installed
checkpoint | Water motor alarm installed
checkpoint | Pressure gauges installed
checkpoint | Nitrogen generator/air compressor installed
checklist-flat | EFPQF06 - Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist-flat | EFPQF06 - Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (60kpa)
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned | EFPQF07 - Fire Alarms Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | Detectors
tickbox | Strobes
tickbox | Speakers
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint | Confirm segregation from other electrical services
checkpoint | Confirm detector fit off locations
checkpoint | Confirm speaker fit off locations
checkpoint | Confirm strobe fit off locations
checkpoint | Confirm fire interfaces connected to sprinkler installation
checkpoint | Confirm fire interfaces connected to security
checkpoint | Confirm fire interfaces connected to mechanical
checkpoint | Confirm fire interfaces connected to BMS
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF08 - MASDS Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | MASDS units
tickbox | MASDS pipework
tickbox | MASDS Power supplies
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint | Confirm segregation from other electrical services
checkpoint | Confirm MASDS pipework installed as per drawing
checkpoint | Confirm MASDS sampling points size & spacing
checkpoint | Confirm MASDS unit fit off locations
checkpoint | Confirm MASDS power supply fit off locations
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF09 - FDCIE Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | FDCIE Panel
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint | Confirm segregation from other electrical services
checkpoint | Confirm FDCIE mounted in correct location
checkpoint | Loop cables terminated to correct output
checkpoint | Confirm OWS cables terminated to correct output.
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF10 - Fire Hydrant & Hosereel Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Pipework.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Isolation valves.
tickbox | Hydrant valves.
tickbox | Hosereels
section | Installation Rough In / Fit Off
checkpoint | Confirm hanger spacing.
label | 100mm - max 5m spacing.
label | ≥ 150mm - max 6m spacing.
checkpoint | Confirm support at change of direction at 1m max.
checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint | Confirm support of horizontal branch from vertical riser no more than 300mm from riser
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Confirm hydrant height at handle between 750mm and 1200mm
checkpoint | Confirm minimum clearance around hydrant handle 100mm
checkpoint | Confirm hydrant valve outlet not inclined more than 35° from horizontal
checkpoint | Confirm outlet has 300mm clearance for a minimum 225 degrees
checkpoint | Confirm hosereel mounting height 1400- 2400mm to centre of barrel
checkpoint | Isolation valve height is 900 – 1100mm
checkpoint | Maintain 100mm clearance around barrel
checkpoint | Confirm hydrant cap and chain installed
checkpoint | Confirm installation pressure gauge installed at top of most remote hydrant
checkpoint | Confirm pipe identification labels installed
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF11 - Fire Tank Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Tank Panels.
tickbox | Roof Purlins.
tickbox | Roof Sheet.
tickbox | Access ladder.
tickbox | Vortex.
tickbox | Pipe nozzles.
section | Installation
checkpoint | Confirm tank slab tolerance within +/- 3mm
checkpoint | Build first panel ring
checkpoint | Build roof including access hatch
checkpoint | Hang tank liner
checkpoint | Fix tank jacks and lift for next panel install
checkpoint | Install ladder sections at each lift
checkpoint | Fix base ring and remove jacks
checkpoint | Ensure internal tank base free of debris
checkpoint | Install geo fabric to base
checkpoint | Stretch tank liner to tank base
checkpoint | Connect pipe nozzles and vortex
checkpoint | Confirm tank level indicator installed
checkpoint | Confirm tank capacity labels installed
checkpoint | Confirm warning labels installed
checkpoint | Confirm ladder guards and inspection hatches installed
checkpoint | Confirm no leaks when tank full
checkpoint | Copy of Installers statement attached
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF12 - Fire Brigade Booster Assembly Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire Boosters
tickbox | Suction Connections
tickbox | Feed Hydrants
tickbox | Isolation valves
section | Installation
checkpoint | Confirm height of booster outlets between 750mm and 1200mm above standing surface in front of booster
checkpoint | Confirm height of feed hydrant outlets between 750mm and 1200mm above standing surface in front of booster
checkpoint | Confirm height of large bore suction connection between 450mm and 600mm above standing surface in front of booster
checkpoint | Confirm height of small bore suction connection minimum of 400mm above large bore suction connection
checkpoint | Maintain minimum 450mm centre to centre clearance between outlets
checkpoint | Confirm front face of all connections within 150mm of the front of cabinet
checkpoint | Confirm caps and chains installed
checkpoint | Confirm isolation valves chained and locked
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-sectioned | EFPQF13 - Gas Suppression Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fabricated pipework.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Nozzles
tickbox | Cylinders
tickbox | Actuators
tickbox | Hoses
tickbox | Gauges
section | Installation Rough In / Fit Off
checkpoint | Confirm maximum hanger spacing.
label | 25mm - max 4m spacing.
label | 32 – 100mm - max 5m spacing.
label | ≥ 150mm - max 6m spacing.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm support at change of direction at 1m max.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm support of pipework no more than 1m from end.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm support of armpiece exceeding 500mm.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm first support of range pipe within 2m of mains.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Cap installation and perform pressure test
label | Acceptance Criteria - AS:2414
checkpoint | Confirm discharge nozzles installed.
checkpoint | Confirm gas cylinder mounting as per manufacturer instruction
checkpoint | Confirm cylinder hoses fitted to discharge manifolds
checkpoint | Confirm cylinder pressure gauges fitted and indicating correctly
checkpoint | Confirm discharge actuators fitted
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
section | Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), PNEUMATIC TEST – 300kpa 10 MINS - PERMITTED LOSS 20% (60kpa)
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned | EFPQF14 - Water Mist Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Pipe.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Nozzles
tickbox | Valves
section | Installation Rough In / Fit Off
checkpoint | Confirm maximum hanger spacing.
label | ≤25mm - max 4m spacing.
label | 32 – 100mm - max 5m spacing.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm support at change of direction at 1m max.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm support of pipework no more than 1m from end.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm support of armpiece exceeding 500mm.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Confirm isolation and test valves installed
checkpoint | Cap installation and perform pressure test
label | Acceptance Criteria - AS:4587
checkpoint | Confirm discharge nozzles installed.
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
section | Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), HYDRAULIC TEST - 3300kpa 2 HOURS - NO LOSS
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist-sectioned | EFPQF15 - Fire Extinguisher & Blanket Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire Extinguisher.
tickbox | Fire Blanket.
tickbox | Signage.
section | Installation
checkpoint | Confirm top of extinguisher handle ≤1200mm above floor level
label | Acceptance Criteria - AS:2444
checkpoint | Confirm extinguisher type signage located just above handle
label | Acceptance Criteria - AS:4587
checkpoint | Confirm extinguisher location signage located at ≥2000mm above floor level
label | Acceptance Criteria - AS:4587
checkpoint | Confirm fire blanket located in a readily accessible location
label | Acceptance Criteria - AS:4587
checkpoint | Confirm fire blanket signage provided adjacent to the fire blanket
label | Acceptance Criteria - AS:4587
checkpoint | Confirm fire blanket location signage located at ≥2000mm above floor level
label | Acceptance Criteria - AS:4587
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat | EFPQF19 - Calibration Record (x5)
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist-flat | EFPQF26 - Fire Penetrations (x 10)
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checklist-sectioned | EFPQF27 - Occupant Warning System Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | OWS Panel
tickbox | Speakers
tickbox | Strobes
tickbox | VAD
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
label | Acceptance Criteria - AS:1670
checkpoint | Confirm cable support/conduit fixings and spacings
label | Acceptance Criteria - AS:3000
checkpoint | Confirm segregation from other electrical services
label | Acceptance Criteria - AS:1670
checkpoint | Confirm OWS mounted in correct location
checkpoint | Loop cables terminated to correct output
checkpoint | Confirm FDCIE cables terminated to correct output.
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF16 - Inspection and Test Plan Schedule
section | Design
checkpoint | Hydraulic Calculations
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2118
checkpoint | Gaseous System Design
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:14520
checkpoint | Fire Electrical
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
section | Drafting
checkpoint | Drafting sprinkler
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:2419, AS:2441
label | QC Form: Drawing Register
checkpoint | Drafting Gaseous Suppression
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:4214
label | QC Form: Drawing Register
checkpoint | Drafting Fire Electrical
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | QC Form: Drawing Register
section | Samples
checkpoint | Sample Tech Data
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: Specification
label | QC Form: Sample Register
section | Off-Site Manufacture
checkpoint | Fire pumps and tanks
label | Works By: Supplier
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2941
checkpoint | Fire Indicator Panel
label | Works By: Supplier
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1670, AS3000
section | Incoming Inspection
checkpoint | Sprinkler pipe
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2118
label | QC Form: ENT-006 Hydrants and hosereels
checkpoint | Fire pumps and tanks
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2941
checkpoint | Gaseous Fire Suppression
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:4214
checkpoint | Fire Electrical
label | Works By: Subcontractor
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | QC Form: ENT-013 - Fire Detection
section | Installation
checkpoint | Fire Hydrant / Hosereels - Rough-In & Fit-Off
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:2419, AS:2441
label | QC Form: ENT-004 - Sprinkler rough in and fit off
checkpoint | Gaseous Fire Suppression - Rough-In & Fit-Off
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:4214
checkpoint | Fire Electrical - Rough-In & Fit-Off
label | Works By: Subcontractor
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | QC Form: ENT-013 - Fire Detection
section | Commissioning
checkpoint | Fire Hydrant / Hosereels
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:2419, AS:2441
label | QC Form: ENT-006 - Hydrants & Hosereels
checkpoint | Gaseous Fire Suppression
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:4214
checkpoint | Fire Electrical
label | Works By: Subcontractor
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670
label | QC Form: ENT-015
checkpoint | Interface Checks - Mechanical / Fire
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668
label | QC Form: ENT-015
checkpoint | As-Installed Drawings and - Manuals (inc. Test Data)
label | Works By: Entire
label | Entire: Submitted
label | Consulting Engineer: Inspected & Review/Approve
label | Builder: Inspected & Review/Approve
checkpoint | Final Defects List
label | Works By: Entire
label | Entire: Inspected
label | Consulting Engineer: Inspected & Review/Approve
label | Builder: Inspected & Review/Approve
section | Defects Liability & Warranty
checkpoint | Entire to Provide Servicing information for Defects Liability Period
label | Works By: Entire Service Department
label | Entire: Provide
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1851.3
checkpoint | Entire to Provide Warranty Information
label | Works By: Entire Service Department
label | Entire: Provide
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1851.4
checklist-flat | EFPQF17 - Site works completion summary (sprinklers)
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF18 - Site works completion summary (hydrants and hosereels)
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (EFPQF10) date completed
text | Hydrants/hosereels fit off (EFPQF10) date completed
text | Sprinklers control valves (EFPQF03) date completed
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist-flat | EFPQF20 - Action Request Form
checkpoint | Action Request Details - Pass once entered
text | Action Request Number
label | This action request is a result of (Tick below)
bool | Audit
bool | Failure
bool | Non-Conformance
bool | Process Improvement Idea
bool | Customer Complaint
bool | Corrective/Preventative Action
checkpoint | Description of failure/Non Conformance/Improvement Idea/Customer Complaint
label | Send to Quality Manager for allocation of number and passing to appropriate person for action
text | Details
text | Reported By
text | Date
checkpoint | Investigate cause and list details
label | State action when and if there is a deeper underlying issue or problem
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | List details of deeper underlying issue and corrective action
label | This section only applicable if above indicates the need
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | Verification/Follow-up
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Quality Manager Signature Sign-Off added below | Yes, No
checklist-flat | EFPQF21 - Register of Non-Conformance Reports x10
checkpoint | Item 1. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 2. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 3. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 4. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 5. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 6. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 7. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 8. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 9. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 10. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist | EFPQF22 - Site Works Completion Summary (Fire Electrical)
checkpoint | Valves and valve monitors installed
label | Specification ref: Drawing and AS:2118
checkpoint | Pressure switches supplied and operable
label | Specification ref: Drawing and AS:2118
checkpoint | Pressure gauges fitted
label | Specification ref: Drawing
checkpoint | Drains connected
label | Specification ref: Drawing
checkpoint | Statutory Labelling
label | Specification ref: Drawing
checkpoint | Certification
label | Specification ref: AS:2118
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Signature by Builders Site Coordinator - If applicable attach below | Yes, No
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist | EFPQF23 - Fire Electrical Commissioning Report
section | Pre-Start
text | drawing reference
text | level and area
section | Installation
checkpoint | Secure cabinet
label | Specification Ref: drawing
checkpoint | Extinguishers installed
label | Specification Ref: drawing & AS:2444
checkpoint | Signage to meet code compliance
label | Specification Ref: drawing & AS:2941
checkpoint | Hangers location and spacing
label | Specification Ref: drawing & AS:2941
checkpoint | Fire blankets
label | Specification Ref: AS:2444
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist | EFPQF24 - Register of Authorised Signatures
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Pipe, Fittings
tickbox | Nozzles
section | Installation Rough In
checkpoint | Mains, ranges & riser pipes
label | Acceptance Criteria - AS:4587
checkpoint | Hangers location & spacing
label | Acceptance Criteria - AS:4587
checkpoint | Manual and automatic isolation valves
label | Acceptance Criteria - AS:4587
checkpoint | Pressure test carried out
text | Test number
checkpoint | Penetrations sealed
label | Acceptance Criteria - AS:4587
section | Sign-Off
label | By Independent Certifier - Attached below as applicable
checkpoint | Certification
label | Specification Ref: AS:2419, AS:2414
label | By Independent Certifier - Attached below as applicable
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Signature by Builders Site Coordinator - If applicable attach below | Yes, No
button | Entire Fire Signature Sign-Off added below | Yes, No