## Master List Templates
Warnings | Id | Type | Name | Values | Prompting Name | Prefix | Postfix
| 531f2512-5464-5ad5-9375-cf532c19b953 | checklist | Add Fire Penetration Checklist |  | Fire Penetration:
| 41ae2d91-a6ac-52bd-b5d3-a07a5297e838 | checkpoint | Treatment Type
| dda08e40-7dd9-531a-a2a2-34cae406e2c6 | dropdown | Treatment Type: | A1,A2,B,C,D,E,F,G,H1,H2,H3,J,K,M,N1,N2,O,P,Q,R,S,T,V
| 4f16d8a7-40e7-5f2f-8120-ee5531a4c1d7 | checkpoint | Photo of penetration and sticker must be taken
| 6bebe046-7503-5351-8608-2524b69b0fd5 | textbox | Installed by:
| 1f933fe7-d624-5fb9-9385-a1b250206f58 | textbox | Comments / Reasons why cannot complete:
| 0588dd2a-d440-5502-9cc1-2a984d2e6c8d | checklist | Add Project Photos |  | Project Photos
| b3a47312-e99b-57a3-b655-b50313c2200a | checkpoint | Attach Photos and Comments
| 72644a6c-34e1-530c-a7e8-5351e29f25a3 | checklist | Backflow Test Report |  | Backflow Test Report
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| 585974c6-02cb-514b-9e87-5b7ac108700e | checkpoint | Description of property or vehicle
| 91e79822-8dde-5aaa-81f9-ad08e78269e1 | note | The description must identify all land or vehicles covered in the application
| d284e6b4-f929-58b8-94d5-0b328a9cf63d | textbox | Street address (number, street, suburb and postcode)
| 4a848919-0a0e-541f-a59c-c2625acc7dab | textbox | Water authority property service / installation number
| 9dc5fb52-17c2-530c-a000-50835cf81245 | textbox | Water meter number
| eb7d2055-3881-5790-b5ce-e9490cc3e55d | checkpoint | Type of test
| 38a9d5f6-b05a-5498-98c5-4bce9616c23c | tickbox | Commissioning of new device
| 8815a749-aa74-5e87-ab81-c49f5d75a947 | tickbox | Replacement
| 1abf7be1-a725-53fe-86df-cd47f8d1769d | tickbox | Annual
| 8d5f7a6e-e223-5aec-9068-1f6429463172 | tickbox | Repairs
| eabc2bab-5633-5361-806d-02a5912b0381 | tickbox | Decommission
| b0097003-182e-5bee-9086-d9aecfce067d | checkpoint | Backflow prevention device location
| dabf55fa-a50b-5e34-aa0f-f1178dd403b7 | textbox | Location of device (eg: Northwest side of building @ FHR external)
| 0f7e2599-45b6-5ae7-aeff-a9e32a79ea55 | textbox | Mains pressure (kPa)
| 167cc3d1-a150-5625-91b7-98a2ff866f98 | textbox | Time and date of test
| 195a525d-2640-51ef-86c4-48fc1bd7b51f | checkpoint | Main device
| 3f607054-57b2-56fd-b5a3-bdd681f9125b | tickbox | RPZD (E)
| 4451b81e-49c5-5893-a754-f1aabfbea05a | tickbox | DCV (F)
| 62c14501-fdb5-5157-8ba8-a68b3c58c61c | tickbox | SCVT (I)
| 4184f236-50c4-5177-9856-70f36e54b629 | tickbox | Containment
| 279b225c-e44e-5aa9-a574-3ca1b344a48e | tickbox | Zone
| 8eed17e7-55b9-5e08-bab3-9e3a37d050e4 | tickbox | Individual
| c9db3a6a-76e1-5823-bf3f-a52d6a8e51d2 | textbox | Make
| 9457a020-8737-57ff-858b-75daf7e11cfe | textbox | Size mm
| 7b3015ab-e9e0-5035-9c59-7fb0cbf10929 | textbox | Model
| 09e8e5b3-85e2-53c5-885b-451cc7ba6d26 | textbox | Serial number
| a2a6c3c8-2301-5317-91a1-aae5b5896c45 | button | Cleaned strainer | Yes,No,N/A
| 58b40ab6-c938-530b-bc7b-d08afedd0d60 | button | Upstream IV | Leaked,Tight
| e1b28486-56bd-59ee-aa85-4ce4c68719a8 | button | Downstream IV | Leaked,Tight
| 037c66ea-b7d8-5f7f-9602-7acb9d67cae9 | textbox | Check valve #1 (kPa)
| 5ebdaeaf-8ef3-52ef-ba56-5233fb655e6f | textbox | Check valve #2 (kPa)
| afc60cf1-7e69-554c-a659-1b74fa1489e5 | textbox | Relief valve opened
| 0cba4129-b150-5f77-a2f5-6454677b69d6 | checkpoint | Device installation notes
| fdd1c243-3089-52b3-af5c-90b48c74adfa | button | Isolating padlocks installed | Yes,No
| 0344672a-becd-5883-9173-5ac4205d9314 | button | Installation complies with AS/NZS 3500.1 | Yes,No
| 4c6f0025-e719-525b-81ac-ef265d68a9e7 | checkpoint | Test kit
| ae15db3e-6952-5cef-95d1-8ada9b262ca1 | textbox | Test kit serial number
| aadc8d9f-7ee3-56a0-9656-caa41158d9ca | date | Date last calibrated
| b65a095e-ac93-52c6-b0db-1e184e5966f0 | checkpoint | Authorised testers details
| 10c31868-8c42-5421-8cd4-4a74de251d0d | textbox | Testers name
| d5dcd8c6-8dcd-5d91-996f-dfc18faf8517 | textbox | Registration licence number
| a93227d5-1a19-5a17-88a6-a5daeab6485d | textbox | Phone number
| 3d9483e0-efb8-5e50-ad56-69f06fa15b7b | checkpoint-no-value | Licence person
| bdc0c5c3-19f3-57aa-8610-ec2e6d576a0a | note | Full company name - Geschke plumbing
| 10d62ae7-66af-5714-bd04-14174f6d98d4 | note | Licensed tester name – David Geschke
| 01ba6182-b263-5b04-ba70-d2c8917ea205 | note | Licence number -50043
| 53a86f34-72bb-5c37-a036-58be8b5e2241 | checkpoint | I hereby state that the information provided in this form is a true and accurate record. I have tested the above device/s in accordance with AS/NZS 2845.3:2020
| fffa76eb-8043-5d23-b241-64d19d311e66 | note | Note: Failed devices must be repaired and retested within 20 business days as per the Water (Estimation, Supply and Sewerage) Regulation 2014.
| 293ff535-4f83-5dac-b044-caeb4ce197e8 | textbox | Signature licenced plumber
| 7419f545-15ef-5d6c-b003-dab505d3db76 | date | Date
| e73241f0-0943-57bb-8c1c-35dd4ee1589d | textbox | Signature tester
| b8763db2-dd2a-5dee-bc73-25179502e2df | date | Date
| 2f972917-46b6-5d42-9c38-b1f4a8c4815e | checklist | Calorifier Periodic Test Record |  | Calorifier Periodic Test Record
| 8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
| 0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
| 4d261301-279f-5a1b-a15e-d0537ddfff4c | textbox | Date:
| dba1c1fc-6d93-5043-a9d9-9a12062e21a9 | textbox | Inspector:
| cde7680e-612a-54c8-bc92-c714902e5cda | textbox | Location:
| 3e3966d0-ceab-58d6-af96-ca4e44beaab2 | textbox | Serial Number:
| fa42814e-2a58-5250-bd7b-f83c714de0e0 | textbox | Barcode:
| 13950ba2-779b-5de9-afec-b96c073dff89 | textbox | Year of Manufacturer:
| 1e39926d-78b2-5fdd-8414-22da81436b68 | checkpoint | Inspect Tank Connections for signs of wear, rust, corrosion - Inlet, Outlet, PTR, Drain, test/gauge point
| 506eb8f1-d709-57f6-89ba-7b0be67601f0 | textbox | Observations:
| d1b949ca-e98e-5951-8a2e-70fa0f1dc1b6 | button | Are cassette/coil supplies fitted with test/drain points? | Yes,No
| fdf27224-2f97-5fe5-a1f6-f61daf3880bf | button | Are inlet/outlet valves in good order, can the unit be isolated? | Yes,No
| 1ae4f71c-32f8-51de-9eb9-3da43543239d | textbox | Confirm operating pressure through cassette (if possible) |  |  |  | kPa
| dcaec7d2-6049-5955-9043-d1404b59bff2 | radio | Confirm presence of back pressure through cassette (if possible) | Yes,No,Unable to check
| f3b78c01-342b-59d5-a6cb-b64f2cb31fcd | button | Is the lagging in good condition? | Yes,No
| 5f65c3bb-0606-5c35-896a-a84079858286 | checkpoint-no-value | Observations
| fbc91134-60ee-56b8-b7a9-dfd10b03580e | textbox | Observations:
| 038ce57b-101f-5869-b805-0d1438c56502 | textbox | Other Comments:
| 6f002ec6-dce0-558c-8fdb-30e47eb710bb | checklist | Day Labour Docket |  | Day Labour Docket
| bebe4fd5-1509-5079-aaeb-c20fb5659019 | checkpoint | Day Docket Details
| 5c7662b9-6d67-5076-b081-34174d83b306 | textbox | Project Name
| b7294f2b-5cf0-527e-907f-9d7ee8f6d1ea | textbox | Job Number
| 87975a9c-dc3f-53d8-b468-d8bf91570174 | textbox | Site Instruction
| fd3b561b-2193-5a5b-b7e3-1de40a68ce7b | textbox | Geschke Reference / Subject
| 43851586-96a4-59f4-8761-4f20e0c93511 | textbox | Requested by name
| bf76ba28-5cd9-5a95-8e48-c79ba2487249 | textbox | Requested by company
| 2340b828-e42a-5a5c-9fb2-c2644dc2d5db | textbox | Brief description - scope, location, other contractor involvement
| 79e98b40-db35-5c2a-8348-61e9ec1a4f7a | note | Attached - requester signature
| 5993b08a-e5d6-5cb6-b10b-38646360139f | note | Attached - photos before
| cf644e64-73f9-5910-a520-92d88986c35a | note | Attached - photos after
| 3ee5ca91-8046-424c-93a1-a381e9e6ff22 | checklist | Fire Hose Reels |  | Fire Hose Reels
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| 6f7a1d01-22a4-4d31-a99c-f2669a5894c3 | checkpoint | 1.1 Accessibility
| d4e161b5-6bfe-562e-9b32-b84610d8bc86 | tickbox | CHECK that the hose reel is readily accessible with no obstacles restricting its access.
| 7de34c7e-20aa-4e44-87ab-0c5c67ff87fd | checkpoint | 1.2 Signage
| 76232eb3-bc25-5fcc-9c69-26291f99136c | tickbox | Where a location sign is required by AS 2441, CHECK that it is correctly located and visible.
| 8d6d7b7a-c210-4b13-af1f-02b928d41d98 | checkpoint | 1.3 Operating instructions
| 2c8c995f-421a-530c-afb3-01e9dcb4b971 | tickbox | CHECK that the operating instructions are legible.
| 3f281de6-ce82-4225-b8fb-fff482fc07c5 | checkpoint | 1.4 Damage
| 8c1d5f7b-5ab5-5280-82fc-c30369caa544 | tickbox | CHECK for any damage or corrosion of components that could adversely affect the operation of the reel
| 01f5c70a-846b-4ba9-9033-d6923d0fe527 | checkpoint | 1.6 Cabinet
| 9b464f1a-b845-50c6-a8e8-50546061e77f | tickbox | CHECK that all hose reel cabinets are accessible, clear of extraneous materials,clearly and correctly marked and in goodrepair.
| 4846e065-fc23-4bc4-872b-a501a877152e | checkpoint | 2.3 Hose fittings
| c98218a0-6b44-588e-b7e0-f465ede9894c | tickbox | DETERMINE that all hose fittings and connections are tight
| fbc31c10-49c8-4846-ab72-e38b37bbe836 | checkpoint | 2.5 Swing arm
| bc50aa2e-7fb8-5149-b6f2-89c3a7024ef6 | tickbox | Where fitted, TEST the swing arm to ensure it operates correctly and allows the hose to be run off in its intended direction
| d09d4354-af03-4447-8a96-873cdbaf8c19 | checkpoint | 2.6 Unwind
| d59949b4-c9c7-58d3-af5e-40b97cebdc3d | tickbox | With the nozzle closed and stop valve open, TEST that the hose reel can be unwound freely in its intended direction by unwinding at least 5 m of hose.
| 2e4ffa55-0def-4cad-b574-9d9d943563f4 | checkpoint | 2.7 Leakage
| 6ce30553-bc51-5796-be9d-cdef9df2b00f | tickbox | With the nozzle closed, pressurize the reel by opening the stop valve. DETERMINE if there are any leaks from the gland, nozzle, stop valve, hose or any fittings. NOTE: In order to check that there is no leakage of water from any part of the reel waterway, it is recommended that the hose be completely unwound off the reel, so that all parts of the waterway can be examined.
| dad6044c-01a7-46a3-87d3-1d30dea38c8e | checkpoint | 2.8 Flow
| edda791e-f810-5580-87eb-5d3a4daecccf | tickbox | TEST water to ensure it is able to flow through the reel by opening and closing the nozzle.
| dce500e0-69a7-4984-8fde-99e37905a517 | checklist | Fire Hydrant Systems |  | Fire Hydrant Systems
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| f9517f0a-4948-48f4-a893-daa79dec70b3 | checkpoint | 1.1 Water supply stop valves and isolating valves
| 287ac7a3-2b31-5f55-a503-7c82412f0bd6 | tickbox | (a) CHECK all isolating valves including underground key-operated valves are in the correct operating position
| 70e247d6-a181-5570-ac93-e61f86b68934 | tickbox | (b) CHECK all above ground valves are secured or monitored.
| 3eb978e5-2026-4c18-ade9-5bf9949669ff | checkpoint | 1.3 Hydrant valves (below ground)
| e2c9f8c0-1791-5696-8ff9-94c6b4d3b522 | note | CHECK all hydrant valves:
| 0ac08324-19c9-5ae8-bf1c-5ade2e5e8cb9 | tickbox | (a) Are accessible.
| 1ba9b5be-dc75-5292-a68b-bfe1d1f4de85 | tickbox | (b) Blanking caps, where fitted, are in good condition.
| 4f66cdfd-2a5c-53ac-bd63-06b5f053ea6b | tickbox | (c) Check cover plate for ease of opening.
| c25324eb-544a-49c9-b9ea-1ac023ae0a36 | checkpoint | 1.4 Booster assembly
| cbd395f2-7bdf-59f8-97fc-f16d2e1deb4a | note | CHECK all booster assemblies:
| aee7f434-4a1c-54f4-82e0-0c4571621b0e | tickbox | (a) Are accessible.
| bf9a126b-560d-5a87-9686-c24c707f9d8b | tickbox | (b) Hand-wheels are securely fitted.
| d4ad7338-3f5b-55f1-aac4-db93b1a81563 | tickbox | (c) Pressure gauges and blanking caps, where fitted, are in good condition.
| e50d9700-2632-5d34-96d5-2be0709b6a0a | tickbox | (d) For condition of washers on booster assembly connection inlets and replace if signs of deterioration.
| 882f3c5a-394d-5e60-9f54-c1de241907c5 | tickbox | (e) For legible labelling indicating maximum system working pressure.
| 266dbdd2-c285-418f-bc16-67b7accab580 | checkpoint | 1.5 Hydrant and booster connections Compatibility
| 9255a92d-613b-5712-906d-9b4435d71757 | tickbox | CHECK that all hydrant and booster connection points are compatible with local brigade requirements.
| a2a57431-040a-4c53-af2e-9f85d73695e5 | checkpoint | 1.6 All valves
| e3473c17-f805-5394-8c71-8b12b7929b79 | tickbox | CHECK all valves for leaks.
| 0ba5b2bd-aa4c-43a5-a1bd-60c768f59ae6 | checkpoint | 1.9 Cabinets
| 6dd4b736-453b-52a0-89f9-ec9f610e2b3d | tickbox | CHECK that all hydrant and booster cabinets are accessible, clear of extraneous materials, clearly and correctly marked and in good condition.
| d2d9f8e0-df1b-4fc7-b72c-cac5b2ecb072 | checkpoint | 1.14 Block plan and pressure gauge
| 4935ed94-e59e-5d96-9165-a6a052935cef | tickbox | CHECK for legibility and appropriate location
| 345c21d1-424f-5dba-ae13-bf8e3b7d10bb | checklist | GPL QA 6 - Quality Control Pressure Test Report (CNRM) |  | QA 6 - Pressure Test #
| 4114736c-2d08-5a3e-ab7b-04288eaa2c81 | checkpoint | Quality Control Pressure Test Report:
| 051833c0-d828-55cb-bd3a-295bf2ec450e | textbox | Drawing No.:
| 3f1c71e8-017a-5454-87e6-aa06385c9645 | textbox | Rev.:
| 4c88cdf4-804e-5c38-a2d6-d148b42ed196 | button | Test: | Air, Water
| 516ab3e2-4ca8-5170-8733-c1577f68d1b8 | textbox | Section
| 6bd6856b-ce54-5c2b-9250-7fabf9f5e32f | textbox | From
| 3dd04f38-7167-5246-b25e-bfd51dd3fed6 | textbox | To
| c23827ae-a5b3-5051-9f75-39d36d7c28f8 | note | Specified System Working (500 kPa)
| 13ea1030-9d27-560a-82a6-a036831afea9 | checkpoint | Specified System Test:
| d0c4b2a8-e8b7-54b2-b0fe-400e0ac031d3 | textbox | Pressure (1500 kPa)
| 64d6538e-fda9-5a8a-a4c1-b32243784777 | textbox | Duration (2 HRS)
| 1dde2b84-4574-5682-aacc-8adb31a1fda5 | checkpoint | 1st Reading
| bb1127aa-8287-5c46-8edf-6d369c183336 | textbox | Time
| 23be1de7-f15b-522b-b6c4-59d464c5a16e | textbox | KPA
| e8af7a90-b785-5081-be19-c3a00a25b8c4 | textbox | Ambient Temp
| 6a22ddb1-0102-5030-a26b-315ec1394bb7 | checkpoint | 2nd Reading
| 5a945a48-e043-5008-81e0-15cb2722afdb | textbox | Time
| aaf76542-229d-523a-bc78-169bd423bfc1 | textbox | KPA
| baef6a07-6769-5823-99fe-177b3e84bb34 | textbox | Ambient Temp
| 59382eed-be99-5466-be0a-acadd7d1c05e | checkpoint | Test Result - Passed?
| c1e783e5-b505-50ee-82cd-976c6baafa21 | textbox | Repeat
| 627239ce-4e1f-5bd0-8952-6ff14cd6ad69 | note | Company: Geschke Group
| 93aff65f-8183-5dc5-bc5a-3d614b81245e | note | Phone: 03 9798 1619
| f5119d99-9ac2-587d-bcb2-c82eb5c3d065 | note | Address: 45 Pacific Drive, Keysborough
| b4561904-4946-52b5-bd29-5cf0cee0ae58 | note | Project: Centre for National Resilience Project - Melbourne
| bf762d1c-7c93-5397-bac3-3b155ca0b8f2 | note | Principal: Multiplex Constructions
| b66248cf-c4f5-597a-86e7-d3e2293fcb44 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
| ff0a7291-1aca-5c08-9741-7f7859d905f0 | button | Geschke Group Signature Sign-Off added below | Yes, No
| 5af96a66-3772-5957-ae10-3ecdcd385bc0 | button | Principal Contractor Representative Sign-Off added below | Yes, No
| 350a95c8-bd04-5f9f-ac63-562c8e02c209 | checklist | GPL QA 8 Below Ground Pipework Checklist - Water, Recycled Water and Fire (CNRM) |  | QA 8 - W/RW/F-00#
| cb139adc-ed6c-5041-bfab-ea116df4cd15 | checkpoint | Principal Contractor Permits Issued
| 3813c446-1046-52e6-9be4-f549c55f0dce | checkpoint | Set out of trench depths and runs
| 50c368e2-e267-595e-916c-6e77c973ffed | textbox | Drawing & Revision # (or Attach photo below)
| ee172f10-30ea-5fd6-aefc-1d32c9cc0e46 | textbox | Survey setout completed by
| e6275d93-0cbe-50b2-9f34-15f21fe44c66 | button | Drawings attached | Yes, No
| 6645f0da-3658-5774-9c75-0f09dd8e49e5 | checkpoint | Pipes and fittings comply with relevant Authority and Specification
| f1002e73-0ff8-5dd2-89c5-1ea70c2c4b99 | note | Spec#: AS3500
| 8b62a0c7-b7ec-5427-b0f8-2fc82279d6ab | textbox | Materials used
| 8943f3c8-4d92-5c2b-a829-9fe29eed384a | button | Approved by Principal | Yes, No
| 86a29427-9c03-5425-899a-47b775e5623c | checkpoint | Bedding placement and compaction and material meets specification
| 52c24082-91b7-5489-8ffc-c9d211af5440 | note | Spec#: AS3500
| 3f558930-55e6-5fe0-a95a-d97a30badb7e | note | Packing sand encased pipe
| d4397ce2-63ef-5949-b39f-a0c867c3aef6 | checkpoint | Jointing of pipes
| bed56ccc-3194-52c7-b693-0fcc79ce1a2f | note | If either of below are selected, please reference the ITP/Attach below - As applicable
| 5dddb535-0148-5c4b-9da2-f0edb4ce429e | tickbox | Electrofusion GPL QA 16 form
| 91b13bb7-8bfd-59ee-9e69-16e4ae3b1501 | tickbox | Butt Welds GPL QA 25 form
| 98c91393-bc7b-56bd-903c-92654de5d0b5 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
| e6485f50-d5ec-5ebe-af34-ffa6cf627ef4 | checkpoint | Testing of pipes are carried out as required
| 5a2b08bc-3f5a-5cb3-ab1f-7ac0ddbdea9a | note | If below is selected, please reference the ITP/Attach below - As applicable
| 6c2403fb-a2be-5f1f-8a53-2204428a9c8a | tickbox | Water system hydrostatic test
| 849a8533-f3af-5436-b95c-ba0574e1f182 | tickbox | Fire system test completed by Independent tester
| 8e05aa1f-c31e-5c82-b8d2-161ba0421fbf | checkpoint | Additional service within trench
| 55927916-04c9-57fc-9bb6-63901dd4d8bc | button | Are there other services to be installed in this trench? | Yes, No
| 236cf1c2-5cdc-5df9-967c-2bdac58479d9 | button | If Yes have these services been installed prior to backfill of trench? | Yes, No
| c2826327-3b19-53f2-a959-a2bc4336ff03 | checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
| 0060e49b-66d3-5fce-92d2-fd4219b9df37 | tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
| 5357a94b-b5d6-5032-bf6a-f547b524dd31 | tickbox | 5% Stabilised Sand
| 7c195169-860b-52b6-859b-9deb3343bdb7 | note | Detectable marker tape
| 0fc60620-1098-5714-8de7-6668a1f5952d | checkpoint | Temporary cover provided to open drain
| a0d9f762-129d-5d01-bd91-a2a4ed9aff34 | checkpoint | PVC/ Plastic caps to open ends
| fd863736-f39d-5803-86a2-8d75a179c74e | checkpoint | As built information updated onto drawings
| 08501715-e012-50ec-a64c-2c6a44049958 | note | Ongoing
| d2ace5d9-1555-5a52-93b3-28ddd404947b | note | To be provided
| 0a14f2eb-7b7d-53bc-ad06-da0347035191 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
| fbda63b9-65ab-59e8-9f51-ac780beee1e9 | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
| a7ba52d3-362f-55aa-a696-553a38adaf28 | note | Company: Geschke Group
| 3effaf47-2728-5f84-ba24-8add9156f65a | note | Phone: 03 9798 1619
| ec9f75eb-53c1-5118-b321-8a24d3e9e5b0 | note | Address: 45 Pacific Drive, Keysborough
| ac50fdf2-d5ab-53aa-8790-cdffadaf56b6 | note | Project: Centre for National Resilience Project - Melbourne
| c986ec2b-0907-53b2-a369-238937f254a0 | note | Principal: Multiplex Constructions
| 225c7a19-4f0b-574b-8c2c-bf35a51b025c | checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
| 7ed2b8ff-0f3a-5ad0-bc78-414806752c3b | button | Geschke Group Supervisor Sign-Off added below | Yes, No
| 7f06b819-7cf8-5f66-9542-144730c66932 | button | Principal Contractor Representative Sign-Off added below | Yes, No
| 7e187625-9f33-5108-99a7-253473160367 | checklist | GPL QA 8 Below Ground Pipework Checklist (Clyde North PS) |  | QA 8 - BGS00#
| cb139adc-ed6c-5041-bfab-ea116df4cd15 | checkpoint | Principal Contractor Permits Issued
| 401eea44-e9a0-5a7a-be92-9d28944fc126 | checkpoint | Set out pits trench depths and runs.
| 94c74e81-f94a-5ffa-82b3-4ac046c72f4a | textbox | Drawing & Revision # (or Attach photo below)
| 254f0294-bc63-519a-8ff6-b7b0f9302bf3 | textbox | Survey setout completed by:
| 0ce6ed72-a6c8-5b20-9d1b-8d2141922183 | textbox | Manhole Coordinates - enter Eastings & Northings
| b9a077c0-3398-5522-b13f-e0be13de716f | textbox | Starting IL established - enter IL
| 53242941-a47e-5a04-9bec-e7cca2b5ff79 | button | Survey confirmed drain started at correct IL | Yes, No
| 2e7c2cba-7669-5787-824c-fe6fefc058de | button | Drawings attached | Yes, No
| 4462d17e-6ffc-5818-9d3a-23aa6a83929d | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
| 3803bd15-8842-5ec0-94a4-96397169f497 | note | Spec#: AS3500
| ed1f1a09-88b1-58cb-9da1-650bb24d82af | textbox | Materials used:
| 38321f98-f746-5abc-91be-0216a94bb7f7 | button | Approved by Principal | Yes, No
| 60fe69ad-c971-5ea6-82b5-648080b1e0f2 | checkpoint | Bedding material, placement and compaction meets specification.
| 35823503-264d-5c95-b51a-15a3c716bbcf | note | Spec#: AS3500
| 0e21f475-bb39-5885-a22c-b7b6c18e44f9 | note | 7mm Q-Minus Bedding
| f1e7d2c4-f0aa-5642-9733-7036f42a0317 | checkpoint | Laying and jointing of pipes - RL and fall
| bd01fe56-24f5-5377-b58f-dbcd80f4b103 | button | PVC pipe with Solvent welded joint | Yes, No
| 23cc0248-cbac-5b53-9b42-adcc8af1e638 | button | Fall achieved | Yes, No
| 98c91393-bc7b-56bd-903c-92654de5d0b5 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
| 15cedaaa-9380-5d2e-8226-032042d9508f | checkpoint | Hydrostatic tests are carried out as required.
| c4144c95-faf0-53ba-9ef7-475b694a1f5c | button | Air or Water? | Water, Air
| 1859611a-103e-57b2-8edf-378cc57b25d2 | note | Inspected and recorded by Independent Certifier or PIC
| 5175fb60-e3c0-5db8-9eeb-61efe7dbda85 | checkpoint | Mirror tests completed
| e8582c5c-3890-5625-9ad0-0951839d2af4 | textbox | Independent testing company:
| f2776431-47aa-5e24-a01a-eaf3b9ad1af8 | button | Inspection report attached | Yes, No
| c2826327-3b19-53f2-a959-a2bc4336ff03 | checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
| c5d4c043-2d66-564e-af33-92330a699557 | tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
| 42ead38c-253f-5fed-ad28-2c25ffbce6b2 | tickbox | 5% Stabilised Sand
| dc3ac396-f569-533b-8121-bcc1f0051bb5 | textbox | Compaction testing completed by:
| 3b79353f-d2f0-57e8-aab9-d5f41ce1ce08 | button | Compaction report attached | Yes, No
| 24589acd-8747-5b15-8162-b11266c7ec2e | checkpoint | Temporary cover provided to open drain.
| a0d9f762-129d-5d01-bd91-a2a4ed9aff34 | checkpoint | PVC/ Plastic caps to open ends
| fd863736-f39d-5803-86a2-8d75a179c74e | checkpoint | As built information updated onto drawings
| a530020f-1b97-549d-a8d9-d4e4a354f477 | button | Drain installed as per nominated drawing | Yes, No
| 21c7fe6e-6da6-5ffb-9b72-e89c7d17fca3 | button | Invert levels checked by independent surveyor | Yes, No
| 8d454213-8c40-5a7d-ba51-861d1127d644 | note | As Built drawings to be updated as required
| 0a14f2eb-7b7d-53bc-ad06-da0347035191 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
| 9c48bf7d-734b-5b8f-840e-abb6c2fffc88 | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
| a63175ad-7b45-55e8-b6bc-625f3689f22b | note | Company: Geschke Group
| 9af93cf5-cda1-5ddb-ad56-10088992e4bc | note | Phone: 03 9798 1619
| 2acd112f-f7f7-54cc-a424-0a01a5e60c8d | note | Address: 45 Pacific Drive, Keysborough
| 6134e066-2e40-5961-b93c-caa3ee914894 | note | Project: Clyde North Primary School
| 85776876-e27b-57ae-b67a-a2139a60ace1 | note | Principal: Hutchinsons
| b66248cf-c4f5-597a-86e7-d3e2293fcb44 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
| 4627f9eb-3565-5c01-bc63-81473ba55986 | button | Geschke Group Signature Sign-Off added below | Yes, No
| e59a161d-3655-5713-9c75-46aff7d4b825 | button | Principal Contractor Representative Sign-Off added below | Yes, No
| 1905102b-036a-5dfa-8fc1-f797c687e54a | checklist | GPL QA 16 - PE Electrofusion Welding - Field Operational Sheet (CNRM) |  | QA 16 - EF00#
| 286304e4-d491-530e-a879-79048a305a1e | checkpoint | Operator Details
| 097ec0d3-af79-52b5-a2c0-ce18b2b6545c | textbox | Name
| de6205d8-cc62-5001-ac3e-29ca4b3c8bef | textbox | ID No.
| f92140c3-99fc-54cb-a8bc-30e972c8287e | textbox | Company
| bbd8f567-a299-50c4-b574-42d9ca170337 | textbox | Address
| 66b87a78-074a-570c-b59f-8aeb22d53d0b | checkpoint | Welding Machine Details
| 177d147a-7091-5ffe-a940-cdfb71abd639 | textbox | Manufacturer
| e121c23a-9303-5f86-bb6a-a1f034ee6693 | textbox | Type/Model
| 8e41462d-dcd9-5212-aa03-e596653b2843 | textbox | Serial Number
| f59779f6-bda6-5b9d-9356-5b7af1522a1d | textbox | Year Built
| 07064409-656f-5d8e-ba2c-57154117505c | checkpoint | Actual Pipe Size
| 8d0e5696-0801-5a52-9e4a-155d1c29fc6e | textbox | Type
| 53b764cc-6339-5609-b20e-ab314dcdf4e9 | textbox | Brand
| 6e1f364a-2fdc-572f-838d-7d99dcf4965d | textbox | En
| 7adfaf7d-3eb6-5215-b3e2-789c9aa2cff2 | textbox | OD
| b9c69a5f-5397-511d-a582-9ce3a10b4f2e | textbox | Ovality %
| e9e19a09-af9a-5dd9-add0-04e44c20d339 | checkpoint | Fitting Data
| 0f7431b4-8f84-51ce-97b6-df4097d2a549 | textbox | Brand
| d503c2e6-8ad9-5bd3-96f0-716baf2a4696 | textbox | Type (Coupling, Tee, Reducer etc.)
| a1ea026f-d998-57bc-8662-5ada0860350c | checkpoint | Unit Setting
| 47785593-5b30-5119-80f9-462a82573a7e | textbox | Manual
| e1436d7b-3589-5545-8fd6-7c2476e51867 | textbox | Automatic
| ee9dc83b-144a-596a-9418-efc47324c835 | checkpoint | Preparation
| c950d7f3-d89c-5719-bce4-d67a9b387a1c | textbox | Cleaned and Peeled
| 2584d68e-bbb6-5897-917d-d756d3b70386 | textbox | Pipe/Fitting Clamped
| d851523d-87b5-5bee-ad87-5b7e17d639fd | checkpoint | Welding Times
| 0d6d9215-7c1e-5786-b59b-10a44cf69842 | textbox | Joining Seconds
| 0714e89f-63bd-5d5a-bfc9-ebff1405eb1b | textbox | Cooling Minutes
| b99ca8e0-f16a-50d3-8db6-7aba95e6486a | checkpoint | Conditions
| 564224b1-45f2-5473-8886-2f071d244cc1 | textbox | Ambient Temp
| 2cb26253-71a8-5b0d-81ea-7f2ed705c084 | textbox | Weather
| 70bcd800-1461-5128-bfc6-07899cb8ee1c | textbox | Preventive Measures
| a4055e15-3d26-5e25-84be-c62c1b1d24b9 | checkpoint | Power
| 33f0f21b-b023-52cd-b112-2c1ec45f8b6a | textbox | Mains
| 0358a0b3-4bc9-5d5e-aa37-6f2da020b627 | textbox | Gen Set
| f39d7021-bda5-5819-9f3a-a3f34b9c769a | checkpoint | Operator Sign Off
| 56c8c806-0a89-5172-a373-b93cd9bb51aa | checklist | GPL QA 25 - Butt Welding Checklist (CNRM) |  | QA 25 - BW00#
| c7213a29-c0df-5418-aeea-4433c7261ec2 | checkpoint | Operator Details - Pass once entered
| 44d7c879-1d1a-5b36-b0e9-6207dfc67732 | note | Supervisor sign off at completion of ITP after weld #16
| b23ef399-68aa-5c16-9c8e-e8b3e4f29083 | textbox | Name
| 40169759-b361-5c48-bf70-c44b29a25c42 | textbox | Certification Number
| 66b87a78-074a-570c-b59f-8aeb22d53d0b | checkpoint | Welding Machine Details
| edd088c2-967e-5e92-84a2-f8a4a225a6d6 | textbox | Manufacturer
| f370b8e3-6a6d-5991-9f8e-c7f63001dd2f | textbox | Type/Model
| b4f3092a-be96-5caf-9e29-184f50161a40 | textbox | Serial Number
| 48fdf86f-5376-51ba-8147-93525b93b994 | textbox | Year Built
| 4a3d3291-e7cf-528f-bde1-8402008e75b2 | checkpoint | Pipe / Material Details - Pass once entered
| 09b9736d-5f8c-54f3-aa47-c5097f710adb | textbox | Dn (OD)
| be5a7d47-f2c2-58d7-8913-7956418bd66e | textbox | SDR
| ffd297a6-e2db-5df8-b9f8-e0709b71ba58 | textbox | En
| 80d6854c-ea34-53b0-a3f8-685ba4a15523 | textbox | Type
| bee7aa58-5514-5354-a0be-d2bc9fdd8f6f | textbox | Parameter
| edd086df-c691-532c-90e7-47dce1b3c2b2 | textbox | SLP
| 9f2761aa-8a73-5515-b310-d91badbb3e05 | textbox | SHP
| e71ff371-f48f-5062-87da-78bd07f92a6c | checkpoint | Weld #1
| bc9699dc-d883-5094-9413-e1b5f91e0284 | textbox | Time
| a5f789cc-0b93-5d51-894c-78351e87151a | textbox | Ambient C
| d3862185-3d9f-5cbf-97d9-425b3e7f438f | textbox | Heater Plate °C
| 3022b20b-c03d-50ca-9dbf-a87820c5e367 | textbox | Drag Pressure
| 2a86c27c-dcec-52ac-9eff-888cd9c6366a | textbox | Bead Up: P1 (Kpa/Bar)
| fc34da7b-21fd-5fe4-aee9-95fa4d715ef2 | textbox | Bead Up: t1 (Evidence)
| 4c67a8e3-f27c-5b18-b3ba-37b244244251 | textbox | Heat Soak: P2 (Kpa/Bar)
| d6087c2f-8cf8-5eb2-abf3-d07fb8860c77 | textbox | Heat Soak: t2 (Seconds)
| d2835900-c38c-5372-8b19-c4b96226f082 | textbox | Change Over: t3 (Seconds)
| ff91d7a6-0916-5784-bf6b-38a069cbdd37 | textbox | Pressure Up: t4* (Seconds)
| d17e9c85-aaac-55e2-bc01-1e71654b31d6 | note | *t4 not applicable for SHP situations
| a7fe786c-ca25-5480-9dc0-09eaa3719874 | textbox | Weld and Cool: P3 (Kpa/Bar)
| a9d53b7f-948e-5ade-8bc9-e1b9b92d59d6 | textbox | Weld and Cool: t5 (h:m)
| 2901ef98-4121-5d15-bf6a-407dfc3bb05b | textbox | Rough Handling: t6 (h:m)
| 17f654c9-1910-5662-a723-b954b77a6ec2 | textbox | Bead Size: Min
| 6a5990c2-ad5f-5178-8465-09691228d4ca | textbox | Bead Size: Max
| 16dcda18-5d2f-5137-bf2d-ffa117a92f7c | textbox | Comments
| 78bd4022-85ef-528f-9710-e8dcfe288456 | checkpoint | Weld #2
| db5a88b3-f59f-5d19-95ad-39edcb36ba85 | textbox | Time
| 9f6e314f-b9d1-5e02-875b-7711078bc7ac | textbox | Ambient °C
| 10cc49b0-9696-5afc-92ab-f35bf2b2a8e3 | textbox | Heater Plate °C
| 35a69463-0fa8-5beb-a482-29cf93f1fc79 | textbox | Drag Pressure
| 3ce4dc43-3b58-5c5d-82ab-9806ef45d250 | textbox | Bead Up: P1 (Kpa/Bar)
| cf9edc1b-4477-5ae3-9db9-dfb264387374 | textbox | Bead Up: t1 (Evidence)
| 7c53d10d-8088-5228-9d6b-5335f3cd6fab | textbox | Heat Soak: P2 (Kpa/Bar)
| 2792973b-b159-5383-81d0-8550c3771314 | textbox | Heat Soak: t2 (Seconds)
| e8a01855-a16b-59ed-8bd7-9a8f37f2aa6b | textbox | Change Over: t3 (Seconds)
| 03ba0a96-99e8-5ee2-89b1-f52fc60f3eb2 | textbox | Pressure Up: t4* (Seconds)
| 0485d298-0310-5829-ad4a-8a49ea9897fe | note | *t4 not applicable for SHP situations
| 576d831c-63c6-56bf-9768-1fdbc270ddd5 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 8439de80-939f-5b71-8f53-673e9926aea9 | textbox | Weld and Cool: t5 (h:m)
| 79b49a2f-2c17-523b-8f9d-ed6b93695393 | textbox | Rough Handling: t6 (h:m)
| 96640787-0b60-5287-bb3b-0e38ee84dd93 | textbox | Bead Size: Min
| da32795b-8891-5466-b216-6b0881a0e9dc | textbox | Bead Size: Max
| 53e70b26-5b42-5157-8c92-7298e0cac710 | textbox | Comments
| 81962d2c-449e-5f3b-93ad-c2c6413fd600 | checkpoint | Weld #3
| 015428cb-d388-5c67-a3b5-c9ceec1b2e98 | textbox | Time
| 0ee00dbe-bb17-59a8-bd7a-054af1783557 | textbox | Ambient °C
| 42476481-8dbd-5b2d-bc2b-72ea07b8f348 | textbox | Heater Plate °C
| e08fa52e-94fa-56a3-a942-5f5080832deb | textbox | Drag Pressure
| e9a5fa43-2b91-5ab5-9c6a-39ae3b212057 | textbox | Bead Up: P1 (Kpa/Bar)
| 8f1a028a-da38-51d5-868c-5d50649ffaca | textbox | Bead Up: t1 (Evidence)
| f7b4ba53-9219-5aba-98fe-b9687818f78e | textbox | Heat Soak: P2 (Kpa/Bar)
| 72923825-7c13-5eb0-b3a2-437be2f4137a | textbox | Heat Soak: t2 (Seconds)
| 4229b6ee-115f-5f3e-8b64-1e742ec88bd4 | textbox | Change Over: t3 (Seconds)
| 5881296c-000c-51c0-900a-9e7ae47d0758 | textbox | Pressure Up: t4* (Seconds)
| c45bd83a-7060-5265-b7e3-e4f6bf16e2f5 | note | *t4 not applicable for SHP situations
| c8b50c41-1781-55dd-ad33-4b99314781af | textbox | Weld and Cool: P3 (Kpa/Bar)
| 78b755d9-f656-5778-ae41-77c9164e42aa | textbox | Weld and Cool: t5 (h:m)
| 25ed308e-fc54-5666-9cfb-a754447435c1 | textbox | Rough Handling: t6 (h:m)
| ae72f6d7-e35b-5163-9f12-83260195b1f1 | textbox | Bead Size: Min
| 6facc60e-5cf1-5145-abbf-8a4888784618 | textbox | Bead Size: Max
| af73991a-c771-53fa-826d-f116da3f2ce1 | textbox | Comments
| a6f39b8c-b097-5c0f-b4d3-7405b4c9e4d0 | checkpoint | Weld #4
| a1c872aa-1822-5b3f-8c50-9aa7d3c89aef | textbox | Time
| 0f6e4430-d60f-5d40-83fe-ad9396dc71f3 | textbox | Ambient °C
| a950a88a-d855-55e1-aa6d-a48de5d73132 | textbox | Heater Plate °C
| 3d2e3ab1-efa5-5f42-8b61-edcaad61ec1e | textbox | Drag Pressure
| 41157317-a7f0-5046-b4a5-77cd1a2ace69 | textbox | Bead Up: P1 (Kpa/Bar)
| c7bedc0b-1173-5889-b044-96e00ebc4bfb | textbox | Bead Up: t1 (Evidence)
| 2c2e97cc-826b-5073-93bb-7e4f93977063 | textbox | Heat Soak: P2 (Kpa/Bar)
| bf54adc8-609b-5bec-94ba-3b5f5fdc57c4 | textbox | Heat Soak: t2 (Seconds)
| d3b17e7e-8561-54a9-bee8-a1ed3e4b815a | textbox | Change Over: t3 (Seconds)
| 0153c081-77b8-5fac-a33c-2691c92b6e32 | textbox | Pressure Up: t4* (Seconds)
| 7de83c66-f8d5-515c-9f73-fe6a53ffa61a | note | *t4 not applicable for SHP situations
| dd2a3ebe-285b-55ca-8f7e-e52336fce2cc | textbox | Weld and Cool: P3 (Kpa/Bar)
| 36b316a5-ffdc-502e-9e6b-f85b7bad2ab2 | textbox | Weld and Cool: t5 (h:m)
| 661818dd-34b1-5b94-9ef5-2f58facd3ee2 | textbox | Rough Handling: t6 (h:m)
| dfd95ce4-6379-5fe0-9745-d7fbf2793278 | textbox | Bead Size: Min
| 9f8fff29-68aa-5eae-b513-1bea33fcb476 | textbox | Bead Size: Max
| 880ccdb5-9bef-55da-b9b7-8a1ed8c9f8d1 | textbox | Comments
| a23fae6e-0eed-51e6-ae33-5dbfa70bc336 | checkpoint | Weld #5
| f3f65331-8e1a-5213-8a5d-c18e5619c628 | textbox | Time
| d40f374b-af87-5067-b050-34e226919ea7 | textbox | Ambient °C
| a693cd62-55f3-5634-a695-ace08d9e2f17 | textbox | Heater Plate °C
| b56db16f-81a9-5124-81f8-adc9fadfd405 | textbox | Drag Pressure
| f7a7b288-12ba-5142-8a7e-89263401b31f | textbox | Bead Up: P1 (Kpa/Bar)
| c894dcad-ead6-5fa7-84ec-9ba62914f18b | textbox | Bead Up: t1 (Evidence)
| c149edc7-b516-5e8e-b11a-242b0cdd4694 | textbox | Heat Soak: P2 (Kpa/Bar)
| fa48e0ba-1901-51f0-89a9-9f61c0f903f3 | textbox | Heat Soak: t2 (Seconds)
| e476b0e9-8da6-5cae-865c-710fc50da6cf | textbox | Change Over: t3 (Seconds)
| 085c7e77-4ead-5a1f-bfdb-bcf3211caf41 | textbox | Pressure Up: t4* (Seconds)
| 306dd4b9-cee9-5e9b-8bb1-fdadb46b189b | note | *t4 not applicable for SHP situations
| 785dfa4d-2420-50ee-9230-52bc2dd0d974 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 29172ad1-0286-582c-8744-ab069d4bdf03 | textbox | Weld and Cool: t5 (h:m)
| 9012091b-1dc9-50da-b1c8-d05ed2dbc6ab | textbox | Rough Handling: t6 (h:m)
| 9c6bcb1c-0014-514c-b928-d923f7dd2c6f | textbox | Bead Size: Min
| 2a2c24c5-6623-5c4d-ba0c-26235e75a16d | textbox | Bead Size: Max
| 2175de99-d1f3-528a-8c87-f43e420eb9e5 | textbox | Comments
| c0b57b2c-b434-5982-a98c-3fe0084a4091 | checkpoint | Weld #6
| fa0e65f9-2bdb-5cf8-8f82-47617c27bb27 | textbox | Time
| d9d1df85-213e-567a-b549-b8d8e35d6a33 | textbox | Ambient °C
| ccc234fa-b311-5644-bb09-82a96eff62d3 | textbox | Heater Plate °C
| 0ebc8625-552d-5e1e-93dd-83a09ec4ec4d | textbox | Drag Pressure
| 353f27f6-5a69-54df-bd95-93e5f1691409 | textbox | Bead Up: P1 (Kpa/Bar)
| 8aa4baf4-ea05-52f5-9d96-73da03648eb3 | textbox | Bead Up: t1 (Evidence)
| 0a092e83-ab13-51af-a34d-f17ecd48fbea | textbox | Heat Soak: P2 (Kpa/Bar)
| c9c54f24-8b24-57f1-b64a-b08dd235359d | textbox | Heat Soak: t2 (Seconds)
| 0c731826-8f00-5a5c-93e7-374ae5a249bd | textbox | Change Over: t3 (Seconds)
| 8d6b54a5-705f-519a-b3d7-0ba2d2a0724f | textbox | Pressure Up: t4* (Seconds)
| a4054f94-95db-56a0-adbb-2356dc6dc68b | note | *t4 not applicable for SHP situations
| 953b9474-5383-51af-9b4c-e116781f332c | textbox | Weld and Cool: P3 (Kpa/Bar)
| 66f411e1-09cd-5a3f-82be-1e4326867536 | textbox | Weld and Cool: t5 (h:m)
| 69148c02-bc23-5f16-9f8e-4bcdf0436a0f | textbox | Rough Handling: t6 (h:m)
| a81eec86-89a3-5a54-98c6-645c62182771 | textbox | Bead Size: Min
| 84472177-d48d-5686-b4d8-af32152f2ecd | textbox | Bead Size: Max
| 13d0760d-d0b0-5de2-8dc1-00ce570e811a | textbox | Comments
| 1efd1e6f-db6d-5dd7-9d7b-afcc272782e3 | checkpoint | Weld #7
| 72534e0b-f47d-5ddd-a43f-51d911cf26d7 | textbox | Time
| 5c57eda9-9557-5b5d-83ae-485262c17583 | textbox | Ambient °C
| 647a07b9-768f-58c5-a7fd-377b33b52295 | textbox | Heater Plate °C
| 22043f46-0d3c-5e4c-a0fc-2b46933d9bbf | textbox | Drag Pressure
| 018fb432-7e4f-53a1-a13e-4ac6f79dd926 | textbox | Bead Up: P1 (Kpa/Bar)
| c5fdbd0b-aa4e-5bb0-a74b-fab198cd5ecc | textbox | Bead Up: t1 (Evidence)
| 69abe86b-d4cd-5405-9507-41d83946fb3f | textbox | Heat Soak: P2 (Kpa/Bar)
| 9099abc3-d722-5b86-ae61-99b47037920f | textbox | Heat Soak: t2 (Seconds)
| 72de2874-b613-55f5-99c2-8090803573ba | textbox | Change Over: t3 (Seconds)
| 935657d6-8d6c-5e7b-9d66-5d3c61d02c57 | textbox | Pressure Up: t4* (Seconds)
| e64ce176-71ac-5979-867b-c38acbd1f710 | note | *t4 not applicable for SHP situations
| 25c04a4c-547e-5b12-8ad8-4eda968ea28f | textbox | Weld and Cool: P3 (Kpa/Bar)
| d06a4478-3217-54fa-89eb-0b28b9f93415 | textbox | Weld and Cool: t5 (h:m)
| 82a7f4a5-18b4-51d9-b9a8-1cdf23cc44b5 | textbox | Rough Handling: t6 (h:m)
| ff220b77-58a5-5389-aa45-77ac8517ccdd | textbox | Bead Size: Min
| 1a0f7413-b0d3-5ebb-834f-59b9dee4b31a | textbox | Bead Size: Max
| 5fed14d7-5ce5-592b-832d-91f5a64450c0 | textbox | Comments
| bad1edd9-cd38-500b-8c1b-43d3c3e966ff | checkpoint | Weld #8
| 274dad37-befa-5d0a-8623-105e6f8833f6 | textbox | Time
| 2ab6ac9a-6c9a-566e-a603-b80dcbbc92fd | textbox | Ambient °C
| b9e91781-d1bb-5395-b2cb-481c722b10c8 | textbox | Heater Plate °C
| ee64d230-19ca-531e-b842-79804e63cbb1 | textbox | Drag Pressure
| 28fcd57d-2e36-5455-afb4-a142b5e89438 | textbox | Bead Up: P1 (Kpa/Bar)
| 2d9404b0-c70f-5d39-987b-9784b1febc0a | textbox | Bead Up: t1 (Evidence)
| 8437d4cc-baac-5971-a765-37dc3309bfd1 | textbox | Heat Soak: P2 (Kpa/Bar)
| 1fd0dd9f-995e-50c2-b061-f1cfe01a5347 | textbox | Heat Soak: t2 (Seconds)
| b2f95662-0ce2-5ed9-a8c0-f60a277ad967 | textbox | Change Over: t3 (Seconds)
| 502a599a-2426-5765-be22-2db409661576 | textbox | Pressure Up: t4* (Seconds)
| 47d63e45-d059-5689-9c76-5f8265a90b3f | note | *t4 not applicable for SHP situations
| 47fabe00-6779-5270-b047-05156c3edf78 | textbox | Weld and Cool: P3 (Kpa/Bar)
| ced994f5-4c73-55f3-8306-3d20db5e9b7d | textbox | Weld and Cool: t5 (h:m)
| c5912eba-cfc2-5437-9321-df95f41f18bd | textbox | Rough Handling: t6 (h:m)
| 87457dd5-45ef-5adc-afec-9e0dfc6c762a | textbox | Bead Size: Min
| 7d1e343c-de68-5016-82ee-a1f19c6222f3 | textbox | Bead Size: Max
| e0b6a4f9-8d07-52a1-a97a-6c527f09a7aa | textbox | Comments
| 90fb97d3-fac4-5796-8508-34edeb78c0be | checkpoint | Weld #9
| 16132c2a-e8fa-5cd8-a245-f0308f43eec7 | textbox | Time
| a56ab8fb-d061-512f-bab6-f6ce2c3845f6 | textbox | Ambient °C
| e37e13c4-a9f6-5b8a-b4f7-23e70daf30b3 | textbox | Heater Plate °C
| 8d4c5a28-8f84-5d91-950c-a5fa0e53d9f2 | textbox | Drag Pressure
| 3708746e-9901-5ac7-86a8-78ec5c221357 | textbox | Bead Up: P1 (Kpa/Bar)
| fb4427a3-dfc6-5449-9802-00fde745f070 | textbox | Bead Up: t1 (Evidence)
| 433dea68-3549-5b90-b84f-f93ee0749d21 | textbox | Heat Soak: P2 (Kpa/Bar)
| d3d2bff1-00f9-58ee-9c79-4d57739ad201 | textbox | Heat Soak: t2 (Seconds)
| 155ec100-336b-5848-87e4-f74fc64a28c1 | textbox | Change Over: t3 (Seconds)
| ef37aed3-7f4f-5134-9946-f462f4517e50 | textbox | Pressure Up: t4* (Seconds)
| 27edcd4d-bafa-5558-8a8c-9176ab0a9a10 | note | *t4 not applicable for SHP situations
| 0f3bd917-62cf-5b3b-8861-d62938cc4b41 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 265a157c-383e-575b-ae0a-9d53e929eee2 | textbox | Weld and Cool: t5 (h:m)
| 10062f86-0fd8-57d0-a346-ce4050ad84b5 | textbox | Rough Handling: t6 (h:m)
| b184f9b8-7607-5fe3-9df6-5ff48d9e3308 | textbox | Bead Size: Min
| 88d034a7-8db2-5ec0-8c34-14362c77accc | textbox | Bead Size: Max
| 571d0dc0-90ca-5223-81b5-b3f4df83b60f | textbox | Comments
| 6bc85937-b931-5303-a9ed-97ac74d4f879 | checkpoint | Weld #10
| 8bee8241-ab4b-5845-a4ab-bde02d4aa22f | textbox | Time
| dc40e920-3714-5299-ab03-d35009c92fac | textbox | Ambient °C
| ac15f54a-ff39-5552-b610-e30311e75cbb | textbox | Heater Plate °C
| e54af82d-344d-5373-ad31-c758fbb660ca | textbox | Drag Pressure
| 1216cff5-9d89-5642-8509-f08bf9ce8dc0 | textbox | Bead Up: P1 (Kpa/Bar)
| 400c2711-d973-55d1-a866-c34eba6d17bf | textbox | Bead Up: t1 (Evidence)
| cfc1d5b5-0d1e-53fd-9b40-b10ef47bd485 | textbox | Heat Soak: P2 (Kpa/Bar)
| 9fe67302-1749-5c29-8a39-9522b10809d9 | textbox | Heat Soak: t2 (Seconds)
| 981ad4fd-0ec8-5ca8-bd8a-1800bbadfbdd | textbox | Change Over: t3 (Seconds)
| f84604a5-003e-5a76-b6bf-612ebeccd287 | textbox | Pressure Up: t4* (Seconds)
| 3bb3dd65-7aeb-53a7-8d52-a1cfd6dc8658 | note | *t4 not applicable for SHP situations
| d89c2c20-3245-52a0-9b88-e59a79ebba6b | textbox | Weld and Cool: P3 (Kpa/Bar)
| 9f5a8fda-1e96-5bea-8f3b-4ea10e34b9b9 | textbox | Weld and Cool: t5 (h:m)
| 00e859fc-097d-5eba-ba5f-49d2f0ac122d | textbox | Rough Handling: t6 (h:m)
| beffe23b-dc28-5e2b-9364-be5ebc4967ba | textbox | Bead Size: Min
| b905df13-4289-5845-a507-afbb497a8030 | textbox | Bead Size: Max
| 3946f003-652f-5ce4-9f3e-c15d7143dc9d | textbox | Comments
| 463bc4c9-ea34-53c0-92ca-2d00f59c91b3 | checkpoint | Weld #11
| 8ebde7b5-91f8-516c-81db-51cc2733b492 | textbox | Time
| a8313b6e-e31c-5944-b641-c53a4078a825 | textbox | Ambient °C
| 5bf6c438-fcda-5c62-95d4-f6fc270edc1b | textbox | Heater Plate °C
| bb207a4f-51f7-52ef-8639-3ee952551455 | textbox | Drag Pressure
| fdf43002-1e47-552f-875a-2f1ac3efb462 | textbox | Bead Up: P1 (Kpa/Bar)
| 60bf122a-39db-5134-ab14-d2f31ef330d5 | textbox | Bead Up: t1 (Evidence)
| 25cbcf31-affa-51ea-b325-0bc5525419cb | textbox | Heat Soak: P2 (Kpa/Bar)
| f584ee40-6190-5886-80ed-4166a957652b | textbox | Heat Soak: t2 (Seconds)
| 5929bb70-5c74-5346-a5ea-f32a5b67d6bb | textbox | Change Over: t3 (Seconds)
| 2f933de2-4334-5515-a5b8-f4705a3751f4 | textbox | Pressure Up: t4* (Seconds)
| 56a23d36-3614-5913-9ed4-daf97e63238b | note | *t4 not applicable for SHP situations
| cb43f9d4-78b0-5871-87f0-55ebc2f3630e | textbox | Weld and Cool: P3 (Kpa/Bar)
| b37fca65-c217-527b-a8c3-87637cb253b8 | textbox | Weld and Cool: t5 (h:m)
| f5b1176a-327a-5c8d-bcdf-1c82e4af79a2 | textbox | Rough Handling: t6 (h:m)
| a8bbe734-0635-51d6-a987-d55ff1868d2d | textbox | Bead Size: Min
| 75456cfb-219a-5f36-9b7d-9b9e2c21f6a2 | textbox | Bead Size: Max
| 513fa48f-5876-535e-a8cd-66059049ac20 | textbox | Comments
| e7525f04-8570-5c1f-b681-a4625b5f59d9 | checkpoint | Weld #12
| 5f9c345b-e9ee-52d7-9811-2de7302d56ef | textbox | Time
| 010c4aab-e8ff-5a68-a3c1-a569d26bb5c3 | textbox | Ambient °C
| c21c7b0c-56c1-5eb7-a372-f97bd6e9a541 | textbox | Heater Plate °C
| b726c46e-3c6a-5d7e-9e80-bf498b35f233 | textbox | Drag Pressure
| f349474d-10bb-5ddb-b868-cce6ca61a5ff | textbox | Bead Up: P1 (Kpa/Bar)
| 08589c14-3c73-5a4d-b420-11ec652801f9 | textbox | Bead Up: t1 (Evidence)
| ae726fcf-631a-5b8b-b176-c78072517f2f | textbox | Heat Soak: P2 (Kpa/Bar)
| d334f903-c4df-5f19-b71a-9a0d7f9c7d1a | textbox | Heat Soak: t2 (Seconds)
| 3bb2306e-452e-5072-aeb0-25cc4ff6cfba | textbox | Change Over: t3 (Seconds)
| e986d37f-37f8-5116-b2d2-f4bece218624 | textbox | Pressure Up: t4* (Seconds)
| 8bbd2649-fd80-5458-b46f-5748a5199426 | note | *t4 not applicable for SHP situations
| bd2b75c5-2033-5087-ba77-68e32c800876 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 13d917ab-89cc-581c-8698-daf3de9d2a9e | textbox | Weld and Cool: t5 (h:m)
| 8078879e-06cb-5bab-8a0a-0f6e955c8074 | textbox | Rough Handling: t6 (h:m)
| 7052ddf3-0a9f-50b5-abef-85a8bf841f9d | textbox | Bead Size: Min
| c1c01554-51a0-530c-8047-43a573263991 | textbox | Bead Size: Max
| 2b0b1306-8d5f-5048-b129-fd4c311cd308 | textbox | Comments
| 45ed4156-e665-5b1e-b249-f74563d124ba | checkpoint | Weld #13
| 15820892-f921-5d4a-8075-9b6c488da292 | textbox | Time
| 622e32c0-ea88-5002-a4d2-d9c66c57849e | textbox | Ambient °C
| e42b61c6-52b2-505b-a53e-577d5ef968c9 | textbox | Heater Plate °C
| 1b15f9ed-67e3-550d-a0a6-21d5bbb0dd36 | textbox | Drag Pressure
| ab1a1da7-98a2-53f3-8ebc-cf57434f5fb3 | textbox | Bead Up: P1 (Kpa/Bar)
| 78196ca7-5756-5328-8f91-74d2b5f91243 | textbox | Bead Up: t1 (Evidence)
| f23afc03-d167-5aed-b330-9afa46d663ef | textbox | Heat Soak: P2 (Kpa/Bar)
| 1e82fa4c-fa0e-5d92-90e1-7f333331237a | textbox | Heat Soak: t2 (Seconds)
| e8925f81-4b0a-543b-9375-23226f4d1b0c | textbox | Change Over: t3 (Seconds)
| 742b7902-23bd-5875-a08e-28c5bbd27756 | textbox | Pressure Up: t4* (Seconds)
| eceb0d9a-bc24-5429-be5c-940fdab26695 | note | *t4 not applicable for SHP situations
| 89a34668-060b-574d-a965-3462d5fca248 | textbox | Weld and Cool: P3 (Kpa/Bar)
| df7236b2-0f1f-5672-976a-2ad9b3b952f2 | textbox | Weld and Cool: t5 (h:m)
| 0d9eb930-0761-51b3-8c4d-b2ef3cbc0e7f | textbox | Rough Handling: t6 (h:m)
| be7bf59e-c85b-579c-a7c0-f69ae72affac | textbox | Bead Size: Min
| 0775c384-d271-5139-9092-b0633ea75c9e | textbox | Bead Size: Max
| fed8a321-9eaa-585e-b120-63f5d2c8c4de | textbox | Comments
| adb2bbc6-dc2d-5a47-ad7f-0666e9952b6f | checkpoint | Weld #14
| 27b5eedd-7caf-540d-ab11-d5455fb39f3d | textbox | Time
| 29c592dd-5875-545c-a9d0-ba738074c3b7 | textbox | Ambient °C
| b428a4f9-49de-53c8-b78a-cb0374f2e627 | textbox | Heater Plate °C
| 80116684-c48e-5f2e-a39a-f44942e87224 | textbox | Drag Pressure
| 8a876851-757e-5741-816a-8fe68e9ed2c9 | textbox | Bead Up: P1 (Kpa/Bar)
| e670de68-384b-5b88-8223-d2fab1af53ff | textbox | Bead Up: t1 (Evidence)
| 0f967ffa-2854-5ed3-a22d-ea050171160d | textbox | Heat Soak: P2 (Kpa/Bar)
| 271a0516-51d7-56d3-8c1b-92c404d71caa | textbox | Heat Soak: t2 (Seconds)
| 9a1a7d93-a538-527e-a05f-5cb9e6c7c6c2 | textbox | Change Over: t3 (Seconds)
| 57f63711-0020-57ba-bf50-4e3073557fc2 | textbox | Pressure Up: t4* (Seconds)
| 7a34e075-f760-53c3-b5d0-0b1a46891395 | note | *t4 not applicable for SHP situations
| ec038315-82ac-5ac7-b63d-d8ed22cdc960 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 40eedc13-f853-5dac-b5a8-9a0eb295aee3 | textbox | Weld and Cool: t5 (h:m)
| 6ee05c5d-7a78-5986-b40f-7607a2628c2a | textbox | Rough Handling: t6 (h:m)
| dfd7a32f-d205-513f-9fd8-6cd7a53e4533 | textbox | Bead Size: Min
| be33065a-d29e-5cc5-bdf0-8fa3ebca5ed1 | textbox | Bead Size: Max
| 8f91594b-31cd-554e-a4eb-386071a25460 | textbox | Comments
| e85e5fa6-a6f6-507e-8211-309716054b4e | checkpoint | Weld #15
| 823901fb-cd82-51b0-8da9-14b172d9730e | textbox | Time
| f230f40c-69cd-597a-a692-e66c6cbe2806 | textbox | Ambient °C
| 651e35cb-9b70-55c6-a166-b4339b28c968 | textbox | Heater Plate °C
| 7ac64a49-0d58-5a38-afbd-7f115d5193a3 | textbox | Drag Pressure
| 0ae7b457-4c86-5bac-92a8-dddb7416f114 | textbox | Bead Up: P1 (Kpa/Bar)
| fac2e750-0c48-585a-9417-c432529d7cd6 | textbox | Bead Up: t1 (Evidence)
| f57c0ab1-d558-59de-9a77-a974ea7f1c70 | textbox | Heat Soak: P2 (Kpa/Bar)
| efef8bc4-2135-58eb-9b19-eb4c3796c734 | textbox | Heat Soak: t2 (Seconds)
| ed8d8a25-171f-5d3d-a431-46e8789b7794 | textbox | Change Over: t3 (Seconds)
| b3e2cf93-8b33-53d1-984d-ea9a9af1091d | textbox | Pressure Up: t4* (Seconds)
| abc329ab-4a52-5603-8035-cab2d9442a60 | note | *t4 not applicable for SHP situations
| c3b70a2e-94cf-515d-929f-18d3f1652fca | textbox | Weld and Cool: P3 (Kpa/Bar)
| 201aa927-0344-596a-8c7a-ab12f77bab40 | textbox | Weld and Cool: t5 (h:m)
| 9c1ea621-62f5-5ac4-9119-9f288b36f03d | textbox | Rough Handling: t6 (h:m)
| 5f156729-65ef-5bb7-b375-a48045a69847 | textbox | Bead Size: Min
| 8b036248-97f2-5b82-ab47-a7d93cf68ed6 | textbox | Bead Size: Max
| ef54206a-6e5e-5ac6-8966-6bd840ac5902 | textbox | Comments
| a23b6c60-dd48-5595-878d-1652527cff42 | checkpoint | Weld #16
| cb7e30bb-1ea3-5659-b39a-ddfb73c13094 | textbox | Time
| 7c1c0478-bad1-526e-a4dd-c36fd39029d2 | textbox | Ambient °C
| 54518f66-a1aa-5b11-afe4-786d65cc4d4c | textbox | Heater Plate °C
| fd488c9e-4267-5f38-84f2-1b38b7aec339 | textbox | Drag Pressure
| 3a5446f0-336c-57d0-bc30-12220733111d | textbox | Bead Up: P1 (Kpa/Bar)
| b95427be-ceff-57e7-9368-ac2bf9e1709d | textbox | Bead Up: t1 (Evidence)
| 3958ba65-a478-56b7-9da3-49589ba1588d | textbox | Heat Soak: P2 (Kpa/Bar)
| d3486e1a-ba04-58d7-808f-45d2fb242aa5 | textbox | Heat Soak: t2 (Seconds)
| 0b012023-3d28-527d-b440-ccb69069211d | textbox | Change Over: t3 (Seconds)
| 3536e1ea-0890-5820-aaf4-badb9d97e8bc | textbox | Pressure Up: t4* (Seconds)
| a111c964-dbf0-5b3d-ba0b-c1af772800fa | note | *t4 not applicable for SHP situations
| 359cb985-ecae-5163-a73b-bccacb97054d | textbox | Weld and Cool: P3 (Kpa/Bar)
| 631bab58-74c8-5c92-94e8-abf885e2c196 | textbox | Weld and Cool: t5 (h:m)
| f9253546-3165-5d9a-8523-b2d08e1cb6da | textbox | Rough Handling: t6 (h:m)
| d22fa83f-c592-562a-bcbe-2787a4a1dd3c | textbox | Bead Size: Min
| 10761089-62d5-5b1a-8a4f-a7d484465c7a | textbox | Bead Size: Max
| 8981e3d5-706a-5660-a632-4fece9d21cab | textbox | Comments
| 0a14f2eb-7b7d-53bc-ad06-da0347035191 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
| f95258a0-3fce-5428-999f-18fcdaa3c6d2 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| 292f79e9-689a-501f-87cf-eb8a74f8582f | note | Company: Geschke Group
| 3ca598eb-b490-5a4e-a613-c17b9eff9dbe | note | Phone: 03 9798 1619
| 593d1a7a-6074-5741-9a88-11200b7a2ed7 | note | Address: 45 Pacific Drive, Keysborough
| d74baf01-2f63-5a5f-9654-8e6754bc0bee | note | Project: Centre for National Resilience Project - Melbourne
| 78eae871-9eb8-5bcd-934d-dec293f08d1d | note | Principal: Multiplex Constructions
| 11ace98b-461a-57fe-bd72-6823b0efb559 | checkpoint | Foreman Sign-Offs completed - Click to Attach Signature(s) below
| 5c8b5786-3cb0-50a9-b372-390ed17c7106 | note | Operator Sign-off added to each weld above as required
| a5196735-7d03-5e01-9a5b-e7516e15cb36 | button | Geschke Group Signature Sign-Off added below | Yes, No
| 225ec6c5-bdfe-5291-acc6-cc7b6e81591f | button | Principal Contractor Representative Sign-Off added below | Yes, No
| b250bf99-1054-592d-983f-b87decdd8e0e | checklist | ITP - Fire Sample Excl. Backfill ACOR Review |  | ITP - Fire Sample Excl. Backfill ACOR Review
| 4736d901-b2be-5732-9bfa-11380f738534 | checkpoint | 1. Approve specialist subcontractor
| 0d3c38a4-c71b-5749-bd7a-d2067c70fa6b | note | STAGE / FREQUENCY: Prior to awarding subcontract
| 75c6828a-f808-58d7-82db-5697b120d741 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
| 20972fc4-f613-5c36-9fdb-b3b59709138c | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
| a4fb11ec-1b4f-5858-9dcb-e6dd466fe793 | note | INSPECTION / TEST PROC: Document
| 76315aac-a835-5cce-b888-18c1af84f9bc | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| c9d4499c-c8f2-513e-9a20-71e1a0029c07 | note | HOLD OR WITNESS POINT: Hold Point
| c09248f9-3cd0-5955-bdba-e77f96f2c162 | signoff | hold point
| 05b29a37-3c3c-5d86-8867-cf4598ae7f3c | checkpoint | 2. Approve Samples
| 5ab0487f-5938-5e09-9b34-d720cf6d1755 | note | STAGE / FREQUENCY: Prior to ordering materials
| e1fc6389-0ab8-5094-8af7-67349927b449 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| db57c290-2a20-56b4-aaa9-755f95ac8543 | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
| 4b66d20e-9e42-55bc-9c26-9d2428688d41 | note | INSPECTION / TEST PROC: Document and Review
| 322fb1ac-3495-5a30-baaa-976941d34e5b | note | INSPECTOR / APPROVER: Engineer. Geschke
| 84ed3336-74ab-5ca7-bdb4-a0df8c14ed95 | note | HOLD OR WITNESS POINT: Witness Point
| 6409b5d7-f8dd-5c02-94a1-87f4c2593ac0 | checkpoint | 3. Approve technical details
| 5090bd27-d972-5bdc-8459-8f7791ad1747 | note | STAGE / FREQUENCY: Prior to ordering equipment
| c1d89ecf-ddec-575c-ab99-87602db0e5fd | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| fe526921-c7c2-572e-8998-3a8f7826deb9 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
| 24a06e65-0f13-592c-9854-5c3509888e52 | note | INSPECTION / TEST PROC: Document and Review
| 7059248c-f190-5668-b990-3f778ed2d7a1 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 04ecf25a-0a35-57ce-9cf3-70802e480fad | note | HOLD OR WITNESS POINT: Witness Point
| 71cbc1bc-bc6c-5c19-bacc-a5d0cabd0294 | checkpoint | 4. Approve shop drawings
| 6673dca8-e50e-5990-a4e9-9f301517e35d | note | STAGE / FREQUENCY: Prior to commencement
| c0fd2d03-3ac2-5872-80c4-b2dcacc5d7fd | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
| a4f7401d-931a-501a-be52-2bf58b0e39ac | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
| 20931c45-aace-563a-9e25-5c0cc1d7cf36 | note | INSPECTION / TEST PROC: Document and Review
| 382c42b2-01da-5f2e-9238-15bc5d4c6553 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 4dc5d5ed-f7ae-59fd-a74f-f428649b195e | note | HOLD OR WITNESS POINT: Witness Point
| 50faf94e-eb3e-5602-a601-f61b18ec3476 | checkpoint | 5.01. Check set out of excavations
| e0acea45-616a-5d20-abf3-dba65f5b042d | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| a932003a-f1bf-513a-b076-8b23298cd31d | note | RECORDS: 'Before' Photographs
| a79969d1-d2cd-57b2-91b9-63f50ca78916 | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
| 56168f84-e867-536a-9e9e-5bbab2444c7b | note | Minimum falls
| 17ce3ec0-095e-5c3b-9cf5-1a3632d43397 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
| 8699d099-999d-5719-a9cf-58f918d3e344 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
| 8ee7adfd-c94f-5661-b4bf-ab906a836200 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 281c4987-bc8e-5f15-ba4b-b2db2af87cb6 | note | INSPECTOR / APPROVER: Foreman. LLB
| 0c5ce48a-dc88-5912-9bee-29d674923416 | note | HOLD OR WITNESS POINT: Witness Point
| 8fa3fa97-e6a9-5421-8492-2f2e31abedb6 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
| 71c8a347-006d-5365-921e-9e44cac8f33a | note | STAGE / FREQUENCY: Each delivery
| fa12bde1-b518-5a46-89fb-babef13fed3c | note | RECORDS: Delivery dockets name, signed and dated by Geschke
| 75a9ac72-65df-59f8-a87b-1dc38aa71ffc | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
| 88d997a5-c74c-55b8-9020-e5a9719ec44a | note | Grade or class matches design
| 277a7844-7c60-57bd-94c4-452897bfdacb | note | Size and thickness matches design
| b5479f1a-3776-560d-a901-d9889f2b3009 | note | Supplied items are free of defect
| ea7e015a-c83a-552f-9c0d-968fe651d66c | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
| 06c249c1-3742-581d-8a31-b45fe282e379 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 77b7e683-16d3-5cb3-9302-2e8b72c7d516 | note | INSPECTOR / APPROVER: Foreman. Geschke
| e66c018c-79b9-5978-a06a-2076f7f2d16d | note | HOLD OR WITNESS POINT: Witness Point
| 826c348b-bad5-5765-9c45-21db995ae514 | checkpoint | 6. Check deliveries of materials
| 2f388e97-f458-5990-ac7a-da231124e69c | note | STAGE / FREQUENCY: Each delivery
| 8c81df1f-03c4-5c8c-a51f-ca446c042651 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
| 0234a70d-72a5-5b1c-ab04-379851f9b6c5 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
| 1dbc0549-5aa5-5312-9f5f-6e50d9973200 | note | Grade or class matches design
| 35679dd2-c8f2-55f3-b15f-9c20d6e079b4 | note | Size and thickness matches design
| b8c8695c-09ec-5b0a-9d4a-b45492a3260e | note | Supplied items are free of defect
| 41fbd58e-c3ff-5994-90cd-c9c715e4f4cf | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
| 084bc65c-4140-520d-a2ab-a7251fdeadf7 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| a13da82d-004c-5fce-b969-d4faf5713e02 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 81bacfe1-6058-5740-b33c-72d3dbd2774d | note | HOLD OR WITNESS POINT: Witness Point
| 6943e8e0-5771-5e26-91b2-eb3a4a9a7a94 | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
| 60895360-5cfc-5d73-9de5-e88b964b0c2b | tickbox | Standard Bead Profile Test
| 95d4ef6d-8a3b-5c71-ad65-a13b083249fb | tickbox | Standard Destructive Tensile Test
| 4143487f-54d2-5389-8e31-8da8c04c360a | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
| a5c4b1c7-e5f9-5f8c-8fec-21b87eda5943 | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
| 9c36cef4-e0e3-59c5-b7dc-c54f2b84876e | tickbox | Gasketing Record
| 0c353f24-9b49-5251-b8bb-8712d155134b | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
| 0828e881-42ec-5630-860e-3762aa3431d3 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
| b1fa0dd3-9b24-5405-a6b4-7da09ed5cc83 | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
| 905b9be1-1a56-57ba-b057-a0050ec4adb2 | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
| ed02e191-a017-520c-8d81-fdb97bb87741 | note | Bead size to be uniform, symmetrical and free of contamination and air.
| 933b0fa1-7688-5a51-90a0-35e19fe810e8 | note | Bolt tightening to be completed using the correct sequence
| 7fbdcfea-dd60-53b4-8fc6-53e1cd61464c | note | Final torque on bolts shall not exceed manufacture specification.
| c5675546-2d97-512f-a5de-cc8a6bc262eb | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
| 072bce59-c557-56d4-b177-af0e6872d5fd | note | INSPECTION / TEST PROC: Document and Review
| 164562ef-e4ee-5470-a15d-7cc3efe78814 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 9471ad2b-4d7b-5e53-b569-df92a175db39 | note | HOLD OR WITNESS POINT: Witness Point
| b3e2f606-7dab-5250-80fc-1db9ce52e67a | checkpoint | 7.02. Check below ground pipework - pipes and fittings
| 5a939c8d-0d66-5415-b8e7-d6b4fe7ac149 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
| 7f370901-a89e-58bd-b582-ed3d2a6439d0 | note | RECORDS: 'During' Photographs & As-built Survey
| 42e5f3ca-069d-53d3-b262-742bc6754cc6 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
| 55b187a5-80e2-5a56-9936-f2b685de3206 | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
| 12c202c4-6038-5ce0-9d83-a18c23f3be6c | note | Joints, fittings and connections match design
| ca9466ae-3314-55d7-b4f5-5dd465d6798e | note | Alignment and position are as drawn
| 63f29fab-a3c5-57d9-aa59-b8dc74013ec8 | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
| ed337331-cad1-56dd-acd5-86f1c084d7c6 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 0a34d3c5-b440-5ab1-8f12-f35365de11d2 | note | HOLD OR WITNESS POINT: Hold Point
| fe1faa23-074e-5fa0-94bc-5f97e1955949 | signoff | hold point
| 1edd3296-b94c-508a-94c7-b1d314d2bda4 | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
| 47d52fd1-27b3-5ab6-b0eb-2c39ca430feb | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling.
| 55136b13-f324-50db-8b1e-1c022e499c61 | note | RECORDS: Standard Pressure Test Certificate QA.6
| 5c3f464d-f212-5da3-9587-31953a60efa3 | note | SPECIFICATION / STANDARD: Clause 2.3 of WSA 03 1999 & Clause 18.3 of WSA 03 1999
| 3d0555c6-9314-5704-a4d3-996c25cbe080 | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,700kPa pressure for two hours
| 04030b35-344f-542b-8954-6a10388cb659 | note | Pipeline is flushed free of all debris
| d5bda7d9-9af6-535c-9571-51ede6e82d5f | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
| e33d1928-937b-58a0-9b54-7b55108e936e | note | INSPECTION / TEST PROC: Document and Review
| 6e7d6f3f-0543-5437-8864-79833c91af1d | note | INSPECTOR / APPROVER: Engineer. Geschke
| 627dd8a3-8f2f-507f-9c87-375e4bf99c00 | note | HOLD OR WITNESS POINT: Witness Point
| ac79eb2f-166e-54ab-b592-d07ae349d2bf | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
| d7819289-6285-525c-9c56-51ae41faef53 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
| 2a073575-1b65-56ab-9360-68bf67bc7f5d | note | RECORDS: Photograph
| bac1b115-ff41-529c-978e-25403beda668 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
| 222792b8-72b8-51ce-85e3-53bffbb14a4d | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
| c08b5490-31be-596a-8548-d38174fa41e2 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
| 7d826ade-6c04-56c3-9881-1d8f47d39829 | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
| cbe2f887-5f8a-5cb3-b77b-dcf9505e9312 | note | INSPECTION / TEST PROC: Visual Inspection
| 421812d5-ab50-5a21-9773-bdeb970d995d | note | INSPECTOR / APPROVER: Foreman. Geschke
| eb35a14a-3205-517d-891a-06a236881dd6 | note | HOLD OR WITNESS POINT: Witness Point
| 25dace2d-13db-5790-a72a-101165116a2a | checkpoint | 9. Check Completed Surface - Make Good
| d678afab-c36f-5430-afcf-ef2ade7da5d6 | note | STAGE / FREQUENCY: Prior to practical completion
| 2a16d9cc-2a78-5e36-99de-9e2da10a631d | note | RECORDS: 'Upon completion' Photographs
| faa3f6d2-55e6-5166-9e9d-fce58af6cfda | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
| 178bad91-4874-50be-8589-bacc16ae0be4 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 25cd5b2f-31ed-51fc-8328-4efeaefb5f08 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 2d97ab42-0b6a-58d9-bdd9-00ae28360671 | note | HOLD OR WITNESS POINT: Hold Point
| 14256e6a-38b4-59ab-982a-4effc4e691dd | signoff | hold point
| 224cf3b9-e2f4-5d92-be53-2204ae1399ed | checkpoint | 10. Obtain as built documents
| 5fb79931-9b5e-5fc0-aca3-2decb8ed9a67 | note | STAGE / FREQUENCY: Prior to practical completion
| 8f369965-ed84-51c4-8206-7a5d30af97dd | note | RECORDS: As built documents
| b9fb074d-7c8d-5509-a1a8-64cad860e6c7 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
| 0f1934b3-17b6-5db0-ba60-0f229a73e3d3 | note | INSPECTION / TEST PROC: Document and Review
| 3c3fd0da-9236-56e0-9e91-68084838a9db | note | INSPECTOR / APPROVER: Engineer. Geschke
| 16c6f24f-a9b2-5a3d-b638-2254ea0a39ab | note | HOLD OR WITNESS POINT: Witness Point
| 2c843525-d62b-5943-9f3d-f7411623ad28 | checkpoint | 11. Obtain operating and maintenance manuals
| 649fe952-9b2d-5420-b002-2836eadc61bb | note | STAGE / FREQUENCY: Prior to practical completion
| e5bc5bf4-2775-5de9-8e12-1c7cf330c43f | note | RECORDS: Manuals
| daca2fdd-9cf8-55bc-a4c9-856fa7f6faa6 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
| fdc35e53-7276-55ea-93d4-37c6317da508 | note | INSPECTION / TEST PROC: Document and Review
| d8e5342d-64bb-555a-941c-db52e4a757be | note | INSPECTOR / APPROVER: Engineer. Geschke
| b9f4ef64-6cb1-5f7e-8bdb-b8e81d4a39ad | note | HOLD OR WITNESS POINT: Witness Point
| 6cd2caf4-ce8c-575b-889a-87eb55ca2094 | checkpoint | 12. Obtain guarantees
| 68138bcf-120f-5833-833b-875c080e3e2c | note | STAGE / FREQUENCY: Prior to practical completion
| 5a2046d0-5b70-5fb1-a51b-f6fc3c6bfc37 | note | RECORDS: Final commissioning checklist
| 5fbd5ec1-d140-5cac-99da-963966f3d4e0 | note | INSPECTION / TEST PROC: Document and Review
| ca326e45-62d2-521a-bfd5-5257d705091b | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 21b6d0f6-ed36-5073-82fb-1ae271ef93d9 | note | HOLD OR WITNESS POINT: Witness Point
| 39811f35-6c89-570e-b376-7f275f736051 | checkpoint | 13.01. Check above ground Hydrants - Signal and Flow Test. Standard Flow Test
| 291a3373-562c-5228-8bb2-45ef34769d41 | note | STAGE / FREQUENCY: Upon installation / one test per hydrant
| 19758053-533b-5c48-894a-814309e29b68 | note | RECORDS: Standard Flow T est Certificate QA 6E
| 4451bffc-0b1c-554c-98c1-2df94a103050 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
| a62a56eb-87d1-5dfa-985b-4e76da52dead | note | ACCEPTANCE CRITERIA: Hydrant flows up to 30l/s
| 89d2dc4c-fa94-5dc3-a8cc-ba457ed103f2 | note | Hydrant tagged and signed
| 2516b1f8-0500-5ca4-8833-e6e4f873f2ce | note | Bollards installed
| 67d7203c-1a2c-51c3-9554-cd17d87d3e58 | note | Signal sent to Building Sub FIP
| de7c92f6-833e-58d4-b4b3-d5d2bba74411 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| dd1e30c0-1016-5e76-b327-70a6c0c28146 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 63088761-164c-55fa-a1be-c94a8d77eb5e | note | HOLD OR WITNESS POINT: Hold Point
| cfa37905-8e79-5127-a801-a6efc8d5689d | checkpoint | 13.02. Final commissioning & inspection & independent report
| d1a4f79a-4798-5403-84ea-2e023bd9b78e | note | STAGE / FREQUENCY: Prior to practical completion
| 7f49657a-c896-5d54-9b80-af8dca574b85 | note | RECORDS: Final commissioning checklist Independent Report
| 813a4a22-5337-56a1-b94c-fa50f04b2e77 | note | INSPECTION / TEST PROC: Document and Review
| e74b5748-d979-57a4-b25d-68594e678588 | note | INSPECTOR / APPROVER: Independent Engineer. Geschke
| 727c7099-d267-57a0-930f-12c1f1d9137f | note | HOLD OR WITNESS POINT: Witness Point
| d21fdfee-8d79-5572-8a0c-26b6b64de2a9 | checklist | ITP - Gas Sample Excl. Backfill ACOR Review |  | ITP - Gas Sample Excl. Backfill ACOR Review
| 4736d901-b2be-5732-9bfa-11380f738534 | checkpoint | 1. Approve specialist subcontractor
| 9ea333d3-e251-5d91-92b8-dad13708f963 | note | STAGE / FREQUENCY: Prior to awarding subcontract
| db29dbe5-4805-510b-b2ec-d2a30b655f30 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
| 1c4b1048-ebae-5109-a1c5-fe60645fbf2f | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
| e31dcff0-918e-5359-a33a-725e87ce2cf1 | note | INSPECTION / TEST PROC: Document
| 54786f94-4968-5706-9dfc-90f6bc42bd42 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 1968fce4-cfdd-5243-8107-c353fe77934e | note | HOLD OR WITNESS POINT: Hold Point
| c09248f9-3cd0-5955-bdba-e77f96f2c162 | signoff | hold point
| 05b29a37-3c3c-5d86-8867-cf4598ae7f3c | checkpoint | 2. Approve Samples
| a93ea1b4-701b-535b-9c01-43e7ab1a9918 | note | STAGE / FREQUENCY: Prior to ordering materials
| 7ecc9f59-fce2-5244-bb31-d7fec10b85e5 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| 28720d0c-e982-5af4-9a71-f347010b9e5a | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
| e7c5dce6-a1f3-5422-85cf-274e6aa390ac | note | INSPECTION / TEST PROC: Document and Review
| 2eb15892-2d82-5d46-8848-9b1d434386f6 | note | INSPECTOR / APPROVER: Engineer. Geschke
| d4e71e4b-9c57-5f88-b57b-def6006b50c2 | note | HOLD OR WITNESS POINT: Witness Point
| 6409b5d7-f8dd-5c02-94a1-87f4c2593ac0 | checkpoint | 3. Approve technical details
| 310221d0-4deb-56e2-8118-33ac56ae503f | note | STAGE / FREQUENCY: Prior to ordering equipment
| ac421837-e634-5a54-b0b3-e93a99f8ea90 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| 7c99100d-b225-5c5d-aa42-8e9886c96d19 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
| 372aee8d-8958-5010-ad4e-800ce2166e33 | note | INSPECTION / TEST PROC: Document and Review
| 01233f45-471e-5ad5-ae0f-e615f419e673 | note | INSPECTOR / APPROVER: Engineer. Geschke
| cf143dd5-5046-581e-ba5a-48524941a517 | note | HOLD OR WITNESS POINT: Witness Point
| 71cbc1bc-bc6c-5c19-bacc-a5d0cabd0294 | checkpoint | 4. Approve shop drawings
| a635d0eb-72f5-5b4d-86fa-cdceb5f37c1b | note | STAGE / FREQUENCY: Prior to commencement
| 9bbcc727-acb0-532e-a758-723be6b0e041 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
| f9bd7c30-8a20-527e-aebe-c5e9f658262c | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
| 49ae78bb-3cc9-5a75-a0fc-cfe5f90211fc | note | INSPECTION / TEST PROC: Document and Review
| ef74c504-43a8-5ec2-aab4-b7cbd50ad9c9 | note | INSPECTOR / APPROVER: Engineer. Geschke
| da543418-5452-5297-a6b6-07d5dd811239 | note | HOLD OR WITNESS POINT: Witness Point
| edbb8d0b-000b-5199-94aa-a2f24d6c6f2e | checkpoint | 4.01. Approve shop drawings
| 82862675-b97b-5bac-9c51-9f072b1bad27 | note | STAGE / FREQUENCY: Prior to commencement
| 47fdcf3d-957a-5d5c-a04f-00fac1813bab | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
| 23a863b3-aadd-5150-a889-91d84f7c034e | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
| 03314676-f5d5-59f9-bf48-9443cdb774ed | note | INSPECTION / TEST PROC: Document and Review
| 6bf4621a-27ee-507f-b0e3-b6176c0cedbc | note | INSPECTOR / APPROVER: Engineer. Geschke
| d352d4ad-56fd-5d0b-9a74-d5f40a09c74b | note | HOLD OR WITNESS POINT: Witness Point
| 442fbcfe-2ce4-5dfe-bf6f-30750d329a9b | checkpoint | 4.02. Approve Method of Work Plan
| 896940f3-2274-5a00-ab32-0907bc7323ef | note | STAGE / FREQUENCY: Prior to commencement
| 6ba3f27a-acb9-5b3c-8caa-5e277fdba933 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.26.10
| 6cd650c0-8012-54b3-932c-d83ccb57a5d2 | note | ACCEPTANCE CRITERIA: Construction staging plan to execute the works
| a249a61c-b1e7-59dd-b701-254616e06e0a | note | Pipeline construction schedule
| 00060701-cebc-567d-9d7d-84ecd0a9721f | note | Nominate temporary supply
| 10edf26a-9eb0-5054-b514-b07708334551 | note | Nominate safe work measures
| 6ac82613-5a71-5f2c-b95f-728896c68bfe | note | Nominate notification procedures
| af8a8354-8e2f-5224-bade-75e31b731e15 | note | INSPECTION / TEST PROC: Document and Review
| 84672809-2759-5d8e-8067-eb989c0af23d | note | INSPECTOR / APPROVER: Engineer. Geschke
| a32f3aac-8b57-5fff-a2b9-06f58cb03cb3 | note | HOLD OR WITNESS POINT: Witness Point
| 50faf94e-eb3e-5602-a601-f61b18ec3476 | checkpoint | 5.01. Check set out of excavations
| 219bbfba-63b5-591a-8f7b-83aaa72e8252 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| eaea237c-88bd-5270-ae70-51ede65a6bac | note | RECORDS: 'Before' Photographs
| 9486341e-caa5-55bd-8cd4-ed377f5b7daf | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
| d6c36211-fe4f-5241-be82-1df031b349f2 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
| 93a5dcd7-f1f2-5bc7-b27b-85ee7ff98333 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
| 9e0e911b-c4f5-50fb-b39a-45606fa89624 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| c2592481-11b6-524d-a952-286bf598114e | note | INSPECTOR / APPROVER: Foreman. LLB
| 8eeb8f06-7f99-5ae6-85d1-d6b44a149571 | note | HOLD OR WITNESS POINT: Witness Point
| 8fa3fa97-e6a9-5421-8492-2f2e31abedb6 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
| e980ec79-41de-51f5-885b-3c0506e619e3 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
| cb9c6239-e14b-5e80-9928-0d9af5848298 | note | RECORDS: Copy of Consent and Traffic Management Plan
| 23d7f1ed-e28f-558e-afed-6e9213380ea7 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
| 38afe6bc-3962-5e7c-a3c5-ea0259cc2b8c | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
| 0e52176a-f3fc-5c33-b581-298c8be10302 | note | INSPECTION / TEST PROC: Document and Review
| e9902a8f-7069-5392-8dbf-b331dfbac91b | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
| f2c7bf91-fb5c-5b9e-8193-fd69557e87a1 | note | HOLD OR WITNESS POINT: Hold Point
| f519f885-05b6-572b-93c1-ecbb0e7ac032 | signoff | hold point
| 826c348b-bad5-5765-9c45-21db995ae514 | checkpoint | 6. Check deliveries of materials
| 8bbb91cd-4a14-5743-8faf-ed8f8a58835a | note | STAGE / FREQUENCY: Each delivery
| d1f3695f-3609-5d75-a7a1-1ce5ae06f1d4 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
| 267755d8-b900-5b54-a052-2dfed8af84c8 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
| 223c4aec-51a3-52c9-9b78-5c20b74cfac0 | note | Grade or class matches design
| 5e8e5672-de19-5ba1-9061-2b25ca5e35a4 | note | Size and thickness matches design
| c664ab5a-b198-573c-9c50-f3ac6e76b760 | note | Supplied items are free of defect
| 7c28391a-4e10-5c8e-a7d4-c38cf666aa5d | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
| b9f89331-4ada-59a1-80be-7b2113613fe0 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 3d7a5e31-24c5-5a27-8853-97de9df7efea | note | INSPECTOR / APPROVER: Foreman. Geschke
| 62906e0f-35a0-5526-8419-ae9814b8a99a | note | HOLD OR WITNESS POINT: Witness Point
| 6943e8e0-5771-5e26-91b2-eb3a4a9a7a94 | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
| c33c1a8c-376f-54fe-984d-4743a7f2ecd3 | tickbox | Standard Bead Profile Test
| 4e67ccb9-ae07-54e4-9b33-dcff5ca1af94 | tickbox | Standard Destructive Tensile Test
| aad1d026-c7b7-5433-b7a2-02a18babc43e | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
| 4f4ebc46-e6ef-5ef8-a451-8b23c2c85a2e | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
| 1608437e-e7f8-5c51-a95e-7429d5794daf | tickbox | Gasketing Record
| 5efc0212-a44c-5337-8f5a-219b924b11b4 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
| 8e566ca9-c3d9-51dc-81fe-a95f7c4dd724 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
| 5300de34-dbcd-521a-a1f9-73489b1521ae | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
| ac3c75e4-b98d-54b4-80aa-f01a0b17f84f | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
| 65727a2b-2689-5178-81fc-34048201e4e0 | note | Bead size to be uniform, symmetrical and free of contamination and air.
| 27354e34-4e6f-51a1-87bc-dac11bddeb90 | note | Bolt tightening to be completed using the correct sequence
| 8ff6b512-f3dd-5127-814c-0578925c569d | note | Final torque on bolts shall not exceed manufacture specification.
| 77390acd-79c8-51f3-ba47-3308e49bc28a | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
| bfe304c9-5d53-5b6e-96ca-d7c6c61a61e0 | note | INSPECTION / TEST PROC: Document and Review
| 935bdf51-aa77-5e50-a8f5-f1d5b013d332 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 5a317e88-e2f1-5f2a-8dec-a06c61917d12 | note | HOLD OR WITNESS POINT: Witness Point
| b3e2f606-7dab-5250-80fc-1db9ce52e67a | checkpoint | 7.02. Check below ground pipework - pipes and fittings
| 96b2dc90-a53a-572f-87bd-bed5a73eabd0 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
| 1eaa3d6c-80bb-5688-9a66-69a0bac1f18c | note | RECORDS: 'During' Photographs & As-built Survey
| 4b2ec00c-fbdf-5e6e-93ee-99d389111223 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
| 533ce572-fb81-503c-9add-12f6107bc54c | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
| 4641189c-1536-5048-b2b5-5d7a6a4e2d17 | note | Joints, fittings and connections match design
| a4f51eb2-de4d-5e00-9f83-e254b8527e76 | note | Alignment and position are as drawn
| 82eb4e20-91ce-508c-8464-e73daecf8ed5 | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
| 1d84c139-66bf-5579-9709-a687af53e932 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 90ecdc67-a645-56b2-8fbc-ac3cea97876b | note | HOLD OR WITNESS POINT: Hold Point
| fe1faa23-074e-5fa0-94bc-5f97e1955949 | signoff | hold point
| 28503935-01c6-5e48-ae8b-ac9ff45b32ff | checkpoint | 7.03. Check below ground pipework - Air pressure testing & swabbing. Standard Air Pressure T est
| a3fd3d4d-0eb5-5274-baf4-1a74b60e50c9 | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling / one test every 750 lm each pipeline
| 0b05dd18-a3d7-5d3d-8c5a-ec3f5a936680 | note | RECORDS: Standard Pressure T est Certificate QA.6
| 538e565f-011c-51f3-aa7f-74274bee5819 | note | SPECIFICATION / STANDARD: AS 5601 ACOR Consultants Civil Specification Section 6.26.8
| b7be1b16-0bae-536a-a5f6-66eefd4591b3 | note | ACCEPTANCE CRITERIA: Pipeline and joints are airtight under the greater of 7 kPa pressure or 1.5 times the working pressure for 5 mins
| 65955b97-2bf3-5cad-ae7c-c10fb5c55dd8 | note | Pipeline is flushed free of all debris
| 989db3b9-f642-5fc5-a14f-787529b5a55e | note | INSPECTION / TEST PROC: Document and Review
| 1d2470da-4eec-5341-b738-c40a22f5201b | note | INSPECTOR / APPROVER: Engineer. Geschke
| 0b4cc490-a25e-5a59-909b-5bc5d1a72cfb | note | HOLD OR WITNESS POINT: Witness Point
| ac79eb2f-166e-54ab-b592-d07ae349d2bf | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
| 678f82ed-989a-57ca-8f48-b0c2128f8207 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
| 752391f4-4ceb-5091-a6f7-aec47a91b841 | note | RECORDS: Photograph
| 37af61e0-0003-5579-bfa8-ba488af3737b | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
| df175655-2d57-5bc9-8736-f6e136882c68 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
| bf555cae-a31f-5c07-9f5e-bb9c6ef18efa | note | Thickness of surrounding aggregate shall meet or exceed specified depth
| 1f5b8960-ed1c-5afd-93fe-93e7286bd07a | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
| 3f9dbcf9-9e49-587e-a740-7ec0ee021fff | note | INSPECTION / TEST PROC: Visual Inspection
| 5d81e7c7-3a65-5400-80b1-a655ac3b13df | note | INSPECTOR / APPROVER: Foreman. Geschke
| 29c18f2e-272c-5c23-9594-fd841a2a8194 | note | HOLD OR WITNESS POINT: Witness Point
| 25dace2d-13db-5790-a72a-101165116a2a | checkpoint | 9. Check Completed Surface - Make Good
| 01e8af79-ec6f-5255-b3ba-f370f211d2ca | note | STAGE / FREQUENCY: Prior to practical completion
| ad485096-b09c-5f50-8ece-9357159b4a9d | note | RECORDS: 'Upon completion' Photographs
| 2e943770-9711-55a8-a890-903a7546f8b2 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
| b5603ac0-496f-520b-9b7d-700777b39cab | note | INSPECTION / TEST PROC: Visual Inspection and Document
| e20abc10-d095-5fb7-94e1-04d4a0a75374 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 74ec5b8b-9f0f-588a-b40c-e1becc90fb20 | note | HOLD OR WITNESS POINT: Hold Point
| 14256e6a-38b4-59ab-982a-4effc4e691dd | signoff | hold point
| 224cf3b9-e2f4-5d92-be53-2204ae1399ed | checkpoint | 10. Obtain as built documents
| fa7428ec-ab25-5b54-ae96-eb9d09eb57ed | note | STAGE / FREQUENCY: Prior to practical completion
| e46696ab-ac46-557f-90b4-b578d13b71cc | note | RECORDS: As built documents
| dd4c67ab-b0f3-5a33-8127-82094438b41d | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
| 95dae544-ea43-5111-a629-06c68d4e54b8 | note | INSPECTION / TEST PROC: Document and Review
| 71aea24a-4f6b-5759-ae78-ce4dccdc3223 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 09e8405c-5565-5dca-8a23-d1b412c75eeb | note | HOLD OR WITNESS POINT: Witness Point
| ac474954-435f-5a27-b07e-c9d30a9e17e8 | checkpoint | 11. Obtain Regulatory Authorities certificates and approvals
| 9f0e2b42-a254-532b-bda4-74b145ec82e8 | note | STAGE / FREQUENCY: Prior to practical completion
| 0abe8a24-605c-5db4-aa4c-207300878772 | note | RECORDS: Certificates; Written approvals
| e80593d1-9028-54a2-90d9-c4e787bd69de | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
| 49c3fe8b-7ada-58fb-871d-c66560d49fbd | note | INSPECTION / TEST PROC: Document and Review
| c6f1dcfb-4ce8-55e4-8c6e-44fabb19f034 | note | INSPECTOR / APPROVER: Independent Authority. LLB
| 339e8698-11aa-5e5f-b052-8535bf25a8c2 | note | HOLD OR WITNESS POINT: Hold Point
| 57e7821e-2d5e-54c7-ac59-b4b988b46a41 | signoff | hold point
| 5e111c9e-1802-5213-b3e8-d8cc1d7f5198 | checkpoint | 12. Obtain operating and maintenance manuals
| 79e0c08b-0dae-5205-a85e-ac9847272086 | note | STAGE / FREQUENCY: Prior to practical completion
| 26cd6238-0569-5297-80cb-d7b728f71a1e | note | RECORDS: Manuals
| 30ce08cc-a649-5ff9-95ee-61aeea8b14b9 | note | INSPECTION / TEST PROC: Document and Review
| c0024638-fd47-504c-925b-be4a72335239 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 441f4cb6-dba8-5e5b-8665-fd25e3a176a8 | note | HOLD OR WITNESS POINT: Witness Point
| 8990e252-b4f0-5060-ab0c-c0e8f62de4c8 | checkpoint | 13. Obtain guarantees
| d198bcee-cd85-5d63-b9b2-2d4b16b9d019 | note | STAGE / FREQUENCY: Prior to practical completion
| 2235cacd-751a-5e41-99c6-95c42dd727be | note | RECORDS: Final commissioning checklist
| 845bbda6-18fe-5c58-9b02-336aca21cb66 | note | INSPECTION / TEST PROC: Document and Review
| 40fdc476-1191-547d-980e-4d113d86a991 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| e8a00238-7392-5ba2-accd-f59593543e64 | note | HOLD OR WITNESS POINT: Witness Point
| 1c370b07-f8d9-59b0-aeb8-eb29ef3ab3db | checkpoint | 14. Final commissioning & inspection
| 5d8cddfd-e471-58dc-a376-37282e09f967 | note | STAGE / FREQUENCY: Prior to practical completion
| bf4bacf6-ca94-5b9d-8280-7a1166715785 | note | RECORDS: Final commissioning checklist
| e266bd23-3f04-5235-b32b-5187e388b10e | note | INSPECTION / TEST PROC: Document and Review
| e84d5907-4791-5a87-9a7a-af8f8d5d1f32 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 872bd20a-6ecf-51a1-82de-c4b90ec1870d | note | HOLD OR WITNESS POINT: Witness Point
| 883d1e2a-10db-50f4-9d72-61e1ea4f8c95 | checklist | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review |  | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review
| 4736d901-b2be-5732-9bfa-11380f738534 | checkpoint | 1. Approve specialist subcontractor
| 20a92ea7-d3e4-5b36-b5ad-e6f51f729ff4 | note | STAGE / FREQUENCY: Prior to awarding subcontract
| cee580cb-2a38-5177-9072-b1372cf465a5 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
| d135b6fd-e847-5da0-853a-7d0fa2b2061b | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
| 9a32b4cd-75a2-5d0a-92ea-307e8e9caa5e | note | INSPECTION / TEST PROC: Document
| e4b8f7b3-6f44-51ac-b8b5-0888ba1adf28 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 9c0711f2-ac2a-557a-be57-55a819b8409b | note | HOLD OR WITNESS POINT: Hold Point
| c09248f9-3cd0-5955-bdba-e77f96f2c162 | signoff | hold point
| 05b29a37-3c3c-5d86-8867-cf4598ae7f3c | checkpoint | 2. Approve Samples
| c9f9ac04-8923-5f00-86ce-4baffea66ecc | note | STAGE / FREQUENCY: Prior to ordering materials
| e3a463c5-6c51-5d7d-a8fb-9b63ee11c9c8 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| 26e8510b-7ab2-5a1a-b61b-c0a32e61e789 | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
| 88f40b6f-04fb-5a47-b5cd-20a3bb0550f6 | note | INSPECTION / TEST PROC: Document and Review
| 493893ca-16a4-5402-a77d-84ecf244af37 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 8fbb0330-143d-5b43-ba26-b340c6b16832 | note | HOLD OR WITNESS POINT: Witness Point
| 6409b5d7-f8dd-5c02-94a1-87f4c2593ac0 | checkpoint | 3. Approve technical details
| d999d84a-c3d9-5063-a790-f0672236e75b | note | STAGE / FREQUENCY: Prior to ordering equipment
| db34993e-4374-5461-94e5-ceb9b4b32d18 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| 8d93dc7e-10a6-529b-bc0f-9922fd673cde | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
| 35b45e72-dffb-54fc-b1ba-880142997ca2 | note | INSPECTION / TEST PROC: Document and Review
| 096b54ff-5079-5a6b-8a8c-ed7c6c295ab9 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 7acbd227-5d7e-53f2-9f67-711562dce1a7 | note | HOLD OR WITNESS POINT: Witness Point
| 71cbc1bc-bc6c-5c19-bacc-a5d0cabd0294 | checkpoint | 4. Approve shop drawings
| b6c8b376-a095-5fe5-b768-c032a5a52891 | note | STAGE / FREQUENCY: Prior to commencement
| b17f7492-a1f4-524a-9254-a3479c8c2e4d | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
| a2bad438-ff6f-5157-a9ec-e5e6ffa0ede7 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
| 7f2d1efb-3749-5b5b-8d2d-f3ecc04a050a | note | INSPECTION / TEST PROC: Document and Review
| 40010cd4-0f32-5df0-9047-6492d4cbf21b | note | INSPECTOR / APPROVER: Engineer. Geschke
| ea7d96ee-4595-5bab-99d0-100768433d7c | note | HOLD OR WITNESS POINT: Witness Point
| 50faf94e-eb3e-5602-a601-f61b18ec3476 | checkpoint | 5.01. Check set out of excavations
| 7cfb3db1-9cff-506b-96fe-a034b2915ed5 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| 95ce4686-6429-5deb-99b9-35e1c19eebad | note | RECORDS: 'Before' Photographs
| 3a12d079-b183-5138-8e30-0f57773ab216 | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
| 0f77604f-379b-54e6-a689-a878a8ec0056 | note | Minimum falls
| 9a1acfde-4a63-58a9-9c30-e8406dbc5ca0 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
| 5e51fc2f-e40e-556c-a45c-26937d6a5e9b | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
| 387b0c92-e2f3-51ce-809d-c5d75a58ab62 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| ba0b40ba-c6ad-5546-91e8-caf7fa17d08e | note | INSPECTOR / APPROVER: Foreman. LLB
| 1aee4ba8-c80a-5338-b5df-8fe7471aea45 | note | HOLD OR WITNESS POINT: Witness Point
| 8fa3fa97-e6a9-5421-8492-2f2e31abedb6 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
| 49e345e9-e6cc-5432-9bd0-7a52e1d11e89 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
| 3ff3f0f3-74ae-5d42-88f5-96d459b5c60d | note | RECORDS: Copy of Consent and Traffic Management Plan
| 6b66bfd0-37ab-54f5-9de4-3fd850a5d3c8 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
| ab9e74cc-5b55-5d28-aedf-187fa4d214c2 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
| e812eddf-b911-5df9-ad09-eb65abbc077e | note | INSPECTION / TEST PROC: Document and Review
| 4fbabfa9-9d2a-5f60-9ff4-d104563e3683 | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
| b8fde221-0a20-5b23-af9d-7fd7c0d9a701 | note | HOLD OR WITNESS POINT: Hold Point
| f519f885-05b6-572b-93c1-ecbb0e7ac032 | signoff | hold point
| 826c348b-bad5-5765-9c45-21db995ae514 | checkpoint | 6. Check deliveries of materials
| faa6417c-f5f1-5b23-8a6b-aaace772b412 | note | STAGE / FREQUENCY: Each delivery
| 9d157d4c-3360-570c-ab0e-c2f57cda8767 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
| 936c1b77-2ea1-5eff-9d22-bc7eb138d6ce | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
| 0e7b152a-7356-52a2-8aa9-2a4bd5254b40 | note | Grade or class matches design
| 8eca59fe-9613-5624-a338-a76da82142ee | note | Size and thickness matches design
| d43706dc-2b60-545a-8d1d-f4ee3d218379 | note | Supplied items are free of defect
| e8427688-6eb7-5e30-a60d-e09d3aa0aa00 | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
| 7e776f7e-b121-508d-9d77-deb2be71b870 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| f1af6ae0-d5e3-5612-9e74-de91cc16b192 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 6e631d15-3f32-51e6-9188-0eace1f362ff | note | HOLD OR WITNESS POINT: Witness Point
| 7463ee0f-80e0-5782-a24a-8462f8caf646 | checkpoint | 7.01. Check below ground pipework - pipe welds. Standard Bead Profile Test Standard Destructive Tensile Test Standard Ovality Test
| 0bc175b9-afa3-5caf-8073-faa0ce974bf7 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling 1 test per 50 pipeline welds approx.1000 l.m
| 336abc30-c34b-546f-8c99-9f7b9c8a5963 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Standard Ovality Certificate Standard Bead Profile T est Certificate Standard Destructive Tensile Test Certificate
| cdc881fa-9f03-51b5-b954-ef4e0e89b9df | note | SPECIFICATION / STANDARD: ISO 13953 ASTM F2620- 20 ASTM F2928 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
| 8754923c-edc0-5e7d-9f23-f9861d3be1a2 | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
| 89dd680b-8521-5757-9e28-1bb9b81c5d74 | note | Bead size to be uniform, symmetrical and free of contamination and air.
| a065e7ab-e5b6-53e9-8df7-5d7e5f5d9ef0 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
| b33bf364-5997-54a1-84f7-ec7c9fca1d44 | note | INSPECTION / TEST PROC: Document and Review
| 4eacc903-dff7-591c-83f5-cf8920a572c3 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 986164c7-9b71-5042-ab51-13b7fa83bdf9 | note | HOLD OR WITNESS POINT: Witness Point
| b3e2f606-7dab-5250-80fc-1db9ce52e67a | checkpoint | 7.02. Check below ground pipework - pipes and fittings
| 3da1e700-45e9-5333-935e-8267ca3cef1a | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
| b9af6399-ebcf-5544-973b-0adf40e1460d | note | RECORDS: 'During' Photographs & As-built Survey
| fa50fcfa-4c2e-5a08-b79c-071f799b9712 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
| bf41cef5-7d76-5a6a-89d6-5ad3b9404b4f | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
| 09809e68-6fbe-595a-87ff-e848f3822f67 | note | Joints, fittings and connections match design
| 6841b510-8010-5353-85f9-ca843e9564f3 | note | Alignment and position are as drawn
| c2edafd1-995f-58f5-8f2a-9bd71497ceaf | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
| 2a6e4987-4c14-5039-beeb-20097dc50b62 | note | INSPECTOR / APPROVER: Foreman. Geschke
| a67af6c1-5f7f-5790-92c7-59cd223e8b92 | note | HOLD OR WITNESS POINT: Hold Point
| fe1faa23-074e-5fa0-94bc-5f97e1955949 | signoff | hold point
| 1edd3296-b94c-508a-94c7-b1d314d2bda4 | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
| 70f9ae23-699e-5867-a648-64f92f407b63 | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling
| 6c46e8bc-6985-5fa4-bc06-1117e207aed7 | note | RECORDS: Standard Pressure T est Certificate QA.6
| 4eead7bf-c06e-5dcc-a910-9f82cbdea57e | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,500kPa pressure for two hours
| 45f3dcb9-41cf-5bf1-b1f6-7e546ed9ccb6 | note | Pipeline is flushed free of all debris
| 33717f4b-06c6-5c20-8f00-1fdb1c855510 | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
| 80af58c7-1422-5597-afba-5c6c2a385a27 | note | INSPECTION / TEST PROC: Document and Review
| b40ecfef-256f-5778-ab24-8d259a704bce | note | INSPECTOR / APPROVER: Engineer. Geschke
| 0769b885-409f-52eb-ac43-2cde4c1a2db1 | note | HOLD OR WITNESS POINT: Witness Point
| ac79eb2f-166e-54ab-b592-d07ae349d2bf | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
| 82ddc18f-0db4-5aa8-b70a-1ea0fb809a90 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
| 0c06d046-0e57-50c9-b10d-3d958ad338ad | note | RECORDS: Photograph
| fb55838d-0000-544b-a71b-13a330597a63 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
| baa2c5a8-94df-5619-b667-0ff6a822d4d2 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
| 0203941c-c1dd-5bb5-ba07-7fd9ad00b5bb | note | Thickness of surrounding aggregate shall meet or exceed specified depth
| bdc55870-69cf-51ac-84e1-c93a90763509 | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
| cdf4b768-2307-5b46-b0de-45d4037279e9 | note | INSPECTION / TEST PROC: Visual Inspection
| b367c5db-13cf-5a05-ad82-b4f363e4ca48 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 2f16ad37-8748-50f2-a280-2df384135d21 | note | HOLD OR WITNESS POINT: Witness Point
| 25dace2d-13db-5790-a72a-101165116a2a | checkpoint | 9. Check Completed Surface - Make Good
| c2c89f72-8aff-5673-9cc3-ba640952b0bb | note | STAGE / FREQUENCY: Prior to practical completion
| c783503a-7d21-5f8b-af46-974d025627ff | note | RECORDS: 'Upon completion' Photographs
| 2bad8e2e-8a68-5b05-95f8-aca36d117e7b | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
| 1cfc28b5-40c4-54a4-bb46-0e33323fe0f3 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| cd5bb78a-93ad-55b9-9234-5a157dbbb832 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 98178df9-b017-54f1-b98e-f15c5c2aaee2 | note | HOLD OR WITNESS POINT: Hold Point
| 14256e6a-38b4-59ab-982a-4effc4e691dd | signoff | hold point
| 224cf3b9-e2f4-5d92-be53-2204ae1399ed | checkpoint | 10. Obtain as built documents
| 59f51a79-9da5-581f-9c2f-2dedfa43e65e | note | STAGE / FREQUENCY: Prior to practical completion
| 8c374076-7f52-5f39-b1f5-a7dc8bb06575 | note | RECORDS: As built documents
| 19c3ba79-e6b0-5c31-bb77-a399af09f475 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
| 9493e692-48f9-5afe-a26f-471153fb2dbd | note | INSPECTION / TEST PROC: Document and Review
| 24db9943-32f7-53d3-88c7-5d71e2142e8c | note | INSPECTOR / APPROVER: Engineer. Geschke
| e479c03c-92ba-5398-9b83-0ef55e68c4c1 | note | HOLD OR WITNESS POINT: Witness Point
| ac474954-435f-5a27-b07e-c9d30a9e17e8 | checkpoint | 11. Obtain Regulatory Authorities certificates and approvals
| d8f8f9f3-aec8-5631-a3ca-2a2fac86f3b2 | note | STAGE / FREQUENCY: Prior to practical completion
| 2d1f9c24-6229-544e-beaf-cc94f8a1ea6b | note | RECORDS: Certificates; Written approvals
| 0e491fa2-97b0-5481-a768-89b586a710f2 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
| 50c92892-d781-572f-a388-9adfdbe993f9 | note | INSPECTION / TEST PROC: Document and Review
| 40d8fef9-d45c-5b73-9729-0c96d3000956 | note | INSPECTOR / APPROVER: Independent Authority. LLB
| a63b4bf7-1474-5353-ae31-f1634af39cde | note | HOLD OR WITNESS POINT: Hold Point
| 57e7821e-2d5e-54c7-ac59-b4b988b46a41 | signoff | hold point
| 5e111c9e-1802-5213-b3e8-d8cc1d7f5198 | checkpoint | 12. Obtain operating and maintenance manuals
| 49cf32d9-595c-5bf5-b8fe-db6d12a1e077 | note | STAGE / FREQUENCY: Prior to practical completion
| 69d36648-92de-5427-b7db-7cc36ec23d4d | note | RECORDS: Manuals
| 3895e359-64f8-583e-9787-d12564bc0168 | note | INSPECTION / TEST PROC: Document and Review
| cdade328-ae96-58cc-b8d9-22a9ccc044dc | note | INSPECTOR / APPROVER: Engineer. Geschke
| 85b7dd92-ec7e-538b-82c5-f3a84e5460d8 | note | HOLD OR WITNESS POINT: Witness Point
| 8990e252-b4f0-5060-ab0c-c0e8f62de4c8 | checkpoint | 13. Obtain guarantees
| 462a0a0c-97d9-5420-8fa1-d7f2cdc75298 | note | STAGE / FREQUENCY: Prior to practical completion
| 684e011c-8b00-5f81-981b-b15c89d24517 | note | RECORDS: Final commissioning checklist
| 2279ff33-2068-5abe-a24b-3e99e5861149 | note | INSPECTION / TEST PROC: Document and Review
| a33b8147-eb8e-5e02-83e6-b0f9334f6d86 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| a2ebf367-f25f-54fa-b6c0-fb928917d2e0 | note | HOLD OR WITNESS POINT: Witness Point
| 1c370b07-f8d9-59b0-aeb8-eb29ef3ab3db | checkpoint | 14. Final commissioning & inspection
| 4e8e831c-bdca-5822-879a-b2b6305e7e14 | note | STAGE / FREQUENCY: Prior to practical completion
| 760d6596-89e5-51b9-a1bb-59ff6626f4cd | note | RECORDS: Final commissioning checklist
| f0a0cad1-9620-53f4-aa45-4448050f5032 | note | INSPECTION / TEST PROC: Document and Review
| 4203b060-62e4-52fa-b73d-20665b486dc3 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 031d02b7-3ada-582f-96f4-75a6c6291ff4 | note | HOLD OR WITNESS POINT: Witness Point
| 3a20300d-01f3-5720-8402-cde775141786 | checklist | ITP - Storm Water Sample Excl. Backfill |  | ITP - Storm Water Sample Excl. Backfill
| 4736d901-b2be-5732-9bfa-11380f738534 | checkpoint | 1. Approve specialist subcontractor
| 579a17e0-8ad3-5903-977f-546ae524560d | note | STAGE / FREQUENCY: Prior to awarding subcontract
| 9897091c-6795-50d8-87b1-2909975ffdc7 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
| 2ce7b111-a674-56f4-907e-c6ae92cbc849 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
| 6fff61e7-4ae4-5c40-9ad9-cd21588e2e0f | note | INSPECTION / TEST PROC: Document
| 9de3f2e4-adae-5b97-8a60-e70d05a4a683 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| a507b848-4988-5b18-b6fa-6668123292e1 | note | HOLD OR WITNESS POINT: Hold Point
| c09248f9-3cd0-5955-bdba-e77f96f2c162 | signoff | hold point
| 05b29a37-3c3c-5d86-8867-cf4598ae7f3c | checkpoint | 2. Approve Samples
| 6f3b5f52-80b6-53cd-9358-eb1fc7d15abf | note | STAGE / FREQUENCY: Prior to ordering materials
| fe1b05cf-5c65-5c03-95d6-d946773baee0 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| ff6a7005-beb1-54c7-82cf-ea3786c3c668 | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
| c3b18f65-a7f8-5111-a9a0-20de8b063450 | note | INSPECTION / TEST PROC: Document and Review
| 2a2ef85c-e1e9-52da-b975-b51a14bffa95 | note | INSPECTOR / APPROVER: Engineer. Geschke
| c2b44cd9-e9fe-538f-97f6-a067f7b37d92 | note | HOLD OR WITNESS POINT: Witness Point
| 6409b5d7-f8dd-5c02-94a1-87f4c2593ac0 | checkpoint | 3. Approve technical details
| 2280be94-248b-5441-ab41-bbf7be009aef | note | STAGE / FREQUENCY: Prior to ordering equipment
| 35098c03-addb-5302-9c2c-0254e57b5b08 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| 39df51df-8e79-5fb2-814e-935ae6d96349 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
| c5780456-3d10-5cbd-afb0-3b7f3549f677 | note | INSPECTION / TEST PROC: Document and Review
| 028eee12-4313-5437-a6ad-be679ae31e68 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 2ad3401a-8dbd-5392-9c22-34a66234bf2e | note | HOLD OR WITNESS POINT: Witness Point
| 71cbc1bc-bc6c-5c19-bacc-a5d0cabd0294 | checkpoint | 4. Approve shop drawings
| a294d36f-be8f-5f48-a44f-9f2a93b4a018 | note | STAGE / FREQUENCY: Prior to commencement
| bd4aa7d0-0326-51ea-8f7d-7a2e2d148066 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
| 5d7e6f5d-d4cf-5dd2-b866-8ba4f0db8ba9 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
| 5bd361e8-03f0-5088-b192-619abb9610c8 | note | INSPECTION / TEST PROC: Document and Review
| 68c57aef-aba9-5484-bd83-bf7bc85319a4 | note | INSPECTOR / APPROVER: Engineer. Geschke
| d8c8592b-0884-5611-a030-5771dca33acb | note | HOLD OR WITNESS POINT: Witness Point
| 13e6f971-9e3b-5bed-903b-7770e22e9c3a | checkpoint | 5.01 . Check set out. By Delta
| 94f39236-b40b-5ccc-9900-8e0b3995cc32 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| 804c7e99-089b-5e84-8967-1baad13b6240 | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
| ba272a2c-f683-596c-b449-420068f3d884 | note | Height control point is marked within 40m of works area.
| e23a708b-8214-54e4-8a05-f4c6451a1250 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
| 64fe05a8-ffa2-5f73-957e-eb70b70c860b | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 4d9bead1-5ef7-5476-b465-c1ba978873e5 | note | INSPECTOR / APPROVER: Foreman. Delta
| d6a6c68a-3414-57c6-a325-8375c0e48de8 | note | HOLD OR WITNESS POINT: Witness Point
| 50acc937-f1df-5c55-841a-1a6d1861c6a2 | checkpoint | 5.02. Check excavations
| 07ddcc0f-e52d-55b3-b5cf-6cecc2c59717 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| 0f01c69e-75bc-57a0-b64d-3e6280919381 | note | RECORDS: 'Before' Photographs
| eec60234-8957-5ad6-9052-ac8450d387dc | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
| bd5f06c3-57b4-57f9-ad5e-02fc0a4034ac | note | Minimum falls
| 2c73ff79-3f88-56b2-b4ff-c8afffdd900c | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
| 398331e2-01e3-55ca-9fb9-4a86b0cb52b5 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| eb9e910d-4edc-58ba-8996-b22810cde5e8 | note | INSPECTOR / APPROVER: Foreman. LLB
| 190978bb-671d-549d-a56e-20fa2a063a88 | note | HOLD OR WITNESS POINT: Witness Point
| be4b0f23-b079-5587-9d6a-3ef346d58d24 | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
| 237645e6-0e32-5387-802f-d9e5fec025f0 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
| fdd73e6c-d553-5764-9aed-a798d64ac203 | note | RECORDS: Copy of Consent and Traffic Management Plan
| 0d6323e4-7b78-5df1-a0cd-39b1e06fd2e6 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
| fa365a6b-c9f0-5df1-9390-4fda655bef68 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
| 601962a5-3a4c-59f8-baea-bc370ce7221e | note | INSPECTION / TEST PROC: Document and Review
| 2deac7b9-04b5-51ac-a8c8-9b30110cffca | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
| 19206954-a178-5ec4-ab53-2a3c37da7841 | note | HOLD OR WITNESS POINT: Hold Point
| 29a572ab-8347-58d0-bae7-e487492e7f78 | signoff | hold point
| 826c348b-bad5-5765-9c45-21db995ae514 | checkpoint | 6. Check deliveries of materials
| 5e961d45-fac9-5707-b1f3-311de95f2ee3 | note | STAGE / FREQUENCY: Each delivery
| e219b9da-0fa3-53b3-994f-5be701378798 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
| eca7fc03-8c1a-5821-ac66-118fe2c1a8ef | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
| 904fdc14-ac50-560a-a2a2-9a7a31068ce9 | note | Grade or class matches design
| c58af743-1b41-5c5f-8d50-aa227bf2aa23 | note | Size and thickness matches design
| 114f8da3-2b70-52ce-93d0-780a6716f798 | note | Supplied items are free of defect
| af88a8d6-64c1-5177-9311-d1a19951fc9f | note | Marking, packaging and preservation is fit for storage / construction
| e0c743cf-f5e5-5a4e-862f-c9d9b3d0019c | note | INSPECTION / TEST PROC: Visual Inspection and Document
| fb9a82ee-a0c5-501c-943a-995eed848716 | note | INSPECTOR / APPROVER: Foreman. Geschke
| c32e73a5-8e82-5937-b270-b4b028f791d3 | note | HOLD OR WITNESS POINT: Witness Point
| d758de90-4aa4-5e13-b434-36b86cad246f | checkpoint | 7.01. Check below ground pipework - rubber ring joints
| 79b07097-14c8-5389-9b53-607eac7e0ddd | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / one test each grid
| d05c7c22-a129-5f43-9ac8-168b3a595008 | note | ACCEPTANCE CRITERIA: Joints are secure and flexible
| d7d1e873-d3d8-531b-beb0-0b1d5b215077 | note | INSPECTION / TEST PROC: Visual Inspection
| 84e84d69-fade-5c5a-918f-c9f24682c2da | note | INSPECTOR / APPROVER: Foreman. Geschke
| 704f4d55-950f-5c90-b662-20e06a1831c6 | note | HOLD OR WITNESS POINT: Witness Point
| 84c26fad-7e84-5aeb-8c37-97b7d1d9de7b | checkpoint | 7.02. Check below ground pipework - pipes and fittings. By Delta
| 932b8696-92c4-5ecc-a1c8-d776e65d83b2 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / once per grid
| aef56460-c00a-5c86-afb0-3d9c0e7a3b5a | note | RECORDS: 'During' Photographs by Delta & As- built Survey by Delta
| ebfa7cbc-afc8-5c91-9e51-84c92b6baa7f | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
| 8cf1d354-86ab-5c82-8033-cc849454f060 | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
| d2765691-e522-5b30-a5a0-913ecb67cde6 | note | Joints, fittings and connections match design
| 761e4e44-0db0-539f-95e7-a8142390d4b9 | note | Alignment and position are as drawn
| 9f49e8f1-0c71-58e6-8907-f0ce1c608a2f | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
| 1789af76-9468-5348-9600-dab084fbd57d | note | INSPECTOR / APPROVER: Foreman. Delta
| c73542c6-7ca0-5dc7-b094-3c73fee732e9 | note | HOLD OR WITNESS POINT: Hold Point
| a8ea1173-bdc0-5b80-a060-3f525db116a3 | signoff | Hold Point
| cdd5e778-d370-57ea-aa84-fd14f216187b | checkpoint | 7.03. Check below ground pipework - bedding, haunching, surrounding and encasing
| 158db5d2-b2cf-54bf-a4cc-db275c70f786 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
| 944bdc59-a716-5110-b19e-fc24abf076e7 | note | RECORDS: Photograph
| b35a6850-eddb-5583-a9f0-b02ca9c517ce | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
| f0526b19-a523-5b3f-b83a-495ab433be39 | note | ACCEPTANCE CRITERIA: Constructed using approved material
| fcd9d1e8-b749-5762-acb3-08933cd53387 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
| d67c16ec-d9cd-5486-91c3-8722146fa29b | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
| bf0be4bf-e2ad-55f6-aea5-517360682175 | note | INSPECTION / TEST PROC: Visual Inspection
| b69e20b8-18bd-55b8-98a1-5b2cec32f6b0 | note | INSPECTOR / APPROVER: Foreman. Geschke
| f08e8d54-7716-5757-bdc2-41b13f36e4db | note | HOLD OR WITNESS POINT: Witness Point
| 86e11d24-399e-5d39-b91b-e6df27f818e4 | checkpoint | 9. Check Finished Surface - Make Good. By Delta
| 799554c8-62a6-5b5b-bb16-5ae94578222d | note | STAGE / FREQUENCY: Prior to practical completion
| d98025d7-d37f-5555-ba31-260aeace4e5f | note | RECORDS: 'Upon completion' Photographs by Delta
| 3b974184-5cef-52ae-b87b-d7d59113e5e7 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.18.5.12
| 6021f566-3fdc-5701-83e2-94e1368064bc | note | ACCEPTANCE CRITERIA: If works are in existing roadways, paving or asphalt has been replaced.
| 5271ad4a-9884-55a1-9203-cfc8fd03dca2 | note | Finished surface is free of obstruction/debris and matches finis
| 7d400862-af0f-59fa-be17-02e77375a3b0 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 58699ed6-1055-511e-a853-d434722107d0 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Delta
| d213bb88-b631-5214-a0ba-063f2dd93304 | note | HOLD OR WITNESS POINT: Hold Point
| f3a0728a-0130-563a-8f83-a5bbef844364 | signoff | hold point
| 955918e1-0493-54c0-a3dd-e6891eaaa900 | checkpoint | 10. Obtain as built documents. By Delta
| 769c69d6-5bb7-5fa0-88ad-1b5200130ef6 | note | STAGE / FREQUENCY: Prior to practical completion
| 94d41758-8345-5935-8481-bc476bd68a78 | note | RECORDS: As built documents by Delta
| fb735312-09a5-5b21-98ee-34f4e229e302 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
| 97d7908f-2bd5-585a-bf57-b81ca5d8d6b4 | note | INSPECTION / TEST PROC: Document and Review
| 150efdf0-2579-59a2-9e9e-bd456ebe937c | note | INSPECTOR / APPROVER: Engineer. Delta
| 4f79dabd-4ad4-5f5d-b0aa-723637338a94 | note | HOLD OR WITNESS POINT: Witness Point
| 2c843525-d62b-5943-9f3d-f7411623ad28 | checkpoint | 11. Obtain operating and maintenance manuals
| c5201abc-ffa0-500d-853d-7fefade54c16 | note | STAGE / FREQUENCY: Prior to practical completion
| 91acd45f-805b-5144-82bd-2b8e71a0ca92 | note | RECORDS: Manuals
| 241affb0-abc1-596a-b6a2-ba72a78fc0b5 | note | INSPECTION / TEST PROC: Document and Review
| 44f29409-ee95-5303-a352-169f70fc14e1 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 7845c777-4f63-53f0-be2c-1b54d84a09cc | note | HOLD OR WITNESS POINT: Witness Point
| 0802e744-669c-59ec-a4da-5b67b9138bd1 | checkpoint | 12. Obtain Guarantees
| c1ddafe7-d690-52b9-a2d7-d637294a67bd | note | STAGE / FREQUENCY: Prior to practical completion
| 1cf4c80c-297a-52d8-aa29-327c7d2e72c2 | note | RECORDS: Written guarantees
| 5097f1c3-1bf0-5cd9-a99c-eb96824e2960 | note | INSPECTION / TEST PROC: Document and Review
| 368370ce-3f96-5716-8cc7-0323ea5dccdf | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 3f30fa19-84bc-5635-9d8b-404ab035a6e5 | note | HOLD OR WITNESS POINT: Witness Point
| 8f31a898-3b28-51f2-8fa5-87eb9d17dca1 | checkpoint | 13. Final commissioning & inspection
| bdb5e9ab-955f-5d85-b5ed-8d547149f4f5 | note | STAGE / FREQUENCY: Prior to practical completion
| 5f7191ea-6c9a-51dd-bdf1-5e10c6d77b4c | note | RECORDS: Final commissioning checklist
| 618e6a35-a03c-5139-903e-c14bd3f04db0 | note | INSPECTION / TEST PROC: Document and Review
| faf5d475-0b90-51b1-8806-799d324cb2e1 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 941ffd4c-5c3b-5f8c-8f28-1b3d5e4d344f | note | HOLD OR WITNESS POINT: Witness Point
| aa012185-8331-5580-8653-3329e390aafc | checklist | ITP - Subsoil Sample |  | ITP - Subsoil Sample
| 4736d901-b2be-5732-9bfa-11380f738534 | checkpoint | 1. Approve specialist subcontractor
| 9d4eb838-dc73-55bf-b69f-c9def836fd57 | note | STAGE / FREQUENCY: Prior to awarding subcontract
| da6e934e-11e9-50eb-aafc-cf7d43313983 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
| 3828bc0d-05a7-5c3d-8b7a-7e232b6d0c0a | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
| df637440-df77-5b80-bda8-ca27cd6c0396 | note | INSPECTION / TEST PROC: Document
| 907bdaa2-ae11-5fe7-9b4a-b8726c61cc84 | note | INSPECTOR / APPROVER:Subcontractors Authorised Representative. Geschke
| 009442fb-4d6f-5780-9dd0-e1d259c035b1 | note | HOLD OR WITNESS POINT: Hold Point
| c09248f9-3cd0-5955-bdba-e77f96f2c162 | signoff | hold point
| 05b29a37-3c3c-5d86-8867-cf4598ae7f3c | checkpoint | 2. Approve Samples
| e0753a28-228e-5b33-9dba-1f2ef8737545 | note | STAGE / FREQUENCY: Prior to ordering materials
| ed2c4902-525f-5084-83cb-3597d98e2b4a | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| c0924802-0d21-5273-893a-36a5e749e8ad | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
| 8d3a4a13-88ad-57f7-bd57-5569ee6bb812 | note | INSPECTION / TEST PROC: Document and Review
| bb6eba40-717f-5c47-a5a4-f9c280ce59a9 | note | INSPECTOR / APPROVER: Engineer. Geschke
| b89ccf68-12f6-572d-8e63-5c97722e8790 | note | HOLD OR WITNESS POINT: Witness Point
| 6409b5d7-f8dd-5c02-94a1-87f4c2593ac0 | checkpoint | 3. Approve technical details
| fd160c9e-62e4-5bb6-b481-0cf089407b1f | note | STAGE / FREQUENCY: Prior to ordering equipment
| 4844bcc0-5510-5ea7-954d-5709d6e77639 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
| 8688973e-580c-521e-a2ef-ab63fd5d5227 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
| bcb9c29c-4d10-58fe-9307-f7fb3cb80757 | note | INSPECTION / TEST PROC: Document and Review
| 650067d7-f4fd-51b4-b854-7a1c032537d0 | note | INSPECTOR / APPROVER: Engineer. Geschke
| e435cb21-9254-5f72-8f6b-dd34ca67dd9b | note | HOLD OR WITNESS POINT: Witness Point
| 71cbc1bc-bc6c-5c19-bacc-a5d0cabd0294 | checkpoint | 4. Approve shop drawings
| e745eb57-8603-559c-a4c8-0161dad852a7 | note | STAGE / FREQUENCY: Prior to commencement
| 7610d3ca-cefb-5da4-b772-f9b08eaa1ef8 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
| 0d000ef2-9abb-5855-acad-717d29720935 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
| 6c873f21-a11b-5fe2-8348-eb058d7a2b10 | note | INSPECTION / TEST PROC: Document and Review
| 04480fbd-5b24-5218-9ae0-41a1add9a686 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 840e34bf-364b-55b0-853c-dbb09dc2b066 | note | HOLD OR WITNESS POINT: Witness Point
| 54b636d8-e4aa-510a-9a49-62980cf21128 | checkpoint | 5.01. Check set out - Works by Delta
| 2f5d3c92-b74b-5a37-8791-2b7410bd4ade | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| 4aef75fb-96f1-56e4-a30c-94d2366ef86d | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
| 896486f4-d9e0-589c-bfbd-ff59e938c842 | note | Height control point is marked within 40m of works area.
| 910ebd13-ef48-5195-b307-d22c12848672 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
| 80584e9f-b783-579a-bdbf-2d373956ff7d | note | INSPECTION / TEST PROC: Visual Inspection and Document
| c9f3304a-3c33-5973-8975-2616504cf418 | note | INSPECTOR / APPROVER: Foreman. Delta
| 9ad7cf58-d4a5-5db8-940f-68975769d27e | note | HOLD OR WITNESS POINT: Witness Point
| 50acc937-f1df-5c55-841a-1a6d1861c6a2 | checkpoint | 5.02. Check excavations
| 31fae4e3-e09c-5061-9060-86d4ed0daa19 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
| 18382bba-eb68-52bb-9f70-b9de3e873c02 | note | RECORDS: 'Before' Photographs
| 5075a1a9-1580-5548-9343-0db42c4f4c21 | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
| 016f9252-71f9-5743-8531-0c0edce96d79 | note | Minimum falls
| f47f7e19-4586-5d39-a733-9f6a253768d1 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
| 01fbf527-7206-5681-a244-1b6f59c3a7a4 | note | INSPECTION / TEST PROC: Visual Inspection
| 65e836c8-b615-5f9b-83b1-d0f9b5e3c02f | note | INSPECTOR / APPROVER: Foreman. LLB
| a5e514d7-adb8-5b8e-a394-df6e6e372568 | note | HOLD OR WITNESS POINT: Witness Point
| be4b0f23-b079-5587-9d6a-3ef346d58d24 | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
| 57bd8763-fd51-5070-8dbd-e9262baa04b7 | note | STAGE / FREQUENCY: Prior to commencement / Each TMP
| aea906af-f26d-5f81-a1ee-1b30392f229b | note | RECORDS: Copy of Consent and Traffic Management Plan
| a845e705-da73-5d36-9ed5-764c10af7bc9 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
| 08946a2c-eb10-5c8c-8cd0-14ff16e194b6 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
| b4a32c14-779b-55e0-80ae-e31020b76fe2 | note | INSPECTION / TEST PROC: Document and Review
| aa2b6ade-d039-5ed6-a124-dc0b69f55bf2 | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
| 591e8f8c-978e-5af7-bfff-6f6f28f8ca68 | note | HOLD OR WITNESS POINT: Hold Point
| 29a572ab-8347-58d0-bae7-e487492e7f78 | signoff | hold point
| 826c348b-bad5-5765-9c45-21db995ae514 | checkpoint | 6. Check deliveries of materials
| 9d8a4093-5711-5eb3-b30a-82ec2309416c | note | STAGE / FREQUENCY: Each delivery
| ddafe402-bf29-5e52-b6e8-92002eeb9866 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
| 55a02ce1-c761-5c8d-997b-7809e49d42e3 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
| dfdcc1cd-2aab-5726-9c19-8cebf0825dea | note | Grade or class matches design
| 71d23c89-7dbb-5c18-83ea-76f954556b73 | note | Size and thickness matches design
| 9e1a1ba9-8427-5d9b-b242-3800df4375a3 | note | Supplied items are free of defect
| 86dcfe28-9be5-5a81-8866-6cc13cd393e9 | note | Marking, packaging and preservation is fit for storage / construction.
| 2e6802d8-89c9-5e57-b922-6504e966cc46 | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 9dc8ff4e-5257-53de-b86c-2fa4ad32b710 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 4d05ae0b-3ec3-50be-9af1-cdcd43203737 | note | HOLD OR WITNESS POINT: Witness Point
| 25df00a5-af00-5808-aee3-f9a9f3a32309 | checkpoint | 7.01. Check below ground pipework - pipes and fittings
| 6587e6f6-8857-58ce-a81e-e69a0d7f018e | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
| 51ff1b33-3f20-5c1b-946d-dfe5b18568dd | note | RECORDS: 'During' Photographs & As-built Survey by Delta
| f63e3666-152a-53fe-a6b3-93c60acab6a4 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
| 11d98606-c4df-5995-9604-5b5d4a5065c2 | note | ACCEPTANCE CRITERIA: Joints, fittings and connections match design
| 19fc3ed7-2d4a-598e-b197-9e5525441206 | note | Alignment and position are as drawn
| a9d3c499-2d16-5906-a2f6-2d40e1ab833e | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
| f87725be-7882-5a46-839c-7d99fe66332b | note | INSPECTOR / APPROVER: Foreman. Geschke
| 63902c13-9d83-5cb0-8476-8552efa85cd8 | note | HOLD OR WITNESS POINT: Hold Point
| ad122882-9d8c-541c-8134-dc553329d3fa | signoff | hold point
| 7e89ab31-36e7-5e89-9075-fc5e9cea036e | checkpoint | 7.02. Check below ground pipework - high ends and flushing points
| a23ebf66-8470-51c4-ad24-e68cff41e6bf | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
| a5f06519-a097-5c0a-9438-394f9a11ff00 | note | ACCEPTANCE CRITERIA: Capped at surface level with hinged lid, cast iron box in concrete surround 300 x 300 x 150mm
| d7d6e1b7-55fc-5b3d-9010-dbf2121c3186 | note | INSPECTION / TEST PROC: Visual Inspection
| 85aa3c7c-a514-53f4-a494-cd0d9424b2c1 | note | INSPECTOR / APPROVER: Foreman. Geschke
| d859aba2-bb4e-5787-9ff8-f51eca18a00d | note | HOLD OR WITNESS POINT: Hold Point
| 860036e3-6843-5cce-ab02-98fb0c2b9068 | signoff | hold point
| 54cff440-47f8-50c9-933d-0e81ee25e23a | checkpoint | 7.03. Check below ground pipework - haunching, surrounding and encasing
| 116b7a4d-b37b-5890-9c19-2ef492f2425a | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
| ad62d472-435e-5bb3-814b-d16aae29631e | note | RECORDS: Photograph
| 46a79d42-7477-5de8-9968-d405dfe77cd8 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.19.3
| c0fbbf83-66c2-59b7-ba63-11f2dd49fd9a | note | ACCEPTANCE CRITERIA: Free draining granular material
| 61b3c230-eedf-5c4c-ab90-9f05e93e2c39 | note | All faces of filter material in contact with topsoil or similar shall be covered in geotextile
| ce343597-2b89-547e-adae-4bf2831ea165 | note | Material used is as specified and approved.
| 918be02e-b6a6-5a1a-9839-eb369acd7333 | note | INSPECTION / TEST PROC: Visual Inspection
| d2767c7d-2d8d-5d33-bd5f-f4856228c8a9 | note | INSPECTOR / APPROVER: Foreman. Geschke
| d74f6797-3c56-5c4d-8779-04c503ef3494 | note | HOLD OR WITNESS POINT: Witness Point
| 77be2007-bcfa-5413-bfca-1a21e83c2e1f | checkpoint | 8. Check Completed Surface - Make Good
| dce6dc94-4517-57ea-b403-733cfca67c81 | note | STAGE / FREQUENCY: Prior to practical completion
| e3846798-21c4-50e2-940e-4efa5c61d919 | note | RECORDS: 'Upon completion' Photographs
| 9e0ec8ef-887d-5a06-a253-0d1424e803ed | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework less depth of works by others
| 1cc14c4a-453a-5a62-b1fc-462636b96b1d | note | INSPECTION / TEST PROC: Visual Inspection and Document
| 33e2b17a-1c55-56c4-9246-90f468242246 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 99c569b5-7437-5d5d-b0e6-884ae95e3856 | note | HOLD OR WITNESS POINT:
| 76009441-b406-5a2c-b191-3ae372055b22 | note | HOLD OR WITNESS POINT: Hold Point
| 889ab768-ee86-5e59-8949-157d8a1bf2a5 | signoff | hold point
| 58e4161b-87a0-5bb4-b648-731e1758cd13 | checkpoint | 9. Obtain 'as built' documents - Works by Delta
| 93c52f42-ea40-521c-b108-a5f5e2cff2cb | note | STAGE / FREQUENCY: Prior to practical completion
| 8087767b-333f-5e05-9eb0-7043923ed488 | note | RECORDS: As built documents by Delta
| 723ca511-6a90-5520-b884-1220284158e5 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
| 07a79762-12e9-5e5c-9b4f-6af501b5b26e | note | INSPECTION / TEST PROC: Document and Review
| 6b1a0a76-d16e-511f-9238-c077e472a5a7 | note | INSPECTOR / APPROVER: Engineer. Delta
| 89918e03-93b9-50cf-9589-ffe0837930f3 | note | HOLD OR WITNESS POINT: Witness Point
| 7d242a54-65d2-5850-83f8-0ca7aaec545b | checkpoint | 10. Obtain operating and maintenance manuals
| 63efa2eb-fea7-582c-9919-aa2f8ceebea5 | note | STAGE / FREQUENCY: Prior to practical completion
| de7d9af8-0442-5628-bcca-4f3d8d4daf8c | note | RECORDS: Manuals
| a5d4f506-c0bf-511e-8f30-2ea093e4fea4 | note | INSPECTION / TEST PROC: Document and Review
| 6cfa71b0-06d6-5bd2-ac4e-59806bcedd44 | note | INSPECTOR / APPROVER: Engineer. Geschke
| 59e07c13-61cc-510b-81e0-f2db1f8b0938 | note | HOLD OR WITNESS POINT: Witness Point
| 501620ec-c848-5809-af8e-2e24f6629f7e | checkpoint | 11. Obtain Guarantees
| 814f23f8-7599-53fa-995a-51f98f900fa4 | note | STAGE / FREQUENCY: Prior to practical completion
| 345d632d-1f3d-565d-b1ce-16d22c671d99 | note | RECORDS: Written guarantees
| 7728e5a2-8c4d-5c9c-8a38-f72b7aa1f7a4 | note | INSPECTION / TEST PROC: Document and Review
| fa565cb3-984a-5bb4-8f59-55e1254fdfd8 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| d11330c1-db74-536f-8249-dcd3a19b564a | note | HOLD OR WITNESS POINT: Witness Point
| 250bd799-7b4a-5d5c-b4fa-5ca7251c5763 | checkpoint | 12. Final commissioning & inspection
| 12376f84-d771-574e-aabc-7a1854862690 | note | STAGE / FREQUENCY: Prior to practical completion
| a1830aad-a648-517b-95fd-6d5a7638c5dd | note | RECORDS: Final commissioning checklist
| a716b483-bd9d-5d53-a3a8-c2e10802245f | note | INSPECTION / TEST PROC: Document and Review
| adbdd134-9141-5c13-b0ee-710c899fc6f7 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
| 40201bcc-ad44-5507-b1d8-b31c30f5ba1c | note | HOLD OR WITNESS POINT: Witness Point
| 20611885-c4bf-5896-b658-85a1a9c461ec | checklist | ITP - Trench Compaction - Various Services |  | ITP Trench Compaction - Various Services
| c9eda634-08ec-5386-8227-10decc8d2091 | checkpoint | 8.01 - To assist with the requirements of not only test results but ensure supervision to assess the competency of the construction methods a Level 1 GITA tester will be on hand to express an opinion on the compliance of the work practices. Geschke Plumbing are to compact in 150mm layers with Trench Pad Foot Roller.
| e6761e40-b5cd-5459-abb7-e85eac4c816e | note | STAGE / FREQUENCY: During compaction
| cda4f2ce-2c9a-5ce6-8ece-cc0dcad2c7eb | note | RECORDS: Written document by Level 1 GITA tester. Geschke mark-up of backfill type, test & observation location by grid
| 243a0fc2-133e-5bde-a079-1c30240fb722 | note | SPECIFICATION / STANDARD: AS 3798-2007
| 9b836e52-e76f-5cf7-a84e-2661a8fddd66 | note | ACCEPTANCE CRITERIA: Geschke are to compact in 150mm layers with Trench Pad Foot Roller
| 0baae71d-5450-58f2-a818-1ccd64ac0a3d | note | INSPECTION / TEST PROC: Audit Activity
| 697e8709-c65f-5077-a162-2c8cddde9ca0 | note | INSPECTOR / APPROVER: Geotechnical Testing Authority. Geschke
| 686a6865-e973-5493-9f2f-f7a5a868d60e | note | HOLD OR WITNESS POINT: Witness Point
| 8cb0b30a-3315-5f1d-9926-e8cfe2c27fbe | checkpoint | 8.02 - If Stab Sand is required for back fill this will be delivered 5% stab sand as per approved material. 5% stab sand on 100 slump poured straight from the shoot
| f6da8555-7024-5c1e-b696-ed91e9c49f6e | note | STAGE / FREQUENCY: Prior to installation / Each pour.
| c0f928e5-90b1-563a-aeca-c31eccc3f025 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
| a383007a-c24d-5d47-909e-c5bdcf59c82a | note | ACCEPTANCE CRITERIA: Stabilised sand mix meets 100 slump direct from concrete truck shoot
| e9d14697-8e61-51a5-9ad9-1bb363150544 | note | INSPECTION / TEST PROC: Document and Review
| 2798801e-6a22-518e-83cf-49b3d894e52e | note | INSPECTOR / APPROVER: Foreman. Geschke.
| f52f94e5-341b-5693-816f-41452db4492a | note | HOLD OR WITNESS POINT: Witness Point
| c09c9177-10a9-54d2-80b7-3a6dd88e6cc7 | checkpoint | 8.03 - Testing to be completed in backfilled zones with 1 test through 2 layers every 40 linear meters. We will test our trenching through 2 layers at finished height less topsoil depth. This test will be completed approx. every 40 linear meters.
| c93b814c-c3d0-5126-a242-75f496017fba | note | STAGE / FREQUENCY: Prior to completion / one test every 40 linear meters
| 8dfb8ae1-72da-5ec7-af4b-e170640db1be | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
| b2e92509-9b11-5bab-9cea-97a9a172ae1a | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
| 820c9b24-e47b-5778-8bed-48bfd891b652 | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivalent density of existing ground found adjacent to the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
| eb9b719a-3676-55e3-bf1e-b82622b04f91 | note | INSPECTION / TEST PROC: Test Activity
| 2b2f294a-748e-564d-a14c-5a112aa12598 | note | INSPECTOR / APPROVER: Foreman. Geschke
| 7142a14c-7874-5ab4-a617-0e7d85de7db1 | note | HOLD OR WITNESS POINT: Witness Point
| ef0f80b3-0b20-50da-ad03-cee2632403ce | checkpoint | 8.04 - Testing to be completed adjacent to work zone as required by digging back top soil layer and testing in ground. One test in existing ground adjacent to work zone through 2 layers at finished height less topsoil depth.
| f7225629-caff-57fc-818a-12a2f41830de | note | STAGE / FREQUENCY: Prior to completion / one test as required
| b5d3f0a5-6cc5-5dac-8e0d-f76cc80b5c91 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
| 600c8976-e8f2-5020-a6e8-fa1f272d7770 | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
| f62b7ea5-7a79-53ad-b39b-dc9a05d43225 | note | INSPECTION / TEST PROC: Test Activity
| cc5d8b35-caef-515a-be2c-d0b4c0d76ada | note | INSPECTOR / APPROVER: Foreman. Geschke
| abd06697-f488-5b7a-8fd2-dc742bb23963 | note | HOLD OR WITNESS POINT: Witness Point
| 2ec87fe5-5756-5834-917a-28a408b5f2ef | checkpoint | 8.05 - Compaction Test Results. Test Results as per above test plan.
| afc35d1a-2d4f-5039-967a-0596d52e1e53 | note | STAGE / FREQUENCY: Testing as per above
| 48e069c3-e90b-5644-b3c2-25c75b49899f | note | RECORDS: Standard HILF Test Certificate
| a78e164c-ccf3-5ecd-b1b4-bbb3591ebd42 | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
| cb38ff9b-48bc-54d3-9689-bf58e6a1bd0e | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivariant density of existing ground found in the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
| 9b873895-8268-55ce-9bcb-127a71fe6424 | note | INSPECTION / TEST PROC: Document and Review
| a2899f31-7ed5-52ca-bcd6-4181d7c4b1a7 | note | INSPECTOR / APPROVER: Foreman. Geschke.
| 21a3e53c-7646-50ce-9896-28bb3f85d099 | note | HOLD OR WITNESS POINT: Witness Point
| 844913cf-0d68-518c-abd8-37a46984d4f1 | checklist | Maintenance Inspection Report (Dec 2021) |  | Maintenance Inspection Report -
| 8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
| de91307b-af90-513a-a394-46b0c4d46d8c | checkpoint | Inspection Details - Pass once entered
Hidden property width:50 | 13c6b75a-0dae-4605-aebd-f22cf8b9ef34 | textbox | Site Name
Hidden property width:50 | e9dd538f-b767-48c5-9a68-71d372c010a6 | textbox | Date
| a7efaae1-c737-4c27-b0db-1ca7d6edb060 | textbox | Site Address
Hidden property width:50 | 467bc035-0cb9-4f08-bcbe-468fafc94873 | textbox | Contact
Hidden property width:50 | 2ae19935-2064-466f-9412-f655a0b16960 | textbox | Contact Phone #
Hidden property width:50 | 609f01ea-7840-49f6-9f6e-516a4476d95e | textbox | Inspection Task Location
Hidden property width:50 | e651c5e2-9313-49e9-860e-b0140927eb67 | textbox | Item/Equipment to be Inspected
| e7581576-5a10-5963-90b0-44587360e1f6 | section | Inspection
| af8aa8e6-9a2f-50ee-b9f1-e68fc6e85d10 | checkpoint | Does installation comply with manufacturer's instructions
| 216de0c5-b5bf-53b5-a247-9b7af08ea207 | checkpoint | Does the item function as it was designed to
| ee7245b7-a6dc-56d5-952f-38ca528f89c0 | checkpoint | Is there any reports from the customer of the item not working or any issues
| 8acc2741-d877-5038-ba10-f5acdc5f2584 | checkpoint | Is the item free from damage or future damage
| 1c87012a-efbd-54a6-b553-023a8f71292d | checkpoint | Has all parts i.e strainers, sumps and pits been cleaned
| 6da8f20c-6323-5f6d-9701-723ab846e7f9 | checkpoint | Is there further maintenance or parts required to complete inspection
| a3826728-fe0d-5393-bbfd-c6aec218395b | checkpoint | Photo taken and uploaded to report
| e512d915-5ea9-527c-a737-2a716b579d41 | checkpoint | Item left in safe working order
| 5efef70f-db9c-5079-ae83-d2b9e2041778 | checkpoint | Inspection Completed
| 4d75975b-ada0-47b0-94b1-1864704bd95c | textbox | Additional Comments
| 9d9dc818-662a-592b-be6d-19e03b083e84 | signoff | Click to Add Inspector's Signature
| d3df87d3-a998-5c08-b62e-8a7f749ba8e5 | checklist | QA (ITC) 8.1E; ITP A1.8 - Installation of Electrical Conduits Checklist |  | QA (ITC) 8.1E; ITP A1.8 - Installation of Electrical Conduits Checklist
| 9f64f9d3-f585-52bb-92ce-33f1c1345199 | checkpoint | Electrical Conduits Installation Report Details:
| 976a7e37-2885-50b4-9a71-c7453141da48 | textbox | Spec No.:
| 799c4ff0-c913-5754-85db-1c631f2dd348 | textbox | Drawing & Revision no.:
| 9f3b30c5-77f5-5a7e-a62e-33887f23c1ce | textbox | Shop Drawings no:
| f70715d2-2d1a-5b23-9d63-ec36fc1e2a50 | textbox | Zone:
| c4ffe7f3-f32f-5cbc-8283-c7269893acff | textbox | Starting IL established:
| 0483b4ad-eace-5baf-bdb4-af66eda812c3 | checkpoint | Conduits Lines
| 6d93e3ef-1594-58b2-a40e-bd23aff4f7c2 | textbox | Date started:
| 83e26c5e-719d-5c80-b998-6f922396102c | textbox | Conduit Line Number:
| 4131f6d0-de16-58c9-8e96-0ff10b849c24 | button | Bedding and Haunching | Yes,No
| 60fe69ad-c971-5ea6-82b5-648080b1e0f2 | checkpoint | Bedding material, placement and compaction meets specification.
| cfe5b3d6-55c5-5398-a86e-c2bca4fa4355 | note | Spec#: Electrical Specification
| 76ca3871-d336-58c4-9a6c-89b045e389c7 | textbox | Material used:
| 7d415809-0252-5322-ba5d-2c8423ff8642 | textbox | Docket #:
| 8f54b0f3-8de8-5e55-8ca7-39d8d077b8a1 | checkpoint | Conduit Instllation Checklist
| 6a3e2c80-0378-5646-9dd2-d91a1893c6c9 | button | STOWE Conduit Installation Checklist is filled in and attached | Yes,No
| b66248cf-c4f5-597a-86e7-d3e2293fcb44 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
| 497055be-5465-5571-9689-f53be3c80bfd | button | Stowe Group Signature Sign-Off added below | Yes,No
| 7fa0ebf5-e950-5139-bcb3-a84b181ab163 | button | Geschke Group Signature Sign-Off added below | Yes,No
| b615d4e1-2ab6-5c8a-b894-043e24c537d4 | button | BESIX Watpac Representative Sign-Off added below | Yes,No
| 2f62d8ef-8fc7-51e2-a37c-ad03a8e94e29 | button | Seqirus Representative Sign- Off added below | Yes,No
| 6ec1d577-3a5d-55a1-b557-23279c1a7b56 | checkpoint | Backfill
| e17dfc5b-6ed4-5b86-88a7-f47c6b53dc9d | note | Spec#: Electrical Specification
| eccf9a51-c5b0-5408-8c5a-840dad0ad91b | textbox | Material used:
| d5e24b82-d9fb-51c2-9350-0537d2cfefd5 | textbox | Docket #:
| 7831fb11-2368-5a11-b327-1ae1e2f71101 | checkpoint | Compaction Test Report
| 2b809eda-5ff8-53bf-a379-351ad2c492ad | textbox | Compaction Test Report No.:
| c64670d1-1b54-44f6-8c95-6a6cc8e16e2f | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
| c512ffa2-9b15-57c5-bf6d-c2d46bf9eb51 | button | Stowe Group Signature Sign-Off added below | Yes,No
| 8e973650-15a0-5000-8886-56a6a84eb3e4 | button | Geschke Group Signature Sign-Off added below | Yes,No
| f475d9ef-733d-5c74-b8f8-11ef8db4b5e1 | checklist | QA (ITC) 8.1F; ITP A1.7 - Installation of Electrical Pits Checklist |  | QA (ITC) 8.1F; ITP A1.7 - Installation of Electrical Pits Checklist
| 9c20f0de-9498-5b13-b2c9-51643e7a56b0 | checkpoint | Electrical Pit Installation Report Details:
| e6cd1a78-144a-5f77-b721-62867b2addf0 | textbox | Pit number:
| b936b1cc-421a-5b9a-92a8-f0731ba4f801 | textbox | Spec No.: Electrical Specification
| a15b0e98-ecb2-5790-a765-54ab569dff2d | textbox | Drawing & Revision no.:
| 9bc0a7a5-450e-58d3-b1ab-d0770a8b4669 | textbox | Shop Drawings no:
| 87a187c6-ef50-52bf-a34c-5b134bf4e37c | textbox | Zone:
| 35d41ae9-ce25-50fe-a004-d37e4d4474b7 | textbox | RL of the bottom of the pit
| 60fe69ad-c971-5ea6-82b5-648080b1e0f2 | checkpoint | Bedding material, placement and compaction meets specification.
| 4133d08c-e1c5-5803-8d14-d4b25256c01b | note | Spec#: Electrical Specification
| 28a35568-01e3-5f28-8c56-71163d8561ec | textbox | Material used:
| e444e53c-e650-5ff5-b127-522ddb6dcd99 | textbox | Docket #:
| a333af7a-1ed7-531c-94c5-fae29832113b | checkpoint | Pit installation
| e7b60cac-6f4d-5431-9034-4634c8ebc0d0 | button | Placement of cover | Yes, No
| 0c6de21e-0b33-52f9-b48a-b85b5aba2369 | button | Concreting of cover | Yes,No
| 759e7757-b7fd-5340-8121-0b2c742fd516 | checkpoint | Pit Installation Checklist
| f0be774a-e3bc-5440-a6a8-97d48cac6ed7 | button | STOWE Pit Installation Checklist is filled in and attached | Yes,No
| b66248cf-c4f5-597a-86e7-d3e2293fcb44 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
| ddc6b497-7ac2-5287-8eac-7d708736eb3d | button | Stowe Group Signature Sign-Off added below | Yes,No
| 6dc8f0db-d240-5e73-a973-554048a9beaa | button | Geschke Group Signature Sign-Off added below | Yes,No
| 285d65f3-5cfb-513c-91f4-5361c1249f1f | button | BESIX Watpac Representative Sign-Off added below | Yes,No
| 1afc22f3-94ff-530b-9bc5-749d13e09e1a | button | Seqirus Representative Sign- Off added below | Yes,No
| 6ec1d577-3a5d-55a1-b557-23279c1a7b56 | checkpoint | Backfill
| 5173203e-8df0-57cb-94c8-047e17628019 | note | Spec#: Electrical Specification
| bdb07636-ab1d-5b69-bc1b-e8002efc6cd1 | textbox | Material used:
| 75ff00f1-6588-5b38-a8d4-29c2fa12855b | textbox | Docket #:
| f87b5094-d0cf-5494-bcec-5c063e6507fb | checkpoint | Compaction Test Report
| 139a0cf0-87aa-57b1-963e-c5596094e0e1 | textbox | Compaction Test Report No.:
| 1c5c52ec-0786-4841-a9e6-9d423f8bd363 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
| 58852269-4222-5e76-a094-de8521a6bbbd | button | Stowe Group Signature Sign-Off added below | Yes,No
| f11162a2-c5d6-5fe1-a31f-2ab7c91dde54 | button | Geschke Group Signature Sign-Off added below | Yes,No
| 95205f90-fd02-5995-9077-97ac82efda45 | checklist | QA 4 - Installation Test Sheet (Waste, Vent, Downpipes etc.) |  | Installation Test Sheet (Waste, Vent, Downpipes etc)
| bbffbe63-d8b4-5952-9ad7-d75592a34e92 | checkpoint | Installation Test Sheet:
| 50010c6a-497e-5442-9047-6492ddcedc0b | textbox | Drawing No.:
| b6c19f8e-eb8a-53c9-b4e8-67dcd34fce06 | textbox | Rev.:
| 6c4bf7ba-2983-56a1-995a-4eaa6d91d10b | checkpoint | PIPE CLIP HANGERS
| 938ff211-8098-5850-9575-547557287724 | textbox | Details:
| 61a94842-7c6e-541b-bad2-1b3201e79bfb | textbox | Tester:
| b28b0af2-61aa-572a-ac1c-e3ca9ddd0b1a | textbox | Date:
| bf76422e-333d-5726-99d8-65920e82aec8 | textbox | Notes:
| 29d25cbe-4aa7-592d-b757-54dd70096c60 | checkpoint | MATERIAL AND SIZE
| 99c29d93-4585-59e5-aaf6-0a0732abe73b | textbox | Details:
| 0c553487-159c-5ffd-b6a3-067893b8312a | textbox | Tester:
| 6d13be7e-a92e-5f79-a73b-929f25b82f73 | textbox | Date:
| 9421d903-7af1-5d2c-a7f9-fbd2aabb05b0 | textbox | Notes:
| b306a341-3433-5336-81ce-0301f9ca9bb8 | checkpoint | ALIGNMENT
| 77660e0b-d569-505a-a31a-b220d1e993a5 | textbox | Details:
| 7d17e639-b3a4-5a7d-9976-ad0cb2ac69f8 | textbox | Tester:
| ceb4259c-3937-598d-873e-fa47ea3ed01a | textbox | Date:
| 70aa940b-9f9a-528e-9295-a408b66037d5 | textbox | Notes:
| 56f12a8e-7e85-5747-af83-274fc1392d83 | checkpoint | LABELLING AND IDENTIFICATION
| b0528441-550f-515a-b6ee-03333d09591b | textbox | Details:
| bda1a7d3-9a71-53af-a354-ceab8bfc2f14 | textbox | Tester:
| 5e844718-ee95-5f26-bb04-7995b0a5b725 | textbox | Date:
| d1ca136a-b3f7-5a7e-a325-b9abd3f25d26 | textbox | Notes:
| ae12828b-92fe-55a7-92e5-d9c87f98cb80 | checkpoint | JOINTING
| 09df9ddf-ee35-57ba-9a0e-1d4ea48284f8 | textbox | Details:
| 2080e1ce-7158-562c-b028-f2e362dd17c2 | textbox | Tester:
| 1caad794-5e16-5e67-89ab-308b732a129d | textbox | Date:
| 650f6886-eeb2-52dc-9c74-db0e726bfdbd | textbox | Notes:
| fde925e3-67b3-5a13-b700-5f5b4e5fd14d | checkpoint | PENETRATION SEALING
| 5fec8545-0bd5-5769-b785-5886e48e0a2d | textbox | Details:
| d5687398-72b2-5175-9227-11829ada762c | textbox | Tester:
| 08552a3d-e64e-5352-a0fd-87d9cce07ff2 | textbox | Date:
| 796b720d-7223-58d3-bc3b-74f444f1c736 | textbox | Notes:
| d0c5e9ea-c239-5c52-a6ed-6c2a4209ac90 | checkpoint | FIRE STOP COLLARS
| b1de19e6-6232-586f-8acc-ab7e8e91002e | textbox | Details:
| 13acb819-4a2d-5ae0-aa5d-f0463cf81883 | textbox | Tester:
| 721432cd-fd09-53f0-a61f-eaffa6e93089 | textbox | Date:
| 9cd6ac9f-62df-55b4-85a2-4ee5f0385d38 | textbox | Notes:
| 11221f52-ebf2-524c-8569-a9ad457365f0 | checkpoint | TESTING
| 2a8de8f4-e50e-58a0-a6f9-4ff82aff92b5 | textbox | Details:
| afff0e22-f456-5c83-85cb-657a96c4b0e2 | textbox | Tester:
| 67f96e93-463c-5056-832b-34fee4b4b963 | textbox | Date:
| c891d953-500a-55fe-af4d-2cc4ca4434a1 | textbox | Notes:
| c2557bd5-4311-5506-9a22-c4ea2f07dd74 | checkpoint | AUTHORITY INSPECTION (if applicable)
| 84adf893-0c43-57df-ac7f-6579c80dfe92 | textbox | Details:
| 898a8d40-cb8b-5a3b-9a3a-39f5585b4a52 | textbox | Tester:
| 4b973924-17ce-5584-b35c-4cc2d19bb4ba | textbox | Date:
| cdbedb38-df79-5a4d-b1fd-36b980b5e7aa | textbox | Notes:
| efa173e9-5e85-5a3d-8e9d-c5a1880b62d8 | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
| 3fc1722d-62e9-5876-ae82-146959941991 | textbox | Details:
| f375dc1b-3bfa-5c81-8ee0-5872cec70607 | textbox | Tester:
| 5d2a97de-b848-59d4-b966-2e1aafd650ac | textbox | Date:
| d1f47705-35b0-54c6-8286-0a94093f6635 | textbox | Notes:
| 91836b11-1ea4-566c-a311-6be185a6d10d | checklist | QA 5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  | Installation Test Sheet (Cold Water, Hot Water & Flusher Line)
| bbffbe63-d8b4-5952-9ad7-d75592a34e92 | checkpoint | Installation Test Sheet:
| 3ab24f75-839e-5feb-8634-746ace1f5ec0 | textbox | Drawing No.:
| a27b0c19-c337-506e-b01c-bd672377243d | textbox | Rev.:
| 6c4bf7ba-2983-56a1-995a-4eaa6d91d10b | checkpoint | PIPE CLIP HANGERS
| 8c6d265d-72c8-5004-8826-735678e11270 | textbox | Details:
| c9f33966-4235-5d2c-a642-55dfe9387742 | textbox | Tester:
| a23e1ec7-52f8-5620-a7d7-b2bddcda1640 | textbox | Date:
| 8b10b5a1-ede7-5467-be9c-8756e0fad657 | textbox | Notes:
| 29d25cbe-4aa7-592d-b757-54dd70096c60 | checkpoint | MATERIAL AND SIZE
| 85f2a050-6afa-5632-828b-afe3efe2bff8 | textbox | Details:
| 6c47264b-1054-5e3b-a3c7-ae22638da042 | textbox | Tester:
| 2306a096-48bf-5628-8f85-1ab5cb86ca41 | textbox | Date:
| d31e1f32-415e-5ad2-8d6a-f453efef7a00 | textbox | Notes:
| b306a341-3433-5336-81ce-0301f9ca9bb8 | checkpoint | ALIGNMENT
| f5e906a4-c6cd-5d02-9781-85aebcb826de | textbox | Details:
| 730d0518-46a4-5cc3-b078-51778c4b8d8b | textbox | Tester:
| 204d18fb-5407-5e02-9e0e-772c5a3c2e52 | textbox | Date:
| b167628e-1b40-523f-a9b9-9bc950edd00e | textbox | Notes:
| 56f12a8e-7e85-5747-af83-274fc1392d83 | checkpoint | LABELLING AND IDENTIFICATION
| 5abc4733-91e2-5ea4-b265-e7c6756baa16 | textbox | Details:
| 8974f3be-8334-55cc-af4a-2bb675612ded | textbox | Tester:
| 84bad23e-8903-5866-897e-c0413010add4 | textbox | Date:
| a0ca3daf-c85a-5c24-aea4-1ecc86442a29 | textbox | Notes:
| ae12828b-92fe-55a7-92e5-d9c87f98cb80 | checkpoint | JOINTING
| 913fc093-f4bc-54b9-a317-bfecc43b50f6 | textbox | Details:
| 519b6096-c428-5344-a043-a484cd7e9880 | textbox | Tester:
| 905fa5ed-ce72-566f-9b3f-fac78692c228 | textbox | Date:
| 04a550b5-9486-5356-b2fb-30fa1a7ccefc | textbox | Notes:
| fde925e3-67b3-5a13-b700-5f5b4e5fd14d | checkpoint | PENETRATION SEALING
| 9be6327d-0481-5941-bb4a-5bf15dca51b7 | textbox | Details:
| c85eca5d-c701-55e4-a5af-08a875a2a68e | textbox | Tester:
| 743a8e40-3b63-5297-867f-405fbe2667c6 | textbox | Date:
| 7e580f26-9c6e-504a-87da-e436fdd65de2 | textbox | Notes:
| d0c5e9ea-c239-5c52-a6ed-6c2a4209ac90 | checkpoint | FIRE STOP COLLARS
| 0200e894-a180-549e-9b0c-989540dd4e67 | textbox | Details:
| 9aa43dfe-a906-5bad-8885-4b764f7e21b7 | textbox | Tester:
| 2a9328f3-06bf-5b16-8c56-3b079327bc60 | textbox | Date:
| ab52bfac-c6dd-5de8-b64a-19a4de88067d | textbox | Notes:
| 6b9e46e7-ca72-5039-bd7c-8708adfc0365 | checkpoint | PRESSURE TESTING COMPLTED (QA6)
| af5b740e-faef-5789-a3ae-8f61f4fdc16d | textbox | Details:
| 055e2025-36cb-5358-b845-3077ed4db718 | textbox | Tester:
| 657b7f34-25e2-5b91-8a7b-58724dae4629 | textbox | Date:
| a766b5a7-0571-5221-8413-f0f52772285b | textbox | Notes:
| c2557bd5-4311-5506-9a22-c4ea2f07dd74 | checkpoint | AUTHORITY INSPECTION (if applicable)
| 2515ced0-5814-5994-b676-f17015782dfb | textbox | Details:
| 1821d907-771d-5c8a-86d7-56dceb371f87 | textbox | Tester:
| a096b3af-3fc2-5ee8-9433-4cdcbaaf1aa4 | textbox | Date:
| c0fd3aac-4831-56b5-9961-9b4fa4a1637a | textbox | Notes:
| efa173e9-5e85-5a3d-8e9d-c5a1880b62d8 | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
| 3f7c901e-6389-5596-a074-565185b26a1a | textbox | Details:
| 41b3f8cd-36a1-5dc1-8c11-361431372622 | textbox | Tester:
| 77f1edcf-168c-5878-978b-5ce8cfa53139 | textbox | Date:
| d9dcab85-f7b9-5291-86ae-31dfa9e23d03 | textbox | Notes:
| 62625ad3-e09e-522e-a81d-22149d4864d8 | checklist | QA 6 - Quality Control Pressure Test Report |  | Quality Control Pressure Test Report
| 4114736c-2d08-5a3e-ab7b-04288eaa2c81 | checkpoint | Quality Control Pressure Test Report:
| 763fb90a-77bd-530a-b6df-f09df5777087 | textbox | Drawing No.:
| 377238ab-017c-5bf4-a86c-fd0a05fc475c | textbox | Rev.:
| ef171ad8-9030-5a90-b621-10466e7e971f | button | Test: | Air,Water
| 78b5cfbc-0b1e-5857-badf-8bef5677741b | textbox | Section
| e593cb21-9700-5405-9c45-7a192a0b9b52 | textbox | From
| 96816a98-8b0f-5e90-9d26-582360018db8 | textbox | To
| 779c7016-ce0a-5f4a-8a04-2ac7cbf79cb9 | note | Specified System Working
| c1866042-532f-537a-9637-cd9a1ab947d1 | textbox | Pressure (KPA)
| 2a580541-ea39-55db-b94e-93e2d5bc073e | textbox | Duration (HRS)
| 752bf769-b934-51aa-af8a-8e9706d24599 | note | Specified System Test
| 421be4fe-6ef0-5846-8e48-808c8cc96a3d | textbox | Pressure (KPA)
| c9b007dc-a936-53c4-ab20-fe1e1a046f3a | textbox | Duration (HRS)
| 1dde2b84-4574-5682-aacc-8adb31a1fda5 | checkpoint | 1st Reading
| 329e9c81-74de-5c4f-a364-de758d416404 | textbox | Time
| 692d5b19-1191-5d41-b5ba-b6712b4cb2b2 | textbox | KPA
| 65a3f29e-e8e0-5d9e-b114-84eeb16dc30c | textbox | Ambient Temp
| 6a22ddb1-0102-5030-a26b-315ec1394bb7 | checkpoint | 2nd Reading
| c4677bc9-425a-511a-93f2-24fe2225546d | textbox | Time
| 81d6c326-30e4-5390-afd9-ab54e48cb0cb | textbox | KPA
| b230e7fb-2924-5453-bbae-ed90b51cd7d4 | textbox | Ambient Temp
| 59382eed-be99-5466-be0a-acadd7d1c05e | checkpoint | Test Result - Passed?
| 8a353ae8-0c9a-5e49-936a-7b86c2c57803 | textbox | Repeat
| 3ceadcd6-d779-5c97-8426-53dd865a89c4 | checkpoint | Sign Off
| dd6f186b-67e9-5218-bc00-7f9ecceb30ff | textbox | Geschke Pty Ltd. Representative
| c7fd4486-479e-5db0-905f-1c6d91cc5207 | textbox | Others Present
| 92abec15-c9d1-5554-9e19-262c60d28f74 | textbox | Date of Satisfactory Completion
| 79ab1221-9f44-512a-bfef-2ae51e4a1850 | checklist | QA 6D - Quality Control Gas Regulation Test Report |  | QA 6D - Quality Control Gas Regulation Test Report
| f4e97549-b4d3-5f31-8888-864555bc2e08 | checkpoint | Quality Control Gas Regulation Test Report:
| b2474475-47ea-597c-8878-544232a4436d | textbox | Drawing No.
| ed2e8944-0c4a-52db-9894-3c339e0c4c53 | textbox | Rev:
| 5784d677-b4c2-5460-b7f2-1caf57ff9d55 | checkpoint | Test - Flowing inlet pressure to project
| b537697e-f43a-5a6f-994a-191577a42caf | textbox | Inlet Pipe and Size:
| 006efab9-0f46-5811-b8d6-e42e873e4771 | textbox | Spring range:
| 74dacd66-d2b5-550f-8945-576709d4ab8e | textbox | Orifice Size:
| 2ec37cb5-2073-524c-b468-28384a70ba40 | textbox | Model:
| 343543a7-4a57-50ae-a5b2-be8518821d54 | checkpoint | Section
| 8ea0efb3-15f5-57db-9f52-72ae9d5429e6 | textbox | Section:
| fb0b5590-2bc7-5d62-b23e-dfe24567ee80 | textbox | Pressure (KPA)
| e235452f-b0d3-5957-9e8f-9ec23c474c5a | checkpoint | Test upstream inlet pressure to regulation
| 3b56a1ec-b6a5-569a-96a0-1bd2cc5523fa | textbox | Pressure (KPA)
| 300c5ab3-6ae7-5638-88a9-d0cf8a32282f | checkpoint | Test downstream out pressure to regulation
| b6671b47-9467-54b0-8646-eb78feb3f51f | textbox | Pressure (KPA)
| 0972ae5d-db47-56d7-9012-d89f2015ce44 | textbox | Duration (hrs)
| c1fb9e1a-2101-5f9e-bf77-72fab365bc43 | checkpoint | Adjust out pressure KPA as stated on GPL shop drawings
| ea5f6265-653d-5a55-859f-5464cc7ff375 | textbox | Reading (KPA)
| 38b3faf8-1274-5f6b-a5bc-00ab1f6d7aeb | checkpoint | Confirm outlet KPA does not fluctuate more than 0.8KPA
| 1430adac-1555-59a0-8559-5093ac692453 | textbox | Repeat:
| 3ceadcd6-d779-5c97-8426-53dd865a89c4 | checkpoint | Sign Off
| 9939deb9-66c8-562a-a833-77d66f1060b1 | textbox | Geschke Pty Ltd. Representative:
| 80d7b81a-d4d1-523c-b839-9ba824c6d170 | textbox | Others Present:
| fbed0f45-5d5d-52e0-923c-ff33638b9491 | textbox | Date of Satisfactory Completion:
| 8b7b2956-7179-5850-a84f-80a41f74e47d | checklist | QA 7 - Commissioning Test Report |  | Commissioning Test Report
| e4899f25-d436-5b4a-b4c3-dd5cb6b2362a | checkpoint | Commissioning Test Report:
| d327703b-f3ba-539b-b251-1bdae31b11c9 | textbox | Zone/Grid:
| 8ae0555c-198f-58d7-96f1-34792d52d64d | textbox | Drawing No.:
| 036bd35e-308e-50b4-83a8-10b735e5014c | textbox | Rev.:
| 020f181c-f792-55c0-b912-56202f3cdf0a | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
| 20eb13e0-a11b-584b-9ebd-a15417a134c9 | note | Test:
| 3db11513-05c7-532b-bf55-bbe4827a2d9d | note | Performance Test CL 2.20
| 0d887cae-55e9-588e-b235-627fdc5d12a2 | note | Fill fixture with water remove plug
| 53e6629a-e167-5ba9-abb0-d6d8c9c0032f | note | Test for:
| 648a4c5e-2393-5020-8f35-eddfe179e4a9 | note | Leaks
| 013055b0-bd75-5aa6-92df-0cac740afe59 | note | Loss of water
| d293626f-d41b-5f0d-a1e7-4d20db791d6a | note | Seal in Trap
| 133d001f-2654-5fff-bbc6-13c0a0704435 | note | Induce siphonage in trap of adjacent fixture
| 20c8db35-41ba-50cb-b99e-5f79d25f9629 | note | Complete draining of fixture
| 31b8d3d0-2c0d-527d-a988-2732a1665c5f | textbox | OK:
| 7316e753-a568-52c8-ad94-1fe21ca06772 | textbox | Not OK:
| 431ab26f-1b7b-55ad-a431-4e10dad53284 | checkpoint | Item: Water Supply
| 67c87bc5-d6b0-5c1d-9155-8433a522d136 | note | Test:
| 2d614b85-72c4-5b5c-adfc-d0c3c663cca9 | note | Performance Test CL 2.20
| b250e969-b551-5d80-be4b-dffa7693ca9a | note | Check for adequate water volume.
| 73abf86f-25d8-595d-b0a6-75317c670dd1 | note | Flush out pipework
| 452b504a-081d-59c2-ad5c-10618af31089 | note | Clean aerator
| ae730b29-0279-579f-8f30-919295fd7d51 | note | Water hammer
| 30e248a3-9146-5ac6-ab8b-e9ce68ed56dc | textbox | OK:
| ecd810a2-8f89-5453-95ae-8d9c6982aae1 | textbox | Not OK:
| 5fb85726-ea98-588d-b15a-923847490066 | checkpoint | Item: Flush Performance
| c9949532-2826-5289-8b56-aab0ff1a7b0c | note | Test:
| b843bc61-cc18-5cbf-9683-a9b62bfc4e59 | note | Performance Test
| 0f892e15-28b1-5230-9deb-3ac3e1966196 | note | Check for:
| 38ece3ca-011e-5795-9208-065bd616d4c6 | note | Water Volume
| dc85abcd-fc9b-50da-a62b-2e6fe40476c8 | note | Duration of flush
| 0aee1722-0560-553f-bb4c-bf1ee62c2a5e | note | Flush out pipework
| 9ae2a9d6-01d8-5d88-8008-cdbb6dee0b7d | note | Water hammer
| 3c4f2bd7-2a10-5147-bbe5-c1f81fb7673f | textbox | OK:
| db3a6357-1846-5330-9f4f-e5142d47ff66 | textbox | Not OK:
| 12c36d30-1d36-54aa-9a51-c192e19f7df5 | checkpoint | Other
| 12ccc2c8-0868-526a-ad02-cdba0d0be6c5 | checklist | QA 8 - Below Ground Pipework Checklist - Fire |  | Below Ground Pipework Checklist - Fire
| cb139adc-ed6c-5041-bfab-ea116df4cd15 | checkpoint | Principal Contractor Permits Issued
| 1ea4ee4c-7477-5816-a44b-ce9f32895a8a | checkpoint | Set out pits depths and trench runs.
| 05cc5510-efff-5b7d-967b-74d6c9831a02 | note | As per DRG#
| 4462d17e-6ffc-5818-9d3a-23aa6a83929d | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
| f8d895c4-538c-501d-94ea-9a93c913af7e | note | Spec#: AS3500
| da8e774e-5ba3-5829-876a-ffa9c0fde3c0 | note | MDPE SDR11 PE100 PN16
| 256f4eaa-27e3-566c-a6ad-2db2ce3d7b3a | checkpoint | Bedding placement and compaction and material meets specification.
| 1d684ccd-9a4a-5814-b8cb-f34c4a847823 | note | Spec#: AS3500
| 6b2b018c-9049-56a8-94da-c684839f2733 | note | Packing sand encased pipe
| d4397ce2-63ef-5949-b39f-a0c867c3aef6 | checkpoint | Jointing of pipes
| e059a789-b443-5d83-988b-b18f28d995dd | note | Electrofusion and/or Butt Welds
| c94dfc17-099f-5a1b-9db1-edc9e82f0a8b | note | GPLQA16 form
| 98c91393-bc7b-56bd-903c-92654de5d0b5 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
| 15cedaaa-9380-5d2e-8226-032042d9508f | checkpoint | Hydrostatic tests are carried out as required.
| 3291b180-c40a-54b0-96ed-a62b051bef13 | note | GPL QA6 form completed
| 895a72af-eba2-5f7f-9ad9-e03b939d4598 | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
| 4b8b1bb6-f90c-5cf2-997a-2b7103b36201 | checkpoint | Placement and compaction of backfill and material meets spec.
| 22e48b2a-9b2b-5246-ab0e-09f290be5adb | note | Compacted crushed rock backfill 80% to 100% compaction
| 9919140f-7dbe-519d-bc48-1107cdfc1ec5 | note | Detectable marker tape
| 24589acd-8747-5b15-8162-b11266c7ec2e | checkpoint | Temporary cover provided to open drain.
| a0d9f762-129d-5d01-bd91-a2a4ed9aff34 | checkpoint | PVC/ Plastic caps to open ends
| fd863736-f39d-5803-86a2-8d75a179c74e | checkpoint | As built information updated onto drawings
| fc897ea4-9347-5687-b049-5e4b9bbd7e46 | note | Ongoing
| cd74ba9a-0e4e-5ae2-985d-71027ffc3f0a | note | To be provided
| b9df4eb4-d28a-55f4-b158-c6a6dc8d640c | checklist | QA 8 - Below Ground Pipework Checklist - Sewer |  | Below Ground Pipework Checklist - Sewer
| cb139adc-ed6c-5041-bfab-ea116df4cd15 | checkpoint | Principal Contractor Permits Issued
| 1ea4ee4c-7477-5816-a44b-ce9f32895a8a | checkpoint | Set out pits depths and trench runs.
| c9361086-e05a-53b6-8dea-dc67b362ba0d | note | As per DRG#
| 4462d17e-6ffc-5818-9d3a-23aa6a83929d | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
| bbb7ff83-9750-5977-a62a-c638a1d6ad34 | note | Spec#: AS3500
| c93c2f8a-b7e6-5087-ba22-3138f0a6d89c | note | UPVC BEP Type ISO 14001
| 256f4eaa-27e3-566c-a6ad-2db2ce3d7b3a | checkpoint | Bedding placement and compaction and material meets specification.
| 058ebf27-f9ab-598d-94a6-cd2b0c236eae | note | Spec#: AS3500
| efec87f9-cd11-5589-8894-6f7d0af1d1a6 | note | 75mm Q-Minus Bedding and Encasement to top of pipe
| 7cf18408-5733-5045-a1c1-59bfec1ff228 | checkpoint | Laying and jointing of pipes R.Ls and falls
| 31379af2-dcb6-5b37-996c-69b600d27b52 | note | PVC solvent welded
| d0cd148a-b809-5cab-afba-5c8a51524399 | note | 1:60 fall
| 18548ed8-1e5a-5a76-bd87-25571cb4aad8 | note | AS3500
| a4ad503d-d291-5b62-b618-a4aa6436da95 | note | RLs as per hyd drgs
| 0628b96f-0911-57b3-8c8a-346bf56700a2 | checkpoint | Connections to pits and existing services
| 15cedaaa-9380-5d2e-8226-032042d9508f | checkpoint | Hydrostatic tests are carried out as required.
| 46b0621b-9913-5855-a981-0a4d96382e79 | button | Air or Water? | Water,Air
| a1ba283a-d239-51fc-a72f-6251909912a1 | note | Inspected and recorded by Independent Certifier or PIC
| 81dda1d1-d4ab-5f78-9631-5a7b86865892 | checkpoint | Mirror tests are completed if required.
| 4b8b1bb6-f90c-5cf2-997a-2b7103b36201 | checkpoint | Placement and compaction of backfill and material meets spec.
| 7d47f2a2-f0b2-5045-b631-538e4abfbe19 | note | Compacted crushed rock backfill 80% to 100% compaction
| 24589acd-8747-5b15-8162-b11266c7ec2e | checkpoint | Temporary cover provided to open drain.
| a0d9f762-129d-5d01-bd91-a2a4ed9aff34 | checkpoint | PVC/ Plastic caps to open ends
| fd863736-f39d-5803-86a2-8d75a179c74e | checkpoint | As built information updated onto drawings
| a742f916-dced-5d3a-8374-2369f82cb9f5 | note | Ongoing
| 4ae5b7bc-a705-5f39-9862-7bc4dc7d0a2e | note | To be provided
| 0105620e-0310-5460-ac00-9f9ea789cad2 | checklist | QA 8 - Below Ground Pipework Checklist - Water |  | Below Ground Pipework Checklist - Water
| cb139adc-ed6c-5041-bfab-ea116df4cd15 | checkpoint | Principal Contractor Permits Issued
| 1ea4ee4c-7477-5816-a44b-ce9f32895a8a | checkpoint | Set out pits depths and trench runs.
| 40f29d7d-0120-5e89-a77f-50955023c5c9 | note | As per DRG#
| 4462d17e-6ffc-5818-9d3a-23aa6a83929d | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
| 7a601a81-a178-5389-ab08-464b5a7033ac | note | Spec#: AS3500
| 53e01994-00e1-5ad6-9870-7a39edecc4dd | note | MDPE SDR11 PE100 PN16
| 256f4eaa-27e3-566c-a6ad-2db2ce3d7b3a | checkpoint | Bedding placement and compaction and material meets specification.
| 10ba4b7f-0b16-50a8-aefa-b1428be83029 | note | Spec#: AS3500
| 3a1062af-a6bc-5032-a50a-47bdb3995511 | note | Packing sand encased pipe
| d4397ce2-63ef-5949-b39f-a0c867c3aef6 | checkpoint | Jointing of pipes
| 5d978e97-0d8c-51eb-a124-0af76135aaaa | note | Electrofusion and/or Butt Welds
| 04ac4e16-5f21-51c5-b0e4-c1385f068f80 | note | GPLQA16 form
| 98c91393-bc7b-56bd-903c-92654de5d0b5 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
| 15cedaaa-9380-5d2e-8226-032042d9508f | checkpoint | Hydrostatic tests are carried out as required.
| f16668c0-ba51-514c-8fda-63afd035b38e | note | GPL QA6 form completed
| 8c445b5e-b26b-53f6-9052-d025369c627e | note | Water system tested to 1400 kpa regularly prior to finished surfaces are completed.
| 4b8b1bb6-f90c-5cf2-997a-2b7103b36201 | checkpoint | Placement and compaction of backfill and material meets spec.
| 6b6e5966-aa91-5be6-8423-40f93b30924c | note | Compacted crushed rock backfill 80% to 100% compaction
| 7a093a69-fcab-5e43-9f9c-d8e5718044d1 | note | Detectable marker tape
| 24589acd-8747-5b15-8162-b11266c7ec2e | checkpoint | Temporary cover provided to open drain.
| a0d9f762-129d-5d01-bd91-a2a4ed9aff34 | checkpoint | PVC/ Plastic caps to open ends
| fd863736-f39d-5803-86a2-8d75a179c74e | checkpoint | As built information updated onto drawings
| 6214f64b-0928-579a-86f7-b78e056e74a7 | note | Ongoing
| 746f7a87-8783-519b-b398-d56de5a7cba0 | note | To be provided
| 97ba0381-6cb5-5bf8-a62e-23d2d2e697b6 | checklist | QA 8A - Grease Trap Checklist |  | Grease Trap Checklist
| 0da94e96-2ff6-5ffd-9b6d-867a3a40f11b | checkpoint | Set out of pits.
| 4462d17e-6ffc-5818-9d3a-23aa6a83929d | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
| 256f4eaa-27e3-566c-a6ad-2db2ce3d7b3a | checkpoint | Bedding placement and compaction and material meets specification.
| 7cf18408-5733-5045-a1c1-59bfec1ff228 | checkpoint | Laying and jointing of pipes R.Ls and falls
| 748c14dc-2921-5325-9f13-b4f4eb85a61b | checkpoint | Connections to pits.
| 628010a8-0292-55df-92f0-d530ff57a0b7 | checkpoint | Baffle is in place.
| 6ba649e9-6077-5909-9762-6822031f4304 | checkpoint | Penetrations are patched and made watertight.
| 48729f8c-e144-5706-ba4b-b81dba902db1 | checkpoint | Suction line is installed as per spec.
| 43971bc7-c3a9-5dd4-8709-ed7875fba374 | checkpoint | Outlet pipework is installed as per spec.
| 000e6a43-38ba-5b77-9d8f-f2995ad02935 | checkpoint | Vents are connected and terminated to comply with Authority and Specification.
| fd863736-f39d-5803-86a2-8d75a179c74e | checkpoint | As built information updated onto drawings
| 16eae0ba-4ca1-5be3-bd1f-ba7aba5bcf94 | checklist | QA 8B - Stormwater Drainage Inspection Report |  | Stormwater Drainage Inspection Report
| a3aca50c-c3f9-5547-a3c3-9aa3c18d0f7e | checkpoint | Stormwater Drainage Inspection Report Details:
| 96534a09-78d5-566b-8e1c-bd616900d8aa | textbox | Spec No.:
| 691a3f85-b396-508d-8efa-b875ee0fa6ed | textbox | Drawing no.:
| b3a97a71-3ade-5cbd-af56-6bba0d0dcf33 | textbox | Zone:
| 12155208-a68a-5d03-8316-c468bf985170 | checkpoint | Pipe Lines
| f0081876-5cf6-5338-ac67-5f20f2359cb8 | textbox | Date started:
| b7047d37-73f5-51b3-aa56-cff3da21a05f | textbox | Drainage Line Number:
| 42206922-8550-505e-b6f1-25ebca54b913 | button | Pipe Damaged? | No,Yes
| 6b87f441-6a74-5296-9ee3-6527a92c5422 | textbox | Size and Class
| 7b89114d-5a43-5a0d-92f2-feba9d0ed240 | textbox | Jointing Required
| a05abd2a-2e04-5664-992c-368b2c9edd4f | note | Bedding and Haunching
| e4724d19-7eca-55e5-960b-780346b59511 | textbox | GPL - Initial/Date
| d2f79eb3-0cbc-53fa-a115-32baa246211e | textbox | Builder - Initial/Date
| 5724832d-4831-5e66-9f88-0f2666e7e6d8 | note | Backfill
| daf9dd11-559d-5e43-92f1-8038f4cda23f | textbox | GPL - Initial/Date
| f0283aee-c6b8-5ffd-b05f-ea1205d24304 | textbox | Builder - Initial/Date
| a30725fa-ff75-50f3-9a99-747b51571cd5 | textbox | Comments
| 21d4c3ec-faa4-5407-ab6e-ea5db3092822 | note | Final Sign Off (Initial & Date)
| c554b75e-1cd7-50a1-b934-401436b07030 | textbox | GPL
| 8f71769b-df8d-5a7c-be1e-094c9078a8ce | textbox | Builder - Initial/Date
| 45fbabb3-bf51-568e-b94b-64c544f33f52 | textbox | HCC/CARDNO
| 31d259a7-f4a3-527a-a915-69499139a502 | checkpoint | Drainage Pits
| 41bfac3e-e736-53f8-a3c0-b67390f7097a | textbox | Date Installed:
| 8872d2a8-c6de-5d27-80ea-3ec21cdcbd16 | textbox | Pit Number:
| f4d320f3-03aa-53f9-b2c0-098e79891a93 | textbox | Pit Base:
| ee317b6c-3f45-54e0-8947-b251c820fb40 | textbox | Step Irons - GPL Initial/Date
| 6b391512-d547-5e5b-a486-7eef0619bdd0 | textbox | Bedding - GPL Initial/Date
| ca144f5a-75d9-56d5-a210-f5900948dc2d | note | Benching, Grouting and Patching
| 2364d5e9-152f-52be-bf4b-cc1844ae4d93 | textbox | GPL - Initial/Date
| d5fe73bf-85ab-5a4a-bf20-927ca8527627 | textbox | Builder - Initial/Date
| ccbd4ec5-df79-5890-bf63-afa05fdb7700 | note | Placement of cover
| 2b12ae14-47fd-5bc2-9c2d-7ab41bb11841 | textbox | GPL - Initial/Date
| 60cec653-e084-5222-9f07-83b41782e285 | textbox | Builder - Initial/Date
| bcd954dd-99df-5aab-801e-a58d959e3274 | textbox | Comments
| 0003d9fb-8379-5766-ad9d-05f3f690c457 | note | Final Sign Off (Initial & Date)
| 169ef68d-afd4-5080-8b58-fffabddf8e73 | textbox | GPL
| 20d519a0-a401-5505-a07f-f42d745dd0d9 | textbox | Builder - Initial/Date
| f85e9d55-97b8-5d67-8142-8c01c4722b13 | textbox | HCC/CARDNO
| ea3bbafc-8635-5a77-867d-d34c2fa3ddcd | checkpoint | Compaction Test Report No.
| b3985592-ee51-5330-9b1c-d05267d1e755 | textbox | Compaction Test Report No.:
| 00d279f7-4c10-5994-9fa6-fb85ee3b1c7c | checklist | QA 9 - Non-Conformance and Rectification Report |  | Non-Conformance and Rectification Report
| 3dbb6f2e-c870-5aa5-87b6-39ec9cfa4da3 | checkpoint | Non-Conformance and Rectification Report Details:
| 497480bc-16f9-57d1-a38d-b53f285ead12 | textbox | Drawing No./Rev:
| 6c7020c8-cb4b-5056-aedc-1eda68789ef9 | textbox | Zone or Grid:
| c1b1944f-9e73-5dfc-85e7-ed80a4769931 | textbox | Issued To:
| ec26a073-1fc2-5a02-a43e-1a4975f7246c | textbox | Item Not Conforming
| 0344f07b-d886-595d-ac05-a2e52a3647ab | textbox | Reason For Non-Conformance
| 6a8fe17b-aeec-5947-a7ad-703f786a7e75 | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
| 162acb0a-6221-5ed8-b32e-8bf9074941a4 | textbox | Action Required:
| 49bb3ead-9d10-58ba-b134-b5dc0c361c05 | textbox | Date:
| 41c65d3b-845e-51e2-b40e-83856850ea32 | textbox | Rectification:
| b80c061a-a1e2-5ec9-a894-87917f2ade88 | textbox | Date:
| 2942d0e2-7101-5037-8548-4a3587576906 | note | Note: Non-conformance register to be updated
| af4c34c3-620e-5cf6-89ef-3fb11c6178c2 | checklist | QA 11 - Equipment Calibration Register |  | Equipment Calibration Register
| a0b01591-964f-5515-85c6-7f96b57877d7 | checkpoint | 1
| b4d2c565-6cee-5beb-9f2a-9a346000f629 | textbox | Equipment Type:
| be6ab2aa-d446-582d-a849-bfe836eb24eb | textbox | Manufacturer:
| 47593f44-3f6c-5547-84c2-26e0bbe47831 | textbox | Model and Type:
| 5941931a-1aa8-58e8-be93-967243c88d47 | textbox | Serial No.:
| c86e3e82-4a80-595b-9779-716c2b19f620 | textbox | Next Service Due:
| 80eb3b16-184b-5f92-932d-71403b994572 | checkpoint | 2
| 0306dcf0-68f3-549c-9016-f7af3b1c6ec3 | textbox | Equipment Type:
| 33c0b8b5-8807-5a36-8e57-78e3b2cffd0b | textbox | Manufacturer:
| 9bc41edb-c3df-5933-9cb9-88e19a0a352f | textbox | Model and Type:
| 95d17765-6174-52b6-af43-d2574c3cf7c2 | textbox | Serial No.:
| 974f94f4-32e3-5b07-b53e-96a207c4e5a9 | textbox | Next Service Due:
| 7a173f6c-500c-553d-b74a-85afb565eb50 | checkpoint | 3
| 76a02e6d-6074-56d0-87c9-bedee5e2fd92 | textbox | Equipment Type:
| 191cf691-0333-562f-84d4-a19180c8c35e | textbox | Manufacturer:
| f4614282-7975-5463-b1d2-174c3a96397e | textbox | Model and Type:
| c30ae13d-364b-5dbc-b392-cb79271ea4f3 | textbox | Serial No.:
| 52bb628b-cc74-5d15-9174-7a2093a79f63 | textbox | Next Service Due:
| b911b1b9-6725-5360-8e28-f6a01e7ce249 | checkpoint | 4
| 3707671d-ca0d-57a3-adeb-787ad49847d6 | textbox | Equipment Type:
| 6b916005-e6be-5e93-abc6-40dfef2a82c7 | textbox | Manufacturer:
| 2ae7293d-67a1-55c5-8559-1f1c7f0191b0 | textbox | Model and Type:
| 2b5afd9c-bed7-563d-9fba-8740e3731118 | textbox | Serial No.:
| b1afa72f-9aca-5386-9ef9-0af842e99e74 | textbox | Next Service Due:
| 24dce8d0-3e3b-5c3c-b560-2a93082053b4 | checkpoint | 5
| 069ace06-2f9e-5ec9-b970-a842724880ea | textbox | Equipment Type:
| 29c5bf83-58d0-556f-92ca-4404d9c3b2bf | textbox | Manufacturer:
| 3f11dbde-edf2-5bbd-8c1a-ca5495acda6f | textbox | Model and Type:
| 502d77c5-8f9b-582c-8fe8-11abd0c65c6f | textbox | Serial No.:
| bd6fb2a4-219a-5322-ba03-0382fa934a03 | textbox | Next Service Due:
| e4ee39db-2ed2-56d4-9d1e-70d41b06e452 | checkpoint | 6
| e8563fe9-3fbd-5210-841b-411bcfb2df35 | textbox | Equipment Type:
| a2683913-abd9-5c90-9c8b-40899f0ea4c3 | textbox | Manufacturer:
| 8b366f34-db94-5c4d-a37b-98b8864a9024 | textbox | Model and Type:
| 556b2989-7730-5701-9d81-b0d8702a4a5b | textbox | Serial No.:
| 3bdbd6e4-a10e-5320-a32f-41e2025dab39 | textbox | Next Service Due:
| 928a8d37-d6be-57e8-9819-49b7c2a1d92d | checkpoint | 7
| d9b32f47-74f7-5c54-86e7-29b5eb68f311 | textbox | Equipment Type:
| c25f1b07-ccd9-545d-bcf1-70f7de3772ae | textbox | Manufacturer:
| 557ae0af-ae79-52fe-ac32-5ae783bfbd24 | textbox | Model and Type:
| da86f339-f33c-5594-ad94-a07efba683a0 | textbox | Serial No.:
| 34b3d541-2c85-5e93-8711-8208ef1ae94c | textbox | Next Service Due:
| b556b88f-cfc7-5c58-a0d3-21aa1fcf562f | checkpoint | 8
| 45af7411-27d7-5290-a4f3-e3c060b1732d | textbox | Equipment Type:
| 439911d9-6d5a-58b9-9d9a-e5fbb711d9e6 | textbox | Manufacturer:
| fbc2bbb8-1c08-5ed5-b94a-64d9a782f33c | textbox | Model and Type:
| ac8e6743-b058-5e6f-bfa5-336be58119a7 | textbox | Serial No.:
| 50731a42-0a37-550f-aacf-70906c6fcaa9 | textbox | Next Service Due:
| f81a9cad-2202-53fc-aea8-cbaacb40a1ec | checkpoint | 9
| 1663dd13-3559-5831-919c-49102d9fec96 | textbox | Equipment Type:
| c8f55def-8873-5711-ad58-9ea5462b3445 | textbox | Manufacturer:
| fac8902a-ff44-5501-b258-36913a18b048 | textbox | Model and Type:
| 9e3de27c-9b55-5e59-bc48-2a233c014957 | textbox | Serial No.:
| 38356761-d8a1-5f92-89db-89d0b9e489a8 | textbox | Next Service Due:
| e48a2151-c0b0-593e-afe7-b90d947c1f50 | checkpoint | 10
| f44f60a4-ad2e-59a7-83c3-f267d022f77d | textbox | Equipment Type:
| f1ff474c-26e8-5ddf-909d-0cdb53b8d9dd | textbox | Manufacturer:
| a001f1d9-90a7-5634-9641-fc9b22fc172d | textbox | Model and Type:
| ca7d7f0c-915c-5e5b-9c73-6e0c60b161d6 | textbox | Serial No.:
| caafb20b-52c7-5415-9dbe-4f70c7fc52a1 | textbox | Next Service Due:
| ad3fbce0-17fd-5817-95d9-add8fb8cfa29 | checklist | QA 15 - Pre Cast Slab Penetration Placement Checklist |  | Pre Cast Slab Penetration Placement Checklist
| 101d06ae-d5c3-5102-8e0a-bd03eaa103d8 | checkpoint | Pre Cast Slab Penetration Placement Details:
| 9b9fa587-4e52-5a3c-bf64-8fe3a0d41b4d | textbox | Drawing No. / Rev:
| b8e010e0-dc0c-5df3-a127-57413e1145e6 | textbox | Slab No.
| 37c620e4-e830-5c4e-b88a-367415b6e782 | textbox | Total: Sewer - waste penetrations
| 06b28005-fff3-5a96-9121-15826feccbd2 | textbox | Total: Stormwater penetrations
| 674df700-7ea8-53a5-8bd3-84f9dcc0a78d | textbox | Total: Water
| 5db08c04-89ae-513a-881f-d66e8502d98b | textbox | Other:
| fc562caa-dfc7-5fe3-bf42-bc54f243942e | checkpoint | Geschke Representative Sign Off
| d6a1ecea-a6ea-58bd-b745-be9209c09624 | signoff | Request Sign Off
| dde82c3d-94f0-52ee-9d80-bcca23f40527 | checkpoint | Construction Company Representative Sign Off
| 574f3ebc-4cbd-5caa-b4cb-ecaf21b2fbe7 | signoff | Request Sign Off
| c6bf1c14-4c30-5052-9dc4-982eb73acfc1 | checklist | QA 16 - PE Electrofusion Welding - Field Operational Sheet |  | QA 16 - PE Electrofusion Welding - Field Operational Sheet
| 286304e4-d491-530e-a879-79048a305a1e | checkpoint | Operator Details
| d09890f7-646a-5143-b4f3-8969ff90db97 | textbox | Name
| 57467f91-fde3-52e0-b267-7ab820283d74 | textbox | ID No.
| ceea6ef6-6308-537d-9437-f8e63b6f21ac | textbox | Company
| 8daea862-b26a-564a-a7a8-38196260bc8f | textbox | Address
| 66b87a78-074a-570c-b59f-8aeb22d53d0b | checkpoint | Welding Machine Details
| 6d41d224-e2e5-546b-8b09-be07b8add981 | textbox | Manufacturer
| c6e1c48b-a115-580a-8f7c-18a9fbd4a3b4 | textbox | Type/Model
| a6161095-5a26-5337-9adb-93ec7a6c00bf | textbox | Serial Number
| f7e39ce5-586e-5ced-9b42-366b61773496 | textbox | Year Built
| 07064409-656f-5d8e-ba2c-57154117505c | checkpoint | Actual Pipe Size
| f984d670-cda8-5f18-bf60-2e0f2a47d258 | textbox | Type
| 494cb07f-d5a8-5039-a6fd-ded454b33aaf | textbox | Brand
| c426b190-d5fb-50b3-8329-bcc5dc0c6c93 | textbox | En
| a28c3702-0c63-5953-ba84-af92909d5e43 | textbox | OD
| 6aeaed54-c92c-599c-9731-2f4ac78f2885 | textbox | Ovality %
| e9e19a09-af9a-5dd9-add0-04e44c20d339 | checkpoint | Fitting Data
| 31760176-42f8-5b20-b8d5-f13e4fe89024 | textbox | Brand
| 183249e9-b8ac-5e48-b375-03c842a1ffce | textbox | Type (Coupling, Tee, Reducer etc.)
| a1ea026f-d998-57bc-8662-5ada0860350c | checkpoint | Unit Setting
| 333602de-d20b-5569-8fe7-680b88bca173 | textbox | Manual
| 8a211235-6a36-557d-ba86-0d8a0adc44bd | textbox | Automatic
| ee9dc83b-144a-596a-9418-efc47324c835 | checkpoint | Preparation
| 8d969b29-d822-5ebc-947a-f3de632ff619 | textbox | Cleaned and Peeled
| 482fee68-93a2-5ef0-8a4c-9456b9d680a3 | textbox | Pipe/Fitting Clamped
| d851523d-87b5-5bee-ad87-5b7e17d639fd | checkpoint | Welding Times
| 0577cc8d-f3e3-52e5-ac80-91e18b37b737 | textbox | Joining Seconds
| 826b512c-5d90-56c1-a74b-8e4e5876e703 | textbox | Cooling Minutes
| b99ca8e0-f16a-50d3-8db6-7aba95e6486a | checkpoint | Conditions
| 32a3c930-dbd3-59a5-a937-863e388c83d9 | textbox | Ambient Temp
| 0bcf9c4f-5183-5a0a-a5b5-f3a6c2ace2ef | textbox | Weather
| 81ba753f-caa6-55ba-ab86-854ee1f6d67d | textbox | Preventive Measures
| a4055e15-3d26-5e25-84be-c62c1b1d24b9 | checkpoint | Power
| af7e98e3-5e08-5b7c-a821-fcde34042cd0 | textbox | Mains
| 7dda302b-01bc-53f8-a5ab-dbc76f069c6f | textbox | Gen Set
| f39d7021-bda5-5819-9f3a-a3f34b9c769a | checkpoint | Operator Sign Off
| 7f452676-6d64-5449-800f-e282a376cb40 | checklist | QA 17 - Water Meter Accuracy Test |  | Water Meter Accuracy Test
| 47148228-30da-5bbc-8da8-3cc2b8857bca | checkpoint | Water Meter Accuracy Test Details:
| 3314fb28-6004-50b1-9780-eefb1b71510e | textbox | Date:
| 430b7245-e716-513b-9047-9c4e4fc6ca44 | textbox | Project:
| 208dde16-7f35-52ce-b4aa-bf9e249d1072 | textbox | Location of Water Meter:
| 72a0013a-b8c3-5856-a4c3-a54ed8e566ff | textbox | ID Number of Water Meter:
| 06f570b6-b549-598c-991a-21c07d01fa4b | textbox | Model & Manufacturer:
| fdbfa2df-492b-534b-b8f1-f7cc5a3e7405 | textbox | Current Counter Reading:
| e89edae7-6e74-57cf-b7c7-7e878428911c | textbox | Zone/Appliances to be Metered:
| 3e193013-f935-59a7-852f-40ae23dec67e | textbox | Pulse Rate:
| 857503a4-a5b8-5ea0-b22e-6414f76d17d2 | checkpoint | Measurement Apparatus
| 1e41da32-9761-534a-960e-e0f9e7e6b264 | tickbox | Bucket
| 360faded-a3ea-5cfa-a0fb-f1b75e6c2aa8 | textbox | Bucket Size
| ea7ae63a-b9ad-5afa-9fe1-43aed4f6003e | tickbox | Water Meter
| 0e4bdf03-1f7b-5f0b-aab1-898e3d630651 | textbox | Calibrated Date:
| 649b76ce-264e-5376-aecb-d46f59de9eda | textbox | Other
| 0faa6954-3d69-5f2e-8d5b-27a52358f137 | checkpoint | Measurement Method
| 3622e18a-b1b3-56de-bf4f-0028521a67c5 | note | Isolate all fixings
| 03c1d46e-10a6-5a14-9b1c-a3947a0e30c9 | note | Place bucket at outlet of fixture and fill
| ccb3121d-2dfa-5a79-a724-46ce9a34d3c4 | note | Fill in completed counter reading and minus "current reading" to measure accuracy
| 32d2480b-6c21-5252-87db-7f5c7291ba03 | textbox | Completed Counter Reading:
| d7938c77-17a2-5fd2-95b5-d442fcd94056 | note | Accuracy
| a90c66bb-a98c-5fb1-9288-5e92871b9098 | textbox | OK
| 39d33286-e360-576e-ba75-e0e81e5c5b15 | textbox | FAILED
| aec8060c-cb17-5fa6-98d5-69f07b2c8640 | note | Replace Counter and Re-Test
| c14044e9-0ffe-5ba8-910d-9271ac1424a1 | textbox | OK
| b6b31f97-d145-51b1-9ab0-d60631df6e69 | textbox | FAILED
| 10225846-1170-53ff-a50b-c95c6d7745f7 | checkpoint | Pulse Check
| c96818d2-e638-55e9-a052-1c9937861a16 | note | Method:
| 6e3c2261-ce63-506b-9a84-1f03bdcf0a8d | note | Connect multimeter to the 2x wire connection points on pulse kit and set multimeter OHMS
| c0ffe883-62e1-5c4c-bcae-49e31526dd70 | note | Turn a fixture on and wait for pulse reading on multimeter, then stop flow immediately
| f4399fce-a9c1-5503-935a-aa5d1cbb5d4b | note | Measure bucket contents:
| 502a4ba5-22e3-53f4-8c1d-97cebc66e345 | textbox | Pulse Registered:
| 9f07c428-edf3-5779-8f6e-58de75fc7371 | note | No Pulse - Install new pulse kit and repeat process
| 5b8950c5-0956-5cc9-a698-3fa49180f8ad | note | If Pulse registered OK
| 6c34fdbd-6bdd-5043-82cf-369de26354df | textbox | Pulse Accuracy:
| 2dc63887-83ae-51bf-84c1-da817edca9d2 | note | (Bucket contents match spec at top of page)
| 46079bb5-7f41-53aa-930b-73bf874e3ebd | note | Failed - Install new pulse kit and repeat process
| 3ceadcd6-d779-5c97-8426-53dd865a89c4 | checkpoint | Sign Off
| ad50d9d8-26e8-56f3-bdd2-19531046f2ec | textbox | Name - Geschke Representative
| 485867d5-005d-5646-ab1b-3a930afb474a | signoff | Signature - Geschke Representative
| 8fd88cab-c71f-5671-a6fa-93ccde270927 | checklist | QA 18 - Gasket Installation |  | QA 18 - Gasket Installation
| f0716ed7-860c-5feb-8dcd-a0c4acf3dfb3 | checkpoint | Gasket Installtion:
| 7be172d1-9829-5a2c-b7f8-00457cfb7cc9 | textbox | Location/Identification:
| f876129f-5eb4-51c8-bb9e-756b83edf312 | textbox | Nominal Bolt Size:
| 9907296c-8706-5b66-9807-55d455c2d7c7 | textbox | Gasket Contact Surface Finish on Flange:
| ea836f76-c300-5007-be0a-6a052b6b7f4f | textbox | Lubricant used:
| 8b341548-e87e-54cd-8475-7e96e7853e4f | note | 1. Galvanised nuts and bolts must use good quality lubricating oil on threads
| c956b192-1fea-588d-bb53-83472d861f51 | note | 2. Below Ground Galvanised nuts and bolts must denzo and plastic wrap full flange and cover bolts
| d5e0165e-cff4-5c8d-bfea-b4a82bd73d4b | note | 3. Stainless steel nuts and bolts must use anti seize / molybond on threads must return 24 hrs later to tighten in sequence and required torque
| d192a8f9-d6f4-58b4-ab1b-8a843ec0f0a5 | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
| 23edc375-619c-5ac0-9792-9449541ee315 | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
| 00b820d6-cc4c-53b3-8f3c-6c72d3b45a68 | note | 6. Zinc bolts, nuts and washers rust when used externally use galvanised
| e379697a-b2c5-5a64-9c25-eafc72ed07b3 | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
| 250b076c-dfae-5db8-a35b-7bba0249a23b | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
| c2d2b3b6-4fa3-506d-83ec-9ec2ec54dbfb | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
| 2bee71dd-e32e-59b1-9420-46b083121224 | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
| d4bf153a-9d1d-5fd0-8512-ebf65e461e96 | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier seek from GPL foreman
| 70414949-d3d3-5c11-a9c3-86105b9cd86d | checkpoint | Check gap for uniformity.
| c40c9bc9-4ac3-5841-ade3-ca4e8b683c56 | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a Round)
| 30d03fea-c825-59b3-9194-9eead2853f3c | checkpoint | Final Torque
| 8c38a178-2bad-569d-8c91-4bb0a1397452 | textbox | Final torque*: |  |  | (Nm)
| 74fb850e-4f2b-5f8a-8595-cf364cd6d87e | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
| 85b780c7-a5d6-502f-aa26-1029459226ac | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
| 9899d5d1-ecd4-5263-ab82-abcf9d1a1481 | textbox | Round 1 Tighten to: |  |  | (Nm)
| b02ee652-b36d-5629-a550-0cfbcf597499 | textbox | Round 2 Tighten to: |  |  | (Nm)
| 2e643e63-79ef-53a3-a263-9351b8b02708 | textbox | Round 3 Tighten to: |  |  | (Nm)
| 6b8d6f2f-5526-5691-95cd-134f8af00f7d | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
| 0bf7c0ca-43f7-56c8-ba42-85e8487fcc21 | note | Final Rotational Round 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
| 6bf8c817-4eba-5a8c-9e3c-974f59942045 | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
| cd968700-19be-54d6-8335-26348bb19bf3 | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
| 0590663a-5191-5add-8e4a-e6747fedf410 | textbox | Other:
| e1bb53b7-18a6-56df-beee-b9bc27ecd4d0 | textbox | Where was torque information provided from:
| a4b9afd0-2ce7-5108-b8eb-79ec7c44d92b | textbox | Joint Assembler Name:
| 45e3ad94-490c-51e3-9a05-c2d308653923 | signoff | Joint Assembler Signature
| fc7dcc9b-15c4-5725-adb8-dc40bd143576 | checklist | QA 19 - Service Cross Connection Check List Report |  | Service Cross Connection Check List Report
| 3d996e18-93fa-51d2-b7bc-3f8b0f3733fc | checkpoint | Service Cross Connection Check List Report Details:
| 384806cb-258e-5258-90d3-e1a938c4939b | textbox | Zone/Grid:
| fbd6a78a-4611-54c3-bb01-878d324421e9 | textbox | Drawing No.:
| f10de94c-e511-511d-b795-ae0056e636f8 | textbox | Rev:
| d907f4be-f675-579a-b8e0-e3b1dd9dab2b | checkpoint | Service to be tested
| b476d468-5583-54f0-a53c-9117067e9335 | note | Isolation of potable supply in general.
| c9007909-0497-5e5b-ad9d-feb280c5bada | checkpoint | Potable Water Supply
| 0fac9376-7e12-5259-aa89-9e5856bb2448 | note | Confirmation of service isolation at all fixtures.
| 27e9f0f1-91a4-5a80-bc20-3b8b7a232445 | note | Keep potable water turned off.
| 281030ec-7b26-5b5a-924c-7bb2725f2c9f | checkpoint | Non Potable Supply
| 5bf38340-bd7e-5665-afc8-d3f0a7362a3b | note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
| c19ad19a-301c-5c27-b19f-d2ece5a07a0a | checkpoint | Turn potable back on
| f0587b91-5d9a-5d4e-ab05-64d20e6df0d8 | note | Potable back on
| bf7308ee-97d2-5181-8206-a81d9cf423d9 | checkpoint | Non potable supply
| 4d783ca5-0eed-5b3c-be44-c51958ad7ef5 | note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
| 746aedca-403d-5ab9-b14b-281c871711e8 | checkpoint | Potable Supply
| 9d0666be-dbab-57ad-abaf-c142eaff17d6 | note | Check all fixtures that receive potable water are still getting potable water.
| 513dc09a-9e0d-5a59-bf6d-3513e98158c3 | checkpoint | Pipe Identification
| 034987f6-3f7f-597c-a330-66077eb2e9bf | note | Confirm recycled water piping is identified by colour and labelling.
| 12c36d30-1d36-54aa-9a51-c192e19f7df5 | checkpoint | Other
| eeec6df6-5156-55e8-924d-d643d380863b | checklist | QA 20 - Fire Hose Reel (FHR) Test Report |  | Fire Hose Reel (FHR) Test Report
| d6f0cce8-3532-5127-a479-3c393bc4c7b6 | checkpoint | Fire Hose Reel (FHR) Test Report:
| 8d58cc5e-d3fc-5537-a781-b5571a20430c | textbox | Location of FHR:
| 1ed8786e-2a65-5227-a0be-d91bf822c43e | textbox | ID Number of FHR (If applicable):
| 9f7035bf-b64c-5d42-b295-a7ac668fd4db | textbox | Manufacturer:
| 0f33f513-1bcf-5cfc-a274-acdca3b342ef | textbox | Model:
| aa16ce4a-c82e-5227-8bbb-a2985e1297c1 | textbox | Size:
| 1a8545b3-89ec-56ab-84d3-7b3191023639 | note | Aust. Standard Flow Rate: 0.33 LPS @ 210-230 KPA
| 0c74b826-3bf4-556d-8b06-9b7497fab69c | button | Measurement Apparatus: | Bucket
| 3a041336-bda3-5a41-a1c7-b87f9eee1496 | textbox | Bucket Size:
| a414a564-d770-59eb-92ab-534b8553fbfa | note | Measurement Method:
| dfdbc226-bd3b-5722-b029-8a8e02c33951 | note | 1. Connect pressure gauge and outlet to end of hose
| 37c1a67b-ee94-5d73-86ee-7eb7e52b36b7 | note | 2. Note static pressure reading on gauge
| c27e9cc1-0383-59f2-b68d-2637e16c5371 | note | 3. Place bucket at outlet of FHR and fill
| 7707dedd-4728-5e5e-b9d5-6f0704d109cd | checkpoint | Reading
| 5576b839-cdde-581c-b9c7-874b85616b36 | note | 3.3L
| 52b49b62-24c4-506e-bcaf-94d4e091021e | textbox | TIME (sec)
| 566d8f60-7640-5204-a2fd-dad1340c35f5 | textbox | Flow Pressure:
| 83243216-be39-528e-acbc-a0ff44e932fe | note | 6.6L
| 64d238f7-5ac7-56b5-9813-338a67069a5e | textbox | TIME (sec)
| 8d3e2d70-5300-5dd7-9f87-c49a717e8f62 | textbox | Flow Pressure:
| cbee89ff-3b69-5b0f-9e2e-b6c1c039de16 | note | 9.9L
| cc5dd111-4c12-50ac-9a41-c9fc10f0d8a5 | textbox | TIME (sec)
| 18bf24da-ab70-51bb-9f2d-7f2272dced90 | textbox | Flow Pressure:
| d80d130d-72f8-5fc9-872b-1fc379f43b15 | checkpoint | Completion
| e8273121-15be-50a1-9f1e-fcc4a4623e61 | textbox | Geschke Pty Ltd. Representative:
| bce6d576-8284-5765-ac7b-64e9f2f68f43 | textbox | Others Present:
| d7b6d998-6693-5342-a037-c4ee2105006c | textbox | Date of Completion of Satisfactory Test:
| b673e5b4-e632-56e0-a40e-f25605af8f04 | checklist | QA 22 - Hot Water Service Maintenance Log |  | Hot Water Service Maintenance Log
| c5e691b7-9a0c-576c-90ee-c7233b18c6e9 | checkpoint | Hot Water Service Unit Details
| 63d73ac6-aea3-5c36-8015-cb51cb592f4a | textbox | Purchased from:
| c701aab0-23fa-54db-8eb4-36a9d8191aab | textbox | Make:
| b8d6242f-6aaa-5426-adc4-bb6721d87868 | textbox | Model No.:
| 9d816d75-87e3-529c-8f2f-94cb5d73f2ab | textbox | Location:
| a4961ada-714a-51b1-afb7-4931cf068cc7 | textbox | Room Designation:
| 322a2297-029b-5812-beb5-79e883c67499 | textbox | Installed by:
| 829ba56b-89f7-5ca2-9552-932647263471 | textbox | Installation Date:
| d30e5faf-4346-5783-b265-0d75243792de | textbox | Number of units in series:
| f3cf3ba4-f0d0-5804-8929-8fce3cd39c06 | textbox | Prescribed temperature set on unit or combined package:
| 22e49bd6-3bda-5925-8ddf-d5c03c2c930e | checkpoint | Does installation comply with manufacturers instructions
| 80ae1e00-4559-5bbe-ac85-8cec3c7d7f8b | checkpoint | Does installation comply with current requirements of the local water supply authority
| a796eb1c-193c-55ee-a848-36fa2706bfb6 | checkpoint | Clean Pump Strainers
| d417249d-461e-5f16-a434-06c2d2193080 | checkpoint | Clean Hot Water inlet Strainer
| 699338bb-deb9-527d-993f-ea45cfcfa842 | checkpoint | Clean Hot Water Return Strainer
| 8a550b57-6e16-5878-90e3-46261f47f7f8 | checkpoint | Confirm all Valve Isolation reinstatement
| d94e369b-35ba-58aa-b2ad-907f3999c239 | checkpoint | Confirm Unit is Operational
| cb76d582-4954-5a36-9f28-07baa4a3930f | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
| df7d45dc-5841-5b3a-8ace-d32f2292d029 | checkpoint | Commissioned By:
| 031d4ebf-deb6-5725-aa7f-0f8d56950e2c | textbox | Name:
| 4569b960-cfdc-594d-9c6d-c0925dd0a8ee | textbox | Date:
| 92a18618-2d1c-50c3-8cc6-d34b4708b9bc | checklist | QA 23 - Boiling Water Service Maintenance Log |  | Boiling Water Service Maintenance Log
| 066a1a64-8669-5c77-b201-0f5a52cf233c | checkpoint | Boiling Water Unit Service Details
| b3f30653-6178-506e-9db0-c86ab4fc3fdf | textbox | Purchased from:
| ff0705b5-a1b1-510a-aa7a-e461a5a774d1 | textbox | Make:
| a78e77ea-e373-5e4a-88a8-8b1fb7066083 | textbox | Model No.:
| a1d24a33-e216-591c-895c-0b159085ad87 | textbox | Location:
| e2697e52-d71d-5775-9301-bf7b11547968 | textbox | Room Designation:
| 28d78b65-0d62-57b6-85c2-041a9d570d33 | textbox | Installed by:
| 880f6bd0-870b-561a-90f2-36aa95480e0c | textbox | Installation Date:
| 22e49bd6-3bda-5925-8ddf-d5c03c2c930e | checkpoint | Does installation comply with manufacturers instructions
| 91cfe6cf-64a6-57a8-958d-53db8414eda8 | checkpoint | Does the installation appear in good working order.
| e1127485-8530-5064-a3cf-362fd95de1e7 | checkpoint | Confirm all warning lights working correctly
| b60eff23-0fa7-54bb-b27a-0810042ad144 | checkpoint | Confirm filter is clean
| 158f5d55-a21e-5343-b3f5-fdbbe93f63ec | checkpoint | Confirm Unit is Fully Operational
| df7d45dc-5841-5b3a-8ace-d32f2292d029 | checkpoint | Commissioned By:
| 679e3648-4bab-5088-ba86-3d3b6327e1e1 | textbox | Name:
| f59ebde1-31f2-5a17-8679-ed7817fee637 | textbox | Date:
| 850a5305-5545-5058-bcd1-f9e1ccf2c06b | checklist | QA 24 - Hose Reel Register |  | QA 24 - Hose Reel Register
| 79d9612c-e0c0-5948-81c4-eadfc20501de | checkpoint | Hose Reel Register
| 04c69248-4f50-5d0e-bab9-f0c2c3a543cb | textbox | Ref No:
| e9a1de0e-57af-58b3-b95b-8ce72f49b3f2 | textbox | Building:
| 24a73e08-b0f3-501e-8bec-420ec5722d97 | textbox | Zone:
| b82a8918-c844-5ed7-895f-5dbe58433300 | textbox | Level:
| 3da07763-abf9-5a11-9683-7b4c2c647592 | textbox | Adjacent to:
| 605ce2d6-c6db-5f48-8420-bc4cfe710ae2 | textbox | Length:
| 0a92798c-9f03-58b9-9264-efe250f07a53 | textbox | Date Tested:
| 48d16d02-b36f-552b-a1af-c7c8f1b9b4a9 | textbox | Flow Rate:
| 737b6415-ead1-58e1-be99-6ce6adfea0f7 | button | Obstructed Access | No,Yes
| 1cc787a0-fbd1-5ee4-9bd3-1786008c4718 | button | Operating instruction visible and legible | No,Yes
| 34efa827-de53-5270-a719-eb8ac7dac657 | button | No leaks throughout hose reel mechanism | No,Yes
| 53417496-304d-52de-9d4d-52b0e3faff0b | button | Hose runs freely through guides | No,Yes
| 4370dc55-52ed-5d36-9e8b-0e98609ab247 | button | No signs of corrosion | No,Yes
| 5d1de247-77d1-5c18-bb12-9c0a485ca934 | checkpoint | Result (Pass / Fail)
| a475ee04-c328-5bbb-86fe-2857c2ae1a5f | checklist | QA 25 - Butt Welding Checklist |  | Butt Welding
| ca4b4cd1-2358-5bf8-8194-06eb8adc280a | checkpoint | Operator Details:
| 46a54668-3daf-53a8-a151-e3d03f8911d6 | textbox | Name:
| 2b5d83a8-6916-5a15-864b-db62bbedc271 | textbox | Company:
| 1abfa6f6-57ff-5614-beb0-a6f453afd4c6 | textbox | Phone:
| 26da7c29-9908-5879-bd26-06afd54259f0 | textbox | Address:
| c83758de-5f0c-547c-bfb1-8463595c99b7 | checkpoint | Welding Machine Details:
| 66ac11be-3c54-5c04-912d-d506cb74a987 | textbox | Manufacturer:
| 9585ac34-0396-5687-a910-6afd1430ff0e | textbox | Type/Model:
| 3717006a-52a1-5b9e-904b-55cf39bac98e | textbox | Serial Number:
| d04d0eee-d87f-5773-9654-72e022766536 | textbox | Year Built:
| a061f28f-55c2-5cab-b2ce-7ff80d0845d0 | checkpoint | Pipe / Material Details:
| 56aa49ac-cf77-536c-b917-c3273ed34133 | textbox | Dn (OD)
| 3473aa61-a0bd-5ae2-9abe-619e51c1b165 | textbox | SDR
| fdf5fe47-d6a7-55fd-b61b-4b7d9f3f9015 | textbox | En
| 8fb7d4e4-466c-5ec5-a881-10d733926107 | textbox | Type
| a36004fa-1394-5ba6-a3f0-d4855d41565b | textbox | Parameter
| 27378260-60c9-5c5b-b8a4-a6addaa79470 | textbox | SLP
| 9ab68ca3-d26d-5bde-9e60-93d9896bca6f | textbox | SHP
| a0b01591-964f-5515-85c6-7f96b57877d7 | checkpoint | 1
| 0db8d60d-7522-5294-8183-cdfea08ef810 | textbox | Time
| f5a8f40e-b467-5125-a090-edf393b5d733 | textbox | Ambient °C
| 1440467f-5fde-5121-9ea8-a6e5a2800a42 | textbox | Heater Plate °C
| 00dd074b-a686-53b6-8cec-6096504ae3e9 | textbox | Drag Pressure
| 2400e408-8c18-5c31-8fd7-e44f93c2ef81 | textbox | Bead Up: P1 (Kpa/Bar)
| a9fd3c12-5904-59ac-9b3d-fc9f2c4df8c6 | textbox | Bead Up: t1 (Evidence)
| 4c773931-c621-5bb5-b506-872ee39facdd | textbox | Heat Soak: P2 (Kpa/Bar)
| 099e0b88-7dc5-5ccd-8022-ce71aa78bccb | textbox | Heat Soak: t2 (Seconds)
| 4365a50d-2804-556c-83a8-f4d469b5e628 | textbox | Change Over: t3 (Seconds)
| f77ed4e8-f999-54f6-a7e0-cbe0c172e5a8 | textbox | Pressure Up: t4* (Seconds)
| c4894126-b54c-5136-9637-7fd9b4b213c5 | note | *t4 not applicable for SHP situations
| 4a131c2e-c3d9-5b81-a50f-6a4af866e043 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 46cddc23-a2e1-5dea-b4e9-ca6bb1e5d16d | textbox | Weld and Cool: t5 (h:m)
| e6defa1e-93e0-59df-9fa3-e2a42ab8ed28 | textbox | Rough Handling: t6 (h:m)
| c30bd40f-f2cb-59a8-9753-f37f19ab31e5 | textbox | Bead Size: Min
| d78eb3b5-1cb3-57a1-a6ef-5964108cdcfa | textbox | Bead Size: Max
| 7e4c5935-5272-5a3e-85b5-3bf99c45bc10 | textbox | Comments
| 61a51d36-aa2c-5cde-817d-4ca50cdfc4ab | signoff | Add Operator Signature
| 80eb3b16-184b-5f92-932d-71403b994572 | checkpoint | 2
| 7858abc5-428a-54ed-8fef-c37697469294 | textbox | Time
| 1cfa4730-2456-52a4-9929-12d7417a31cb | textbox | Ambient °C
| 3c9c2a26-c894-52df-8a0a-f068a48df402 | textbox | Heater Plate °C
| 84339dc2-878f-5dfe-92de-21e71a1e4759 | textbox | Drag Pressure
| 7c2e3e5f-bfa4-5f80-b156-db516e6803f3 | textbox | Bead Up: P1 (Kpa/Bar)
| 56b89cfa-138d-53dd-b4d7-cf0582bd5081 | textbox | Bead Up: t1 (Evidence)
| 4cd79080-ad88-5291-a420-864d9ecf123f | textbox | Heat Soak: P2 (Kpa/Bar)
| 5e06c1f4-5fb1-5372-9436-1256a3452506 | textbox | Heat Soak: t2 (Seconds)
| 5bb56bcf-9bf0-5f44-bac0-543c14cb09e0 | textbox | Change Over: t3 (Seconds)
| d365fd07-deac-5fa5-b778-cf586149acef | textbox | Pressure Up: t4* (Seconds)
| 6625be94-0187-52f7-9f4d-6b0881825de1 | note | *t4 not applicable for SHP situations
| ef636e50-3085-5671-9d2c-995d1539c53e | textbox | Weld and Cool: P3 (Kpa/Bar)
| 9771b85a-af6c-5693-960b-d1662063818f | textbox | Weld and Cool: t5 (h:m)
| 97a80bdc-cf6c-5e66-b367-ccbad6ab6b3f | textbox | Rough Handling: t6 (h:m)
| a0ca4822-cfa0-5a85-9305-d2323108f15a | textbox | Bead Size: Min
| f2f58170-c484-57e4-a1bd-b6606185c49e | textbox | Bead Size: Max
| 8c762868-6b9b-500c-bd41-454e79b789c3 | textbox | Comments
| 6c544df2-1bf7-598f-b986-996e61a18da3 | signoff | Add Operator Signature
| 7a173f6c-500c-553d-b74a-85afb565eb50 | checkpoint | 3
| 37c593c4-fe01-5350-bb10-d64a0893c68f | textbox | Time
| ef19d41f-da99-57bb-8f40-3c067a66de5a | textbox | Ambient °C
| 6276b928-ddcc-5bff-b3a5-13d24fac9aa9 | textbox | Heater Plate °C
| 20841de0-1811-54fb-af1f-fba13a0ac8d4 | textbox | Drag Pressure
| c1be99a8-d192-5c6b-b7cf-40c7fb0688c3 | textbox | Bead Up: P1 (Kpa/Bar)
| 7b6c08a6-2e8e-5d9e-9546-94190f68b8aa | textbox | Bead Up: t1 (Evidence)
| d17558db-4cc7-5545-bf8b-1aa2e2f54ddc | textbox | Heat Soak: P2 (Kpa/Bar)
| f56b19b7-7670-59a6-a0f0-47ecadd9008d | textbox | Heat Soak: t2 (Seconds)
| 55574ce8-c096-5dfb-9bc6-055804e07282 | textbox | Change Over: t3 (Seconds)
| f91cc93c-7588-5634-ad13-b2e294327807 | textbox | Pressure Up: t4* (Seconds)
| d6c29471-709d-573e-9533-f3c4664ef232 | note | *t4 not applicable for SHP situations
| e25a490d-2e19-5b38-bae2-bbac03dad96f | textbox | Weld and Cool: P3 (Kpa/Bar)
| 99635b19-e826-5e89-9411-e27801a4a38e | textbox | Weld and Cool: t5 (h:m)
| 4d8f28ab-e025-5d13-b1ca-e82586be5a2e | textbox | Rough Handling: t6 (h:m)
| d7b56e20-1e16-5422-a8f2-cc915f232800 | textbox | Bead Size: Min
| 4dd96d85-f6cd-5391-8bfc-ab03c721e08a | textbox | Bead Size: Max
| ce572f4b-3a9a-52f8-9204-0796e056b4c0 | textbox | Comments
| 47ba15b3-e1d2-5188-8d03-4a2b6e7a828f | signoff | Add Operator Signature
| b911b1b9-6725-5360-8e28-f6a01e7ce249 | checkpoint | 4
| 51daddf4-f5ae-5f4e-9634-ee241615fd92 | textbox | Time
| c4a74ddc-4dce-5ace-a620-e104b196d494 | textbox | Ambient °C
| 6c9b499b-cff3-5937-b360-ce6decc063ee | textbox | Heater Plate °C
| 49ba7e6f-08cf-57d9-ade3-168db33509ea | textbox | Drag Pressure
| 4f4f6de0-69db-5755-ae12-cea2cbd7df0d | textbox | Bead Up: P1 (Kpa/Bar)
| a7532573-46f7-5e0f-8463-da4ff38946c9 | textbox | Bead Up: t1 (Evidence)
| 0123f480-9e99-5c8f-9531-bc8fbe1d24b0 | textbox | Heat Soak: P2 (Kpa/Bar)
| 3dd77afe-a845-5e29-b997-ab2eaddd96b1 | textbox | Heat Soak: t2 (Seconds)
| 2c300354-a2c4-558e-b6dc-de91a259d66f | textbox | Change Over: t3 (Seconds)
| a1b5b247-199e-5cff-954b-e5d3f1fd4cb0 | textbox | Pressure Up: t4* (Seconds)
| 70286c1b-6c09-5500-9d52-93e488c4a136 | note | *t4 not applicable for SHP situations
| 3ac31eb6-dad3-5fe3-9c4c-1d08d2845f0f | textbox | Weld and Cool: P3 (Kpa/Bar)
| 8ba47d42-db0e-52c2-8127-a6589ae88a10 | textbox | Weld and Cool: t5 (h:m)
| 9b364ae5-7fda-5f80-b19a-d734900c5d90 | textbox | Rough Handling: t6 (h:m)
| 7404fa90-02c6-51b5-bb2e-7becf2a552b2 | textbox | Bead Size: Min
| 00609065-4f58-5d9f-856e-211c2e3e7597 | textbox | Bead Size: Max
| 540fb917-4ed2-58f1-801f-3483011fef4d | textbox | Comments
| 3edcb550-ab62-5c27-8568-2953aec00e0f | signoff | Add Operator Signature
| 24dce8d0-3e3b-5c3c-b560-2a93082053b4 | checkpoint | 5
| 13239f5f-1f8a-5019-b566-9e319c80acd9 | textbox | Time
| 5b118ae6-4ba9-5bad-8975-91ae7311b7b9 | textbox | Ambient °C
| 879505e6-6aa5-5bf0-8162-5ec7f85a085f | textbox | Heater Plate °C
| 1041f8c1-e35e-58bd-b9e1-fa037cd4b21c | textbox | Drag Pressure
| b4570a54-9b5e-50d1-a7ac-dbfff9480f0f | textbox | Bead Up: P1 (Kpa/Bar)
| a79dcfae-0969-5a9d-89c5-ad4ad3082e0f | textbox | Bead Up: t1 (Evidence)
| 6748028d-2b9b-5290-8c21-98e9f8dfac93 | textbox | Heat Soak: P2 (Kpa/Bar)
| 1a2bef15-4acc-53cf-bb48-95e2f565c83c | textbox | Heat Soak: t2 (Seconds)
| d6ec3494-e711-5413-8f7f-2d91f7320dc9 | textbox | Change Over: t3 (Seconds)
| 2e717ebc-4a9b-595c-8816-1af63b4a9e58 | textbox | Pressure Up: t4* (Seconds)
| 57db01d7-e6c2-5e37-a3cd-74bf3c938b9e | note | *t4 not applicable for SHP situations
| 99c43286-1200-5dd7-bc4b-b0ec941959a9 | textbox | Weld and Cool: P3 (Kpa/Bar)
| ba5d1f54-3d21-5656-85d5-60c8df82a31a | textbox | Weld and Cool: t5 (h:m)
| a646bad0-5ab4-5664-a5c3-7e59553a3e80 | textbox | Rough Handling: t6 (h:m)
| e7ac60f7-3ab0-5562-bd49-1ee193c5719b | textbox | Bead Size: Min
| 86f7e9b4-141c-54c9-a855-4aaa2c7b027f | textbox | Bead Size: Max
| 44306b91-0190-5627-8049-51e163f997dd | textbox | Comments
| 21c2e6a7-eaac-5418-9948-945da90380f2 | signoff | Add Operator Signature
| e4ee39db-2ed2-56d4-9d1e-70d41b06e452 | checkpoint | 6
| c9f3a0fe-2fab-5a91-89b1-9764a223b93f | textbox | Time
| 41c4a495-7520-57b9-bce3-7878bae669ef | textbox | Ambient °C
| c808acf5-2f07-502e-9688-2f24492af699 | textbox | Heater Plate °C
| 30d8d23c-105a-52c2-a741-bd834b3f37dd | textbox | Drag Pressure
| a8a93726-6d74-5c1d-8648-db8e18b1b003 | textbox | Bead Up: P1 (Kpa/Bar)
| 530a314d-5ab2-5605-80a7-aa264c1b45ef | textbox | Bead Up: t1 (Evidence)
| 941274f2-a3f7-5f34-99bc-5e04bab74876 | textbox | Heat Soak: P2 (Kpa/Bar)
| 82385811-9bab-5c69-b475-b583f7583ae0 | textbox | Heat Soak: t2 (Seconds)
| dcb2556a-fa5a-51ba-b67a-19bcf4c3428b | textbox | Change Over: t3 (Seconds)
| 3f1a67ea-768c-5f79-9fdc-662c76dbf4b4 | textbox | Pressure Up: t4* (Seconds)
| dc700e13-9645-50bf-a154-c34f8c0b288e | note | *t4 not applicable for SHP situations
| 096898ab-46e8-56b9-8bdc-e55533668d76 | textbox | Weld and Cool: P3 (Kpa/Bar)
| b8bcef6c-5667-5690-b507-c03dee966d50 | textbox | Weld and Cool: t5 (h:m)
| dcc821c0-9918-5f5a-867f-0aab3b249829 | textbox | Rough Handling: t6 (h:m)
| 73aacf78-7d9b-544a-b824-435aab9e1b64 | textbox | Bead Size: Min
| 1c2dd7d6-2b2a-5e42-9c37-6910e41eb33f | textbox | Bead Size: Max
| d09127a9-51a0-556a-845e-512a56f4f8e7 | textbox | Comments
| 80690888-5962-5968-addb-c40a8fbb8f0a | signoff | Add Operator Signature
| 928a8d37-d6be-57e8-9819-49b7c2a1d92d | checkpoint | 7
| 0c10e1be-c838-5343-98b6-642a7e8903a0 | textbox | Time
| e52142b7-2655-54c8-92ce-c5658f09a5e9 | textbox | Ambient °C
| d2ecc2ee-cbbd-547b-bf15-7744dad17c30 | textbox | Heater Plate °C
| 2a6d8a9c-192a-5295-ba4f-3ee1805b3462 | textbox | Drag Pressure
| cee2da90-ab6d-5722-a379-f620e6e3e210 | textbox | Bead Up: P1 (Kpa/Bar)
| 0ffa0f68-f28d-59d5-bd59-7c06d3a79aa5 | textbox | Bead Up: t1 (Evidence)
| 2ad53234-469f-5ab3-97c2-f642a7f37820 | textbox | Heat Soak: P2 (Kpa/Bar)
| ccbecc9a-2c4b-5d30-8e26-31c041316285 | textbox | Heat Soak: t2 (Seconds)
| 58432c0d-3dba-520f-a019-38eb82315dbb | textbox | Change Over: t3 (Seconds)
| 466e8485-db20-5f7e-8532-bba280995899 | textbox | Pressure Up: t4* (Seconds)
| b7fab505-9b68-5b63-a8e1-1795df504af5 | note | *t4 not applicable for SHP situations
| 9f0933c1-1a99-51bf-9aee-dc8a8f9c3429 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 9b9dc124-4452-58cb-8e11-4e0d6d3ddb08 | textbox | Weld and Cool: t5 (h:m)
| cae2a92e-d62c-597b-960d-bbdd9d2448c1 | textbox | Rough Handling: t6 (h:m)
| df6274ad-0d65-5d2f-8ad0-5d8e51dfac89 | textbox | Bead Size: Min
| a761fec6-c829-5103-ae44-caca2694b87c | textbox | Bead Size: Max
| 1b2a5930-c652-5fdb-8078-744c32476a49 | textbox | Comments
| 9c34bdb1-0b35-569d-a4b1-cf94c5ef5c49 | signoff | Add Operator Signature
| b556b88f-cfc7-5c58-a0d3-21aa1fcf562f | checkpoint | 8
| 866722b3-aa94-5c05-b768-e3f3c2afd1a6 | textbox | Time
| 931196fb-778e-5314-8f70-97a6037357d8 | textbox | Ambient °C
| 121fa6b5-5566-5ba0-8f85-73da1c8dcae4 | textbox | Heater Plate °C
| 161b7d12-a950-5c51-8f61-471846a81f37 | textbox | Drag Pressure
| f4c8a800-30d2-5ff2-b156-555ff94bbc5e | textbox | Bead Up: P1 (Kpa/Bar)
| 9c00aa83-30d1-52d3-bc6f-fc66f10bf475 | textbox | Bead Up: t1 (Evidence)
| 5b72a478-b2f7-5141-88ad-3a0cc23532ce | textbox | Heat Soak: P2 (Kpa/Bar)
| 1a347705-2201-5a16-b549-96f01a7eaacf | textbox | Heat Soak: t2 (Seconds)
| b304443e-23e1-59f2-8802-67ae6436e952 | textbox | Change Over: t3 (Seconds)
| dc495ef6-2fc6-55ee-a814-61946a50cfc7 | textbox | Pressure Up: t4* (Seconds)
| 349a7808-1e9f-5d18-8f70-156f8e9aa373 | note | *t4 not applicable for SHP situations
| 18e95f0c-08c5-50fb-8da6-de7c4ee7881e | textbox | Weld and Cool: P3 (Kpa/Bar)
| c3196fd5-dfe6-50b1-aeb3-ae8a06b4b70b | textbox | Weld and Cool: t5 (h:m)
| 8aab0d41-c8af-5fe1-b35b-30b1be882210 | textbox | Rough Handling: t6 (h:m)
| 9bdee718-d0d9-57fe-9915-e734d0dccc1a | textbox | Bead Size: Min
| bf57a7e7-88b4-5d3d-9492-6ef3920cfadd | textbox | Bead Size: Max
| fc5a6f22-71b0-517f-9103-d45edbd1e8df | textbox | Comments
| e893ee60-d3c8-5157-9bf6-e21703049a66 | signoff | Add Operator Signature
| f81a9cad-2202-53fc-aea8-cbaacb40a1ec | checkpoint | 9
| 2c79cefc-aaf9-57b9-8781-5b26502d45a2 | textbox | Time
| e46d12b4-751f-5f12-b435-5de42b6ea1f5 | textbox | Ambient °C
| e1c59bcb-dd92-5fd0-ae3c-a276e79e5f90 | textbox | Heater Plate °C
| 8d92a942-eaf6-5c37-97c3-17334f3afb28 | textbox | Drag Pressure
| 79138fa8-783d-5ae3-bdf0-6db58ef9daf0 | textbox | Bead Up: P1 (Kpa/Bar)
| 35d1c479-4710-5411-b51f-520e9ee2bd7f | textbox | Bead Up: t1 (Evidence)
| 4c7bff51-fd41-580b-b366-2572f5019c6b | textbox | Heat Soak: P2 (Kpa/Bar)
| 0231f7b6-2bbc-52fd-9293-2720bf89c590 | textbox | Heat Soak: t2 (Seconds)
| a6d2663d-f402-54c3-b90b-5647ad1943bd | textbox | Change Over: t3 (Seconds)
| 8dba2c13-16d5-50e0-99b1-7829ba447443 | textbox | Pressure Up: t4* (Seconds)
| 99e5e633-b91b-59f1-95f6-c883fd560261 | note | *t4 not applicable for SHP situations
| 14cd0078-2664-5624-88df-1a0a070f69d5 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 689a73a5-db8e-50cc-8e15-e973bdc64f46 | textbox | Weld and Cool: t5 (h:m)
| 685abf86-ae3f-5485-bf90-dbae9f453d0f | textbox | Rough Handling: t6 (h:m)
| 320c993e-72ba-58c6-8b02-52f41709d669 | textbox | Bead Size: Min
| ed77ab77-b645-5da0-97f0-e1fa2011bc28 | textbox | Bead Size: Max
| 60c75f13-475d-5a5e-bd2e-02d1de1be078 | textbox | Comments
| 20d0e98f-904e-5a83-816a-aea5353f2053 | signoff | Add Operator Signature
| e48a2151-c0b0-593e-afe7-b90d947c1f50 | checkpoint | 10
| 13ebd8cd-7e46-5e58-ac80-3969e63659b6 | textbox | Time
| 3db617d6-c55e-5b1b-9bc0-2060de7cc58e | textbox | Ambient °C
| e76f7ff5-3752-555e-b9b5-2b68da0eeb92 | textbox | Heater Plate °C
| 678b39f4-b138-592c-ad7a-ff86edcda462 | textbox | Drag Pressure
| fe052fff-e524-510d-90ae-d0e0b378bf2b | textbox | Bead Up: P1 (Kpa/Bar)
| 95f3bc5d-4bab-5569-8b81-c518272cc777 | textbox | Bead Up: t1 (Evidence)
| 0db83871-a500-5c23-80b7-d414bac79e91 | textbox | Heat Soak: P2 (Kpa/Bar)
| 62de5984-72e4-58cb-abc0-3ed4ee1ed36c | textbox | Heat Soak: t2 (Seconds)
| 6510e35f-c6db-5791-97a1-c218145efeea | textbox | Change Over: t3 (Seconds)
| 38c66fc8-c2f7-5be1-849c-9b2712b2a659 | textbox | Pressure Up: t4* (Seconds)
| d0a4931a-daf3-52be-8357-3e56e9a44643 | note | *t4 not applicable for SHP situations
| 4371880b-5991-54f0-97a7-ebac0dfd77c7 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 9a0b6d19-2df5-5c23-ad28-4ac5854fd1dc | textbox | Weld and Cool: t5 (h:m)
| 5c343646-c8e7-5eea-a1e8-24990a277796 | textbox | Rough Handling: t6 (h:m)
| ffcac9cd-f968-55b3-9b14-61a405f27661 | textbox | Bead Size: Min
| 6ce557ce-f756-53bd-a2e5-6fda7e99d876 | textbox | Bead Size: Max
| 91307927-b19d-5b0a-b370-aaada4f41cc6 | textbox | Comments
| e99bd6f2-989e-5d94-bd70-78959c220c98 | signoff | Add Operator Signature
| 2b0bea58-0539-585d-af09-3bb070c1b6d5 | checkpoint | 11
| 53b2f860-eea7-5a3e-a64e-901575ae0fd9 | textbox | Time
| 543469d9-517d-54a9-ab4d-040df6becd9f | textbox | Ambient °C
| 4019160a-8475-5dd7-86cf-25bd345c2583 | textbox | Heater Plate °C
| 96f95b28-4bee-567a-958e-b24b477dffd6 | textbox | Drag Pressure
| d548ba3a-c539-591f-9c6f-379b7e74daa7 | textbox | Bead Up: P1 (Kpa/Bar)
| 46c89aea-23a3-5471-9764-5d39ee0b24a0 | textbox | Bead Up: t1 (Evidence)
| a486b75f-2f39-5fdc-af45-e5f97f1427d7 | textbox | Heat Soak: P2 (Kpa/Bar)
| 84c6f7a8-855e-55c4-8aad-fb74a5c66dbd | textbox | Heat Soak: t2 (Seconds)
| f0175d97-9f0e-5c5d-8c01-4204b9b66b0b | textbox | Change Over: t3 (Seconds)
| cfefa22e-cde7-51e3-8be6-c4c624a55533 | textbox | Pressure Up: t4* (Seconds)
| 64337296-f6c1-56d2-9d37-e5887baa0618 | note | *t4 not applicable for SHP situations
| 25b7cc88-e7da-5c46-9a9c-f013d1b7dcb4 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 8280b597-2298-5ae2-81b5-e94025c75b82 | textbox | Weld and Cool: t5 (h:m)
| a2e3befa-30db-5d9b-923e-a2e43e81c4a5 | textbox | Rough Handling: t6 (h:m)
| 90d16c4d-4a09-554e-a5b1-a3e414b0865d | textbox | Bead Size: Min
| 26115009-8dbf-566d-9438-ac58659694e7 | textbox | Bead Size: Max
| 93bc5a1c-5698-587c-acad-5fdd8fcd9b29 | textbox | Comments
| 46e0965a-29e5-5e68-a1a7-64201f269c65 | signoff | Add Operator Signature
| 0e643ae4-e6c2-54a9-8747-f8b26568f716 | checkpoint | 12
| ff13f2af-268d-5c52-8f57-66ce637063dc | textbox | Time
| 9e9c46cc-0690-5a79-a35e-bf57c9a2025e | textbox | Ambient °C
| 0b15c02f-8ef8-5ede-a025-777ff9c0ce25 | textbox | Heater Plate °C
| 106acc3a-add6-5b20-a30c-23487e6d58ea | textbox | Drag Pressure
| b70e0548-ae95-554f-b70e-b2c68afde17e | textbox | Bead Up: P1 (Kpa/Bar)
| 42779eba-89d8-5e6f-9204-d94c047daa35 | textbox | Bead Up: t1 (Evidence)
| a40f693d-96ce-560c-8582-487d21756759 | textbox | Heat Soak: P2 (Kpa/Bar)
| 8975e037-bcc2-51fc-ac6f-0a4318bf354a | textbox | Heat Soak: t2 (Seconds)
| 3c75c233-e69d-5d5a-a6c9-43a26cbf3812 | textbox | Change Over: t3 (Seconds)
| 5c3388be-bb16-5984-84a4-72e50ead1129 | textbox | Pressure Up: t4* (Seconds)
| a787c89d-9594-568d-bca6-b607465311a4 | note | *t4 not applicable for SHP situations
| 25fab38e-55a5-502b-b13c-57b6b808cbe1 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 2d95d398-025d-59c6-9768-000abbc056aa | textbox | Weld and Cool: t5 (h:m)
| 2e6e8933-b8a0-5b82-939c-09796f5540d3 | textbox | Rough Handling: t6 (h:m)
| ab34fddd-b094-5057-9a65-9b7d7a189285 | textbox | Bead Size: Min
| 9cb40fac-ad4a-5be9-8ad4-a7842288cce2 | textbox | Bead Size: Max
| 988e914e-850b-57fa-b02d-ee5b6c102b84 | textbox | Comments
| 1d6d316f-f043-5d0d-8221-86db1634ab9d | signoff | Add Operator Signature
| 30bc1dbb-5ad3-52f3-bcae-8c3add468ed4 | checkpoint | 13
| 748b51fe-3a53-5c2d-bcfd-3df1d00ca0d1 | textbox | Time
| ac72861e-30c7-55cc-9466-968c3f6de48c | textbox | Ambient °C
| db47b348-f555-57f4-b63e-7bfd6b784815 | textbox | Heater Plate °C
| a92d4d48-a6c9-51c3-8e79-952642d69c06 | textbox | Drag Pressure
| 28bc6b16-0ae2-5641-ba6c-004068d1041e | textbox | Bead Up: P1 (Kpa/Bar)
| 2fed65ac-def0-5f82-b88c-b811da9965a1 | textbox | Bead Up: t1 (Evidence)
| 82259554-c0c2-56b9-b36f-3b55cffad1b6 | textbox | Heat Soak: P2 (Kpa/Bar)
| d381bdbe-33a0-54b6-9629-ef55fd71e903 | textbox | Heat Soak: t2 (Seconds)
| ed458da1-4766-50c4-b3a5-5188b32c8aec | textbox | Change Over: t3 (Seconds)
| ba3c330d-f2a7-5fb1-9e56-e65bd6782a91 | textbox | Pressure Up: t4* (Seconds)
| 009742be-7b0d-50ac-98e8-5eb3923b5977 | note | *t4 not applicable for SHP situations
| adfbec0d-e7f4-5f29-8019-de03bb33a055 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 3e7bf794-a143-56e7-8068-d7d7a0ca5720 | textbox | Weld and Cool: t5 (h:m)
| 5da0e128-0c38-538a-8723-f23ad0ab15de | textbox | Rough Handling: t6 (h:m)
| 298241c2-04d5-53a4-9682-f47274449c44 | textbox | Bead Size: Min
| facd45ab-fee1-5b38-8f4c-125657c1d7c6 | textbox | Bead Size: Max
| 6ada4d34-58fb-59e9-9956-968fcf92af91 | textbox | Comments
| 1858c9df-5b26-5c9d-a77e-f354de7235f2 | signoff | Add Operator Signature
| 45e03f67-4db9-5263-9332-bc9ca56b237b | checkpoint | 14
| a7612892-71fd-5c4e-910d-64ae742ac696 | textbox | Time
| e76a5509-9558-5be7-8d62-c8b58e36f04e | textbox | Ambient °C
| 04fd5155-5e47-5e7f-9612-e8e16cf52c40 | textbox | Heater Plate °C
| 862c1535-e1da-5054-86a6-cff4772c11b9 | textbox | Drag Pressure
| 8d9b7892-d0c9-54e1-8d53-df1aa92a7054 | textbox | Bead Up: P1 (Kpa/Bar)
| f9c0ce2f-1d3e-52c4-b282-579531e7d6b4 | textbox | Bead Up: t1 (Evidence)
| cf18d780-76cf-5c75-be93-07a817646e14 | textbox | Heat Soak: P2 (Kpa/Bar)
| dc237503-ebfb-5a09-abdf-fc5c1eb24f0d | textbox | Heat Soak: t2 (Seconds)
| 71caa803-60a9-520d-bc3f-d697de1cd147 | textbox | Change Over: t3 (Seconds)
| 93054656-87b0-5c6c-bc5e-92d7612ef99f | textbox | Pressure Up: t4* (Seconds)
| 0f0dac9b-b2b8-5ced-a346-68bf1137b01c | note | *t4 not applicable for SHP situations
| 67bf54cb-515e-560b-b0af-a0c385b93180 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 91a16908-7a75-56fa-8e74-548795f0a95f | textbox | Weld and Cool: t5 (h:m)
| 0b074d4a-a6cd-5238-9064-d11a75c4bd12 | textbox | Rough Handling: t6 (h:m)
| 2a10f2cf-e0be-5a79-84e5-33dbcd522e97 | textbox | Bead Size: Min
| 8d2e450b-487d-5837-b735-f94a0621e840 | textbox | Bead Size: Max
| b1d20e13-32e8-514a-a611-a247bcc3e657 | textbox | Comments
| a272b3bb-fb42-577d-b8b0-bbaf9df2e749 | signoff | Add Operator Signature
| c4f85408-0c95-5c6e-926d-cd261cc5057f | checkpoint | 15
| e4908b7e-ea08-566c-833f-65fc5ecfbdc3 | textbox | Time
| 5a214473-d982-5938-a146-47bc64d4efd4 | textbox | Ambient °C
| a49ff0e6-04ac-539a-9bf0-32e64a73816f | textbox | Heater Plate °C
| f318954f-5b32-5b37-978d-b9555a361be1 | textbox | Drag Pressure
| 7d42aa3f-83c3-5159-86b7-70aeb7e88d3d | textbox | Bead Up: P1 (Kpa/Bar)
| eb18063d-dd2b-52d9-99ef-6e743cf85068 | textbox | Bead Up: t1 (Evidence)
| ecce34d2-5aa5-5df7-9927-83ef5f51f867 | textbox | Heat Soak: P2 (Kpa/Bar)
| e0494f53-b7af-5b2f-b862-da90602027d7 | textbox | Heat Soak: t2 (Seconds)
| d828b996-b513-512f-8697-9fcdcd50f51a | textbox | Change Over: t3 (Seconds)
| 0c57053d-043e-5704-9e5c-a5dcf43126b6 | textbox | Pressure Up: t4* (Seconds)
| 41c80c9b-7961-5d92-ad7c-f25e0d5f71f6 | note | *t4 not applicable for SHP situations
| 246d0ed9-97fa-576b-b262-cca124664915 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 49d17b6b-0d97-5422-b887-0e3a06a3e14d | textbox | Weld and Cool: t5 (h:m)
| ef20136f-08df-5ac4-af0a-535f4f28192c | textbox | Rough Handling: t6 (h:m)
| b6c69118-760d-5c00-bb10-5efafb78912b | textbox | Bead Size: Min
| 9215262f-c875-5d5b-8b74-92dd0c2831f6 | textbox | Bead Size: Max
| 9b817919-9485-5e3c-a7b9-25d8b93704eb | textbox | Comments
| 720bf538-b609-5363-809e-c29bb4056269 | signoff | Add Operator Signature
| 5ab7a9c9-d48c-5adb-8a4c-40224667d9ab | checkpoint | 16
| 83cd7473-1388-5a2a-8755-b5def54256b8 | textbox | Time
| e8e4f420-3047-5608-8132-e29dc812ffa5 | textbox | Ambient °C
| 21051102-a589-51f4-aad9-3b8ad92af892 | textbox | Heater Plate °C
| a2973ab5-51f3-520f-a3c8-75ce65ff5551 | textbox | Drag Pressure
| 3d051440-88a0-5abf-adef-2faf517a94e5 | textbox | Bead Up: P1 (Kpa/Bar)
| b0095b18-9a25-56f5-b2bd-997dba748629 | textbox | Bead Up: t1 (Evidence)
| 3b071995-d27c-5a53-8e1a-778218da0782 | textbox | Heat Soak: P2 (Kpa/Bar)
| efc9070f-0a39-50cb-802f-9db1127431da | textbox | Heat Soak: t2 (Seconds)
| fcc4d142-cece-50e8-91fc-205fd24f6a5f | textbox | Change Over: t3 (Seconds)
| 7ecc3263-dcfc-53ab-a7e6-eddd9dbb7125 | textbox | Pressure Up: t4* (Seconds)
| 551ac8b9-5f7c-5249-9810-1ac1c85355dd | note | *t4 not applicable for SHP situations
| bbfbb28d-f2f3-53e2-bfdd-7c0f3b219350 | textbox | Weld and Cool: P3 (Kpa/Bar)
| 25be3ce1-36a8-5ea1-8a27-d8fb5dbb946e | textbox | Weld and Cool: t5 (h:m)
| 4836e23b-4258-54fd-9cd4-d2c17018b188 | textbox | Rough Handling: t6 (h:m)
| de193e04-fb91-522a-b753-b73aaba7c062 | textbox | Bead Size: Min
| 686dede9-217b-5301-a4c1-e1ecf0d79483 | textbox | Bead Size: Max
| b276dde4-4711-5011-80a6-5bf9e134857d | textbox | Comments
| 39609a98-67de-52e9-9586-9605f5f5f44c | signoff | Add Operator Signature
| 959d0e0a-a6d6-5426-b03b-2bff74b44df3 | checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  | QA 29 Periodic Flushing / Copper Protection Test Sheet
| a7c0662e-60d1-58f3-8e2d-b23aa5deb9ba | checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
| 80e7c297-50b7-5d0b-866f-1fb9ddb7de55 | note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
| d81741ec-c794-5f58-95ad-a812b36878a9 | note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
| c282be0d-845e-5462-823f-cdcdbba87e3e | checkpoint | Flushing Details:
| dba80432-6184-5118-abb0-60a9def9c585 | textbox | Level / building being flushed:
| 570dae14-a5d9-5816-a08d-1f3632f279c0 | button | Time and Type of flushing: | Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
| 5c90528c-6f25-5216-9e89-177c70735552 | textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
| 4fd14e7f-23eb-524d-b588-c15fa5163600 | textbox | Start time of flushing:
| b33f0b58-edf1-51c2-98ad-d9a86e9fb41b | textbox | Zone/branch to be flushed:
| 652e9774-91c3-55fe-83c2-53f9b5e0e8aa | textbox | Finish time of flushing:
| 818ee21c-2c8f-5875-acf1-cac8da47d1c8 | textbox | Zone/branch to be flushed:
| 0e2d19e5-f225-5d0c-9924-50ca86745f4c | checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
| e94bef9c-e533-5f2d-8e8a-f268d7fe3370 | checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
| 92e6e588-d313-5e44-8fe3-823f289e9f8d | checkpoint | Have you set a reminder for the next flushing of this pipework?
| 775bfb0a-0611-54a1-8637-06238dfb568d | checkpoint | Have the hot and cold been interconnected for flushing purposes?
| 7e05ef7f-bd31-5667-948d-82bc4fe5a610 | checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
| f2d29014-ec27-5e96-98ef-fa7b4678ca54 | textbox | Date for next flushing:
| 3e794e02-826c-5832-b41b-34920b3e5122 | textbox | Test completed by:
| 7ad215f2-899c-5874-b842-20631844d69d | textbox | Builder Representative:
| 50721303-a038-5977-9642-47de2d9caf8f | checklist | QA 30 - Fixture/Hydraulic Installation |  | Fixture/Hydraulic Installation
| a9e1ea2b-799a-5449-8020-407dbe196b58 | checkpoint | What is being installed?
| a2d7abd6-97f6-5639-9052-0bec5a4ea929 | checkpoint | Where is this fixture being installed?
| ea0cb74b-d31b-5934-b73a-8c9c3592824b | checkpoint | Have all parts been connected/completed and tested? If no, please detail why?
| 9466f9f1-c3f3-5da5-a1a6-b3cc08b62b8d | checkpoint | Has photos of installation been taken and uploaded?
| 36c4fc54-5ba1-5ba6-9d8e-659a3a5e4f9b | checklist | QA 31 - Hot Water Service Maintenance Log |  | Hot Water Service Maintenance Log
| c5e691b7-9a0c-576c-90ee-c7233b18c6e9 | checkpoint | Hot Water Service Unit Details
| 5ba17582-ab6f-5989-ae29-87f5fadb283f | textbox | Purchased from:
| 493fe2fb-5879-5cb8-b822-680d9a6988a1 | textbox | Make:
| 6a5a4743-6599-5456-8980-a14aa118f8cd | textbox | Model No.:
| a3035425-7210-5171-9336-4911cfb04e8c | textbox | Location:
| af109ad8-4faf-5771-b51a-69fe136b80c8 | textbox | Room Designation:
| 149190a9-e305-597c-8018-331afd1b1ac3 | textbox | Installed by:
| ea06dcaf-d924-5479-b384-78ff1b210cbb | textbox | Installation Date:
| ffa0020b-5d50-522e-89ba-d401f8650320 | textbox | Number of units in series:
| a49b22a6-39bf-5cc1-9011-51a78aaf5f3b | textbox | Prescribed temperature set on unit or combined package:
| 22e49bd6-3bda-5925-8ddf-d5c03c2c930e | checkpoint | Does installation comply with manufacturers instructions
| 80ae1e00-4559-5bbe-ac85-8cec3c7d7f8b | checkpoint | Does installation comply with current requirements of the local water supply authority
| a796eb1c-193c-55ee-a848-36fa2706bfb6 | checkpoint | Clean Pump Strainers
| d417249d-461e-5f16-a434-06c2d2193080 | checkpoint | Clean Hot Water inlet Strainer
| 699338bb-deb9-527d-993f-ea45cfcfa842 | checkpoint | Clean Hot Water Return Strainer
| 8a550b57-6e16-5878-90e3-46261f47f7f8 | checkpoint | Confirm all Valve Isolation reinstatement
| d94e369b-35ba-58aa-b2ad-907f3999c239 | checkpoint | Confirm Unit is Operational
| cb76d582-4954-5a36-9f28-07baa4a3930f | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
| df7d45dc-5841-5b3a-8ace-d32f2292d029 | checkpoint | Commissioned By:
| 2b06b16e-168d-5fd3-9842-9300234ee973 | textbox | Name:
| c18f1ab9-b5a8-5adc-956b-c7d1fe467c18 | textbox | Date:
| f533f4ea-6e7a-5539-8b71-ff611bbb0a27 | checklist | Safety Shower Functionality Audit |  | Safety Shower Functionality Audit
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| 8778cc5a-77c4-534d-b2b8-78002ad04a20 | checkpoint | Accessibility
| 255bf2ea-4dbc-53b9-bc9a-a6af586de43a | note | Is the location of the product in an accessible area, eg, no more than 10 seconds away from the hazard and has a clear path leading from the hazard to the safety product.
| 9191443a-00d7-5558-975a-a31ac9e31359 | checkpoint | Identification
| 50236b37-8a2b-5916-bc9a-7ea2ebf07827 | note | Is the safety product clearly identified with appropriate signage visible from the hazardous area
| 9158f8ea-6228-5832-83b3-c2c3e5bc3ebb | checkpoint | Support Brackets
| c003348d-5c73-53b2-9fa0-16798f9ed71b | note | Is the safety product securely fixed with corrosion resistant anchors and brackets
| 717737fe-4d6c-5e08-9b70-a0af5142aeb0 | checkpoint | Installation details
| 1befcad8-5fc3-5d60-a971-11f3ff38b326 | note | Is the safety product installed at the appropriate height
| 896e788d-5834-568a-8fe6-53e752b44d2f | checkpoint | Exterior and operating instructions
| c61c1603-c881-53f3-8178-b14ba6c9dd7d | note | Is the safety product fitted with operational instructions and a test tag
| 5d30ff43-ceac-51ce-9d57-19b5881bed10 | checkpoint | External Damage
| 08690f65-1d6b-5973-ba4e-a7e7d6c00005 | note | Is the safety product free from visible damage
| de9bc879-8f58-5820-ab7d-b364384f9c73 | checkpoint | External Corrosion
| 8c661f44-0fa1-55e2-825d-0903798a5720 | note | Is the safety product free from external corrosion
| 611d4d2e-00cc-531f-83bf-b333eb9eb80c | checkpoint | Activation Points
| 583165d7-3768-5774-b165-505e3d627ded | note | Are all activation points secure and in good working order
| f367e555-5a95-5529-bad9-a5bbec830c0a | checkpoint | Leak Test
| 2a811285-4187-571f-a88d-316c691bdd2d | button | Check that shower/eye/face wash has no leaks - shower rose. | Pass, Fail, N/A
| b3712b69-9e14-5fd2-bcd0-8b90b7d313a3 | button | eye/face outlets | Pass, Fail, N/A
| e9a4585c-19ec-5923-9824-58ca8beefe8a | button | ball valves - shower 1" | Pass, Fail, N/A
| c79097a2-183d-5861-881d-158fb2de9c71 | button | ball valves - eyewash 1/2" | Pass, Fail, N/A
| cf8b2fa4-5ee7-52b8-b162-45ad50fda255 | checkpoint | Dust Caps
| 6af7dd37-3df9-5493-a18b-53d8b083d02b | note | Are the dust caps correctly fitted and in good working order
| 169e8112-387b-5606-a711-e874cc957e1b | checkpoint-no-value | Flow details
| cde02bc4-cdee-5ccf-84cb-7c9a8f10bee2 | note | What are the flow details from the safety eye wash outlet
| 8ecdc839-b77a-5068-8d60-47b4eb1377e1 | button | Does the flow meet in the middle | Pass, Fail, N/A
| 0b60768c-9d03-5f77-8d6f-bec913077777 | note | what are the flow details from the safety product with all outlets flowing
| 3d1677f8-34d4-5760-830e-fa2d3da5102d | button | Litres per second | Pass, Fail, N/A
| fb21f277-d956-570d-9ee7-020548573432 | textbox | LPS
| 20c4b5cf-749a-5834-91e3-35dc9da30a05 | checklist | TMV 12 Month Service Log V.040221 |  | TMV 12 Month Service Log (use a separate checklist for each valve)
| 77049996-5759-5a66-a03e-18741f60b6a0 | checkpoint | TMV 12 Month Service Log
| 6f50691a-1052-508d-8942-49e4f9fee3e3 | textbox | Building name:
| 4b152a5c-c292-5f2b-b65c-9bd875e1b6b0 | textbox | Contact person:
| 9009d3d3-e172-5e90-98c6-2424962fd352 | textbox | Address:
| fe012bfe-2595-5101-b131-a979e02183bb | textbox | Phone number:
| 2474ad68-5cf5-5eb5-bfbd-2aa6b41ee866 | textbox | Make of valve:
| b58ba77d-9724-59e0-b632-a2c01965168a | textbox | Model number:
| cec86261-f94b-5a41-ac58-08fa2f04f68d | textbox | Valve location:
| e0416798-48a1-5701-87e1-805195bb6fda | textbox | Room name:
| 07f0cc2d-796d-535f-ad26-3220c5fe212e | textbox | Date of service:
| 74dc33f9-1bd1-5c78-a8ca-969583863bd7 | textbox | Temperature: |  |  |  | °C
| 34c78806-8271-5c24-911f-9d7ebdc7ae05 | button | Element: | Ok, Faulty
| 7b702738-5414-58fe-a150-2d29a9bfc558 | button | O' rings: | Ok, U, S
| 42b01cf6-fa34-54d8-8d06-354262c6949c | button | Strainers: | Ok, Dirty
| 5b9b3278-8c97-5b0f-849a-0a296e4355c0 | button | Non-return Valves | Ok, Faulty
| 3364de9b-9acd-5733-b0fa-6204cd3ed21b | button | Fail-safe test | Ok, Faulty
| 71c93ee4-c284-55ce-99e2-9bd18f206e34 | textbox | Serviced by:
| 4fd502bb-1d32-589f-b31f-cc82df6a231d | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
| d80d130d-72f8-5fc9-872b-1fc379f43b15 | checkpoint | Completion
| bb196e3b-d980-5044-b91f-ae492fc70d5c | textbox | Plumber Name:
| 531f64fe-81d4-5217-9fc6-6a442b449dc7 | signoff | Add Signature
| cb1720a3-9665-555f-aaa7-61a44084e1a2 | checklist | TMV Commissioning Log Sheet V.040221 |  | TMV Commissioning Log Sheet
| 2eee693f-4717-525c-8936-347782dbe5d0 | checkpoint | TMV Commissioning Log Sheet:
| 26208a38-cac2-5918-9058-d6adb270105d | textbox | Building Name:
| 787ef829-aee9-54fc-a8fc-d4e33aabce85 | textbox | Contact Person:
| 9824ebd0-4dfb-5815-815b-add1ffc95121 | textbox | Address:
| cd626b90-22ca-5992-bd5f-ab6086b4c2b3 | textbox | Lic:
| 82ed12b7-69b1-577b-bf22-722957661691 | textbox | Registration number:
| 07f933ec-5bcf-542f-9e95-50b4b99e4def | textbox | Phone number:
| 01186232-24be-5ea9-b7b4-5b0f1683cd16 | textbox | Make of valve:
| de882b36-bfe4-5030-8645-4723ae74aacc | textbox | Model number:
| 8bdd78ff-e6a0-5a00-8c68-b3ec31b3c9f0 | textbox | Valve location:
| a8dad8ea-077e-5472-9d1c-e77b6e4de212 | textbox | Room name:
| ebd818f4-1e15-53d2-a9c8-f391da455ace | textbox | Valve purchased from:
| eb6724cd-5f16-5c95-8c50-4a975f90a34c | textbox | Installation date:
| 75b6926b-f474-5f4e-a8e4-46e55d7e5b1c | textbox | Valve installed by:
| b4b5c4ce-9f24-51ec-b78e-e8e6560aa58c | textbox | Number of outlets served - Baths:
| 66597c56-2cf7-5863-bfe5-78ad7d624a84 | textbox | Number of outlets served - Basins:
| b62cedc0-a3a0-58d8-a8e5-e1782bf98dc3 | textbox | Number of outlets served - Showers:
| eeafb204-d20a-5630-84dd-39203fef67e7 | textbox | Total number of mixing valves on site:
| 62c1e723-7b4d-55f6-a717-edcf40fa36c3 | button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
| 91258da4-776c-536b-acc9-d1e75ae8315b | button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
| 85217217-7ea6-569a-b659-e3b40f2e6f2e | textbox | Temperature of hot water supply?
| bdb81617-ceb6-5279-b3cb-aa4d42f75ac6 | textbox | Temperature of cold water supply?
| 30190140-47c3-5ce7-9389-198b882367aa | textbox | Temperature of warm water delivery at outlet fitting?
| 5ef75339-02af-5d05-8161-0937873b45c9 | textbox | Dynamic pressure of hot water:
| db48ded7-f764-5dba-a1ae-dd93bc84c96d | textbox | Dynamic pressure of cold water:
| 4f07e862-63a4-5510-9bb5-28041ddf9970 | checkpoint | Check fail safe operation (hot water at least 20c above warm water)
| 4355dc79-ce72-53a2-bb34-68f3e45b61ea | checkpoint | Commissioned by
| 65f86cba-77a0-5c26-afdf-7b53eef90330 | textbox | Commissioned by:
| a3daefa7-afd4-5c1d-aae3-7ac0018157bc | textbox | Company name:
| 0669c9d9-dd98-52ae-876c-a2426952d228 | checklist | TMV Routine Service Log Sheet V.040221 |  | TMV Routine Service Log Sheet
| 4b8e9ff3-e317-55fe-820b-a7d1d1978b1b | checkpoint | TMV Routine Service Log Sheet:
| 3c46d042-a662-50ff-97e5-fa7e49457aa9 | textbox | Building name:
| 4c91d7fa-44c1-5e5a-9579-d0ace27e6a4c | textbox | Contact Person:
| cf04d76f-e714-5108-b29b-9f8e5358a006 | textbox | Address:
| 2954099f-da86-5fe0-ac4b-ec657dc24197 | textbox | Phone number:
| 38da5784-8c05-58cc-8c2e-504bd857f216 | textbox | Make of valve:
| ed15bce9-8c6c-58c1-9a8f-2393b7b3a8e9 | textbox | Model number:
| 6d06dbe5-021d-55c8-adea-5c4de075304d | textbox | Valve location:
| 4e8c9288-3144-50f5-92b1-fe6ecce0da68 | textbox | Room name:
| 6c4362c9-c50d-54c4-9ba5-d7db15b9820c | textbox | Date of service:
| fb53c14a-bd8f-5d0a-88cd-b9ca8414b000 | textbox | Outlet water temperature:
| de222692-69fa-50dc-821b-7c9a91ef6e54 | button | Outlets flushed for 15 seconds | Yes, No
| 4d8f7a63-c119-53ab-94e4-41a9172f8728 | button | Shower heads disinfected | Yes, No
| fb96229d-b921-58f9-aaeb-6504200b316d | textbox | Serviced By:
| e88448a1-261a-5433-a2ad-91db33a5f5df | checkpoint | Recommended Service Periods
| c302b43c-ebfd-5a23-b91e-249dce98dbb5 | note | Outlet water temperature = Fortnightly
| 8fa78483-a776-56c5-bf5e-1d073c25a39a | note | Flushing of outlets = Weekly
| 511f6143-865f-5710-b8e8-c3c2c6aa3ed2 | note | Disinfect shower heads = Monthly
| ac7917c1-c075-57ca-80bd-09cfec841701 | checkpoint | Completed by:
| 3eb1dcb5-47c5-53b7-8026-074388ae4da4 | textbox | Plumber Name:
| 1862f941-b645-54d2-bde6-e9dc670f9e7c | signoff | Add Signature
| f28c37c6-c2e4-5ccf-984f-1d374c916d01 | checklist | VHH - Water Protection ITP (V.090421) |  | VHH - Water Protection -
| efd5b141-8b5f-5dbb-937c-282341f1e0b4 | section | Part 1 - VHH Periodic Flushing / Copper Protection Test Sheet
| 2ab05d22-5099-5fac-96d7-e5561c94d25a | checkpoint | ITP details
| a47c0c3f-ba3d-5343-89b3-c9d48dcb12bf | note | Copper systems are failing in the construction industry due to issues relating to design, water quality, the management of water during construction, long term maintenance of buildings with issues arising from building management team not following protocols outlined at hand over. Stagnant water being left in both hot and cold copper pipelines have been deemed to have been a contributing factor to recent copper failures. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water
| 1d28916f-c0b9-5b56-a63b-6e8696d5f957 | note | Geschke Plumbing in consultation with John Holland & AECOM have put forward a proposal of periodic flushing of the systems during construction to mitigate the stagnant water issues that have arisen in the construction industry. The purpose of this ITP is to help create a strategy to ensure water is flowing through the piping system and flushed at nominated locations
| 31d10cf0-faa0-5586-ba19-071507a56087 | note | Plans to flush to be submitted to John Holland prior to any flushing occurring on site
| a2245977-ec0f-5a38-b6dc-5d3c8369dcea | checkpoint | Flushing Details (Flushing to be Completed with Water ONLY)
| 7b1d1710-7b4b-51ae-8730-a9daf62f4d69 | textbox | Level being flushed
| e02bf841-2c07-52d5-a32d-c28a41c6e070 | note | Stage of Flushing During the Project
| ef70b62a-e9ad-52ba-b3e4-3b6708c8a509 | tickbox | 1. Initial flush after installation of pipework and prior to Quality Control Pressure Test Report (Geschke QA 6)
| 1ebbe732-5f30-5d2c-9c7f-c0f8237e83d3 | tickbox | 2. Final flush post disinfection
| 721a0b3e-8674-53a7-9f46-e70584e99fd9 | tickbox | 3. Periodic flushing during construction (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
| 359ae6ea-f072-5bfb-af85-9b37600846b7 | tickbox | 4. Periodic flushing from final flush until PC (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
| 03f646f8-850a-5a62-80a4-3ada34a268cb | checkpoint | Time & Type of Flushing (As per reference table below)
| d17d12ef-8873-5504-880e-de81e25b2eb3 | tickbox | 5. Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush
| 3e8df79c-f834-5272-806c-3deb90fe3fca | tickbox | 6. Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)
| 5158ed6e-0535-59fc-b4da-300528c7d793 | tickbox | 7. Short branches of copper that feed rehau do not need individual flushing
| b8871cfd-d894-5857-9236-248be85ca6fd | checkpoint | Which fixtures are being used to flush the system (Point of Connection & Point of Discharge)
| cdfb0da9-8da8-561a-a7dc-55408dd2b9ca | note | Fixture 1
| 9577e8cb-39b9-5d62-ac8b-3159431438cd | textbox | Start time of flushing
| 6aa572e2-e41b-586d-ae60-8ec47bfae425 | textbox | Zone/branch to be flushed
| 62fd0ad3-4584-506f-86ab-f7b867275f34 | textbox | Finish time of flushing
| 6a3d0718-efef-5bef-b6aa-ec5651746668 | textbox | Zone/branch to be flushed
| 7ce9f1cc-9f3d-56c7-b821-f7e41cc577b0 | note | .. ..
| 3c9b2bbc-45a8-54d8-af7b-acac7bb42edc | note | Fixture 2
| 9e7b2ae9-9f82-58ce-aaaf-7806ee5ad521 | textbox | Start time of flushing
| 1add0bfd-7ea2-5b86-a3e5-e8e278228a85 | textbox | Zone/branch to be flushed
| e5500dd1-6ee2-5330-9b83-3d4f8afc4845 | textbox | Finish time of flushing
| 0012f34c-0c2a-55ef-a9d0-11c11087093c | textbox | Zone/branch to be flushed
| 03b690ad-827b-5df0-94d0-8fc1be67b69b | note | .. ..
| 715e45d7-33bf-5df6-9cab-f9dc2c9e821b | note | Fixture 3
| 3b961fc4-98bf-5e11-b7fe-f58d222b2a2a | textbox | Start time of flushing
| 3b45cf52-af6b-5e87-9e42-5c49a9e7e3b0 | textbox | Zone/branch to be flushed
| dddf2579-34a5-5e4c-9d74-af72729fbca3 | textbox | Finish time of flushing
| 11c7eee3-6580-55e1-b1b3-4236385d16db | textbox | Zone/branch to be flushed
| 74ffc707-4c12-521c-8be7-c8af7eba48e4 | note | .. ..
| dfc67b06-a031-5b2f-84e2-4d4fb87877dd | note | Fixture 4
| ce13de99-f351-59ba-ac36-d658c7fb4f11 | textbox | Start time of flushing
| efb1dc6d-0c2d-5f69-9202-2140ad900924 | textbox | Zone/branch to be flushed
| 8fbd05d3-b443-5b39-b3ab-2f631976c7ef | textbox | Finish time of flushing
| 17eebb25-70a0-52c7-9e0a-1559d4e52a0d | textbox | Zone/branch to be flushed
| 19df8e61-1f11-51c5-a20f-f8f81462420a | note | .. ..
| 99d1a2d9-e8d1-5d7b-b854-3bc2382f80c5 | note | Fixture 5
| 9896504b-030c-543f-bb02-03c1e3db9dca | textbox | Start time of flushing
| a478cfc2-683f-5adc-9a15-1d01ce5ed022 | textbox | Zone/branch to be flushed
| 2ec13bc7-8b11-5425-94ef-e4950caa0aa4 | textbox | Finish time of flushing
| 1270cdde-a99d-5cbd-9375-bbf58147bc4d | textbox | Zone/branch to be flushed
| cf660ccf-2e0f-5f72-8c10-80ec6d356f57 | note | .. ..
| 16fe33ed-dca3-5011-9fd6-f50ff87a1740 | checkpoint | Sign-Off - Pass once entered
| ca622f3b-d1bd-5f3b-9e43-f9491c175c1a | note | Add comments/photos below as applicable
| ef2ad896-5038-5b96-87e8-c4b0a70a2851 | button | a. Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated | Yes, No
| fc5129fd-e3bd-5648-a7b5-1ae4d657f161 | button | b. Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case | Yes, No
| dbca4f9f-0741-5694-8b22-1e329d0b22f2 | button | c. Have you set a reminder for the next flushing of this pipework | Yes, No
| a5a2cf9c-1411-5fdf-be6c-bbd8ee514949 | textbox | Test completed by
| d0dff097-67d8-5ad4-84b1-85b1c10bc2aa | textbox | Date for next flushing (Flushing to be performed every 4 weeks at a minimum)
| 72eda57a-1f0b-5e7e-995c-d96b6e49dfcc | signoff | Click to add Builders Signature(s)
| 7c9a9e1a-1d4e-5ea4-a9bb-a82737153162 | checkpoint | Reference Table
| ba92ffbf-ef7b-5d98-9be2-354484227217 | note | 25mm Pipe / 0.49 (L/m) / Flush for 0.15 (Mins)
| 92c1ca36-90ff-5c84-832c-b8c414f1577b | note | 32mm Pipe / 0.80 (L/m) / Flush for 0.25 (Mins)
| 98e44198-4a8a-5f20-ba53-a128e83c81a2 | note | 40mm Pipe / 1.26 (L/m) / Flush for 0.39 (Mins)
| 67087260-04fc-5a9d-9d8c-272b4ab28478 | note | 50mm Pipe / 1.96 (L/m) / Flush for 0.61 (Mins)
| d0b82f22-83ac-54d4-9226-7c5121c04a17 | note | 65mm Pipe / 3.32 (L/m) / Flush for 1.04 (Mins)
| ece32ea9-e6f8-52ed-9908-308dea4bb8b3 | note | 80mm Pipe / 5.02 (L/m) / Flush for 1.57 (Mins)
| e9731a23-b9d5-5c1b-bb1e-e1a9849e0248 | note | 100mm Pipe / 7.85 (L/m) / Flush for 2.46 (Mins)
| e84c2bd9-4927-5fdb-b42a-2afb1bd9c419 | note | 150mm Pipe / 17.66 (L/m) / Flush for 5.53 (Mins)
| a8ca5914-ec89-598a-a33e-5d54a2f086b3 | note | NOTE: The table flushing time is based on 100 metres of pipework discharging through 16mm nozzle at 350KPa
| 431f5903-29b6-5f4c-bd3d-31ba409ddb70 | section | Part 2 - Water Quality Testing Frequency
| 061d1007-5427-5484-9010-724ad045be72 | checkpoint | Water Quality Testing Details
| 4cad266e-f3dd-5ca8-8225-c0dd77d2e5ff | note | Stage of water quality testing during the project
| f1323cc2-208d-5270-813d-f7ec443609b2 | tickbox | 1. Periodic water quality testing during construction (to be completed every 3 months)
| ea7af0d4-d5a5-5951-b6cc-f7101ea08957 | tickbox | 2. Water quality testing post final flush
| 09f91e64-7f74-41c9-8af3-8a3fbf4e237f | checkpoint | Sign-Off - Pass once entered
| 38ce1d14-ee5e-5937-8518-d466ffe1d6be | note | Add comments/photos below as applicable
| 5fe20241-cab8-5014-a263-4cfe4a87f95a | button | a. Geschke and John Holland management informed of sample / testing | Yes, No
| 92dc9e8c-cd9c-592d-857d-241abdecce38 | button | b. Has the schematic / location of the sample collection been highlighted, attached, and nominated | Yes, No
| 41ef2235-966a-5a10-a83c-69104b8b0eed | button | c. Sample captured as per laboratory requirements | Yes, No
| bd7b5737-42ed-586f-bd43-5194c8d054ab | button | d. Time and date of sample recorded | Yes, No
| f434af43-132e-55d4-8ba0-ca19640d884e | textbox | Time of Sample
| 09ad9cd2-6420-55fd-baeb-826a49a0d75f | textbox | Date of Sample
| 01329bfa-7873-5948-9989-46c05c34dc24 | textbox | Location of Sample
| 94850d26-fd8e-5068-8bf2-3e4cbba33fb2 | note | .. ..
| eb981d73-4fb0-5906-8813-caf839fdd903 | textbox | Sample collected by
| 429d63ca-ae20-5c19-b8cf-ed9ef8cd2a9d | textbox | Date for next Water Quality Sample (Water quality testing to be performed every 3 months at a minimum during construction)
| c8cdcd60-f957-5d5e-b2fa-bdaf57a8901b | signoff | Click to add Builders Signature(s)
| 4ecf8bfe-5836-55ec-b9df-1d5234e6182c | section | Part 3 - Disinfection of Pipework & Tank
| 46345207-4520-5b88-b10c-408665b0e340 | checkpoint | Disinfection Checks - Pass once below completed
| e6e740dc-b3cb-5901-99b4-f631a4c39b95 | note | Add comments/photos below as applicable
| 52c8136b-76cb-53e7-85ed-54e63c1f35b8 | button | a. Geschke and John Holland management informed of disinfection with plan provided | Yes, No
| 02f71b91-dc2f-58b7-bf4f-4dc69cae6967 | button | b. Has disinfection occurred for 6 hours as per AS/NZS 3500.1 appendix I | Yes, No
| 208783e5-25c1-503b-b137-ce9e1016b2ff | button | c. Time and date of disinfection | Yes, No
| 26180882-c7d8-5581-9204-90d2c73ee6d3 | button | d. Flush all levels and branches until chlorination levels have reached safe chlorine levels as per Australian drinking water guidelines. | Yes, No
| 7a9959a7-ea24-5920-93d8-a57bf7313d70 | textbox | Time of Disinfection
| b459ff69-10b5-5d36-a11c-b4ed70288867 | textbox | Date of Disinfection
| 2283b912-d3e8-580f-a3bc-2c977a40b50f | note | .. ..
| a59575c6-9598-5a37-a010-b30b6707cca6 | textbox | Disinfection Completed by
| 309d5d01-8cdf-55cf-af85-cb80b487d829 | signoff | Click to add Builders Signature(s)

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
b2b04e82-8039-4c95-9c87-0fe9bfa081e1 | checklist | 8.1B Stormwater Drainage Checklist |  | 8.1B Stormwater Drainage Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d1bf1f23-c527-4e27-81ac-cc9f1f98a87d | checkpoint | Stormwater Drainage Inspection Report Details:
5ca5186f-d787-5753-a7eb-1283b42e8bdc | textbox | Spec No.:
4fa73495-3d65-5b33-a9d4-53e777d004f2 | textbox | Drawing & Revision no.:
b3258eab-529c-514c-8d1d-5218a7f9aba1 | textbox | Shop Drawings no:
6db35440-f7a3-5b68-94cb-9c84d3c6e448 | textbox | Starting IL established:
20af8f8a-6442-4468-8174-f88ed1d09ad2 | checkpoint | Pipes and fittings comply with relevant Authority and Specification
3b9a9a2b-76f4-5248-9c89-1d508af23c47 | note | Spec#: AS3500 and Project Specification
e8fad1ad-83dc-5b08-af80-6f9c983ec248 | textbox | Materials used, Size and Class:
8987608e-ee2c-5609-b92a-e5bed4c5f6a9 | button | Approved by Principal | Yes,No
4c0156a9-4f07-4dca-9f8b-c33cbfb25a0a | checkpoint | Pipe Lines
b8e3d7ca-d5ff-5cdc-9d66-8019d5a30d28 | textbox | Date started:
e80f37cd-2a7f-5d90-b52e-960ec777e2fd | textbox | Drainage Line Number:
d9c047d4-8997-5b25-8571-2a083a604cfc | button | Pipe Damaged? | Yes,No
2bc2a4da-c656-571e-94a7-c4642d1cd2c8 | textbox | Jointing Required
b801e12f-8032-56da-a9c9-217c72a3e04c | button | Bedding and Haunching | Yes,No
7e65382f-7f65-4be0-8b21-46cb76267e06 | checkpoint | Bedding material, placement and compaction meets specification.
2d8a3f50-3671-59f2-9ee2-9a89e456fd5e | note | Spec#: AS3500 and Project Specification
73fc5883-839a-52da-92a2-370b9f210602 | textbox | Material used:
2aa6e259-122d-52de-a524-1f99d63174a7 | textbox | Docket #:
4153c577-0962-5553-be5b-20ca05825b4c | textbox | GPL - Initial/Date
9fed9dfe-79ac-582c-b583-968336854126 | textbox | Builder - Initial/Date
5098ec0e-6b8a-49e7-b1a7-3ef73c795b00 | checkpoint | Laying and jointing of pipes - RL and fall
c92c4f65-8e64-5a69-94a6-27908abcb603 | textbox | Jointing Type:
ffc3b5d4-b448-587b-9b4f-cafa2fe2c1ea | textbox | Fall:
e92ba7c5-7aaf-57af-8207-0edd22fdcc3d | textbox | AS3500
013936bc-1d1e-59ec-b755-9c8061ede9b0 | textbox | RL's as installed
ef48b45d-1681-555f-a081-4bcc9f0bd427 | textbox | GPL - Initial/Date
ea1ba8bc-bdc7-58fd-a198-7df6748e0a8f | textbox | Builder - Initial/Date
dc2d036c-a261-4952-9804-6e1d0653e394 | checkpoint | Backfill
72826f09-36e8-5a7f-84a0-bc5aaf43928a | note | Spec#: AS3500 and Project Specification
2e2d46a3-67e2-550b-917f-cc863125f522 | textbox | Material used:
a1fa0d56-d31d-5153-aac2-e167eb82922e | textbox | Docket #:
e5fa4b64-ea10-411b-abe7-533316f38956 | checkpoint | Pit Sign off: Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
c033d389-98f3-504f-a274-95eac9bf2750 | button | Geschke Group Signature Sign-Off added below | Yes,No
a3e01c8a-f6cf-58d4-be0f-e1427cd8c1bc | button | Builder Representative Sign-Off added below | Yes,No
0a3aaa5a-8fa6-41e9-851d-ae9c78805e4d | checklist | Project Photos |  | Project Photos
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8fdac399-981f-44cd-993c-66e47500eec3 | checkpoint | Upload Photos and Comments below
e588168f-118e-4112-81b9-057eac3c0148 | checklist | QA 6 - Quality Control Pressure Test Report |  | QA 6 - Quality Control Pressure Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
42818efd-5f9c-41c0-8385-bb7103f1334c | checkpoint | Quality Control Pressure Test Report:
9836c29c-eb2e-5af3-97b5-14400554310c | textbox | Drawing No.:
fa90e29b-adee-51f9-8f7b-bffda5f1e478 | textbox | Rev.:
d71bddd9-b22c-5cf0-b310-0f03511b6b03 | button | Test: | Air,Water
d0eeb296-54fd-5cb4-b5a8-4fdf067e34bc | textbox | Section
d47e139b-c4fc-5b58-8e4c-0e6e874d4546 | textbox | From
b59baaf5-d8e8-5bee-8c67-dd82d1c39c1a | textbox | To
987b5dc9-5bc5-575b-acea-31c1c4d4c107 | textbox | Applicable Standard No.
b8723984-9d63-56f3-a533-e59a8cfdd956 | note | Specified System Working
f569cb93-e81d-5000-9006-57ff8a6133eb | textbox | Pressure (KPA)
79f7345d-83b8-5626-b5cc-e526051c7498 | textbox | Duration (HRS)
ecac5d6d-b949-5b10-bab3-a1bf7f748caf | note | Specified System Test
40ef7618-ba01-5ec4-aa60-5f9bef3815b5 | textbox | Pressure (KPA)
192fbdf9-4d04-5872-b629-d484bc7275cc | textbox | Duration (HRS)
8ec3e6e5-9410-4ac9-9049-96bf5145e585 | checkpoint | 1st Reading
bab3e826-c6f0-5180-9924-091c3f2150c4 | textbox | Time
a3b14ea3-2ed3-54aa-a23e-c1806eb4e8b1 | textbox | KPA
7e3026d1-cb36-5e46-a3d8-71f74d9966e4 | textbox | Ambient Temp
1db68e0e-305e-4a72-8578-184e644487f4 | checkpoint | 2nd Reading
7aac49c6-3697-5f29-920b-c2cfcb66a134 | textbox | Time
17cf8cf7-91e0-5c2a-aa9d-b1968aff517d | textbox | KPA
0e04f901-2e9d-5405-b004-13acc5485ff6 | textbox | Ambient Temp
4d945158-7f06-4035-834a-74b9dd309245 | checkpoint | Test Result - Passed?
bb03721c-0947-5f9e-86a7-ac7a30a2f0af | textbox | Repeat
3cde0c62-5751-4e31-96dc-538397fe3260 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
67bcc90f-3b57-5172-9c10-ac0cb0b3e201 | button | Geschke Group Signature Sign-Off added below | Yes,No
eaf25597-4993-5a3f-be33-08c6b15f4d36 | button | Builder Representative Sign-Off added below | Yes,No
cb302e15-782f-445f-a83e-4b0e3c1653c1 | checklist | QA 7 - Commissioning Test Report |  | QA 7 - Commissioning Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8accb0d0-d454-4154-8984-85cbd39c602c | checkpoint | Commissioning Test Report:
efc3833a-ae0d-5262-93c5-7bb9bdd62a0a | textbox | Zone/Grid:
f6dff740-c0a2-5c0c-9614-42f68e0f4e71 | textbox | Drawing No.:
36b4601e-7795-5192-b24d-f1147a13f18d | textbox | Rev.:
4674feb2-eca5-46d0-9615-eefb0d6246c4 | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
4cf2de1b-f7d3-59b0-93ba-d6ee3376f6c6 | note | Test:
b19b79ec-855c-5784-b6f0-eb319cb7b9aa | note | Performance Test CL 2.20
c0908ee4-8516-535c-91ab-2ef44f1e5226 | note | Fill fixture with water remove plug
3a7a4ad8-a4db-5c82-b30b-aeb33e155329 | note | Test for:
8b62b452-0cad-5e37-97f9-5e51aecc90cf | note | Leaks
40ca50d8-731e-5f6b-850b-087b2d8da07d | note | Loss of water
e3e2fc57-735f-523b-bc34-1930c043b1cf | note | Seal in Trap
53257ab9-73ad-5d6b-8850-2c0eead852a5 | note | Induce siphonage in trap of adjacent fixture
927e9c89-e5b7-50ca-81ec-3ce9b724d3a0 | note | Complete draining of fixture
f2f983a0-e235-5396-8cbf-03ec9b7bbc07 | textbox | OK:
438787a0-a183-56a0-a828-3b7d7af8cf79 | textbox | Not OK:
b0535e97-74a2-498f-8c77-91e0ba01dc04 | checkpoint | Item: Water Supply
d715b920-1f41-59dc-93b0-e08300c12cbb | note | Test:
dde2e34f-0e49-542f-b816-337e0d0ee190 | note | Performance Test CL 2.20
0841f1bf-c30a-5ec7-b50e-cb701d223b0a | note | Check for adequate water volume.
92364d40-01f0-5bab-900b-dfdc8b59a2bb | note | Flush out pipework
3e4b9afe-ab73-5c08-836f-b1d6e9723cc2 | note | Clean aerator
4f95e074-797d-58b1-ae8c-ab20be9f4b14 | note | Water hammer
7c95dffc-adce-5c8d-8752-fec6c27b6192 | textbox | OK:
bb7afb3c-2c14-531e-b58a-68362ccba9cd | textbox | Not OK:
279dac45-d9d8-4f06-8ccf-04246675d87f | checkpoint | Item: Flush Performance
8ef2573e-bc86-5078-ab7b-cf5f01315e86 | note | Test:
bcafbee1-d46a-5f0e-951b-1469b400878e | note | Performance Test
8d79f26f-b3cf-51ed-9dbf-3bf6b30d9d93 | note | Check for:
14022ee4-c70a-5c55-b4a6-38b659e6d1cb | note | Water Volume
d8468de0-78c4-540a-93db-6c10cfa535d0 | note | Duration of flush
4d0a8f3a-c4a1-5ecb-ab4b-778d8fdb5ad1 | note | Flush out pipework
27065f43-6ad7-5785-a3b4-9cb8dc4bed2e | note | Water hammer
4a3b3620-9e6f-5c96-af3d-7caa26c28f5d | textbox | OK:
d7a07a31-f775-5b87-b6b2-f74915f83352 | textbox | Not OK:
28a5bc78-9d98-44eb-b442-3dec937b6988 | checkpoint | Other
d8cfa2cb-5492-430f-88e2-0fe41831c8c1 | checklist | QA 8.1A - Below Ground Sewer Checklist |  | QA 8.1A - Below Ground Sewer Checklist
9834878c-7990-4134-b008-ee1375dc4a7a | section | Details
4e0d7bba-99ef-4bf3-a75d-d57f49630b92 | checkpoint | Principal Contractor Permits Issued
c29e05a2-2371-4043-8a88-683ff85f4225 | checkpoint | Set out pits, trench depths and runs.
ccbee870-2504-5d17-8cb8-d28a3db00dc8 | textbox | Drawing & Revision #
51f96e6a-b657-5dac-9dd9-e7451c0d4614 | textbox | Survey setout completed by:
58e42ecb-cb0a-5220-8f7b-c2ad7bb44672 | textbox | Starting IL established - enter IL
4e4ba7db-80ca-4448-92d2-776577150c29 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
2442ed04-371d-5957-b382-e4a8da16e426 | note | Spec#: AS3500 and Hydraulic Specification
3fea3018-35e1-5aea-b693-5b9fd6fb4897 | textbox | Materials used:
6484da01-8574-501f-9c8d-1fab7b9c2362 | button | Approved by Principal | Yes,No
3ee51f1b-8a0f-441a-9aea-5a8238fbb292 | checkpoint | Bedding material, placement and compaction meets specification.
6d07f887-d242-5115-b7ad-3dd8b9c4c190 | note | Spec#: AS3500 and Hydraulic Specification
524242a7-14dd-5465-aa1f-bad10affa201 | textbox | Material used:
08e6de0b-6c49-4c68-b92e-ba0136e2a752 | checkpoint | Laying and jointing of pipes - RL and fall
5a7dc8e1-5a7f-58d8-bcb5-b68a71cce16a | textbox | Jointing Type:
fb883bcc-113d-57e0-8d33-4e3fccd9c340 | textbox | Fall:
aae69d73-a339-5cb6-a7fc-866d3913fee0 | textbox | AS3500
e5ad54f2-b12d-5179-9967-70efe2d88e36 | textbox | RL's as installed
d04058a4-2931-4f6b-a16a-85cad18f3005 | checkpoint | Connections to pits and existing services as per Hydraulic Specification and Australian Standards
b16c6697-de57-4e14-b0c0-787c3fc90065 | checkpoint | Check of each inlet
d27aa7e3-fbfe-52e4-bc39-0da1cbe27c76 | textbox | Comments
eebb7540-d599-4998-b19f-b9fa0a57e2dc | checkpoint | Service run was inspected prior being covered
d186015f-0f33-5914-b200-c79c87469da0 | button | Geschke Group Signature Sign-Off added below | Yes,No
94f97ed5-c615-4570-a9dc-1f7db58fd66a | checkpoint | Hydrostatic tests are carried out as required.
625d9efe-5359-59d4-aa66-20fc8016a5a5 | button | Air or Water? | Water,Air
3b213bcf-205a-559a-903a-a80dde50ca5b | button | Inspected and recorded by Independent Certifier or PIC | Yes,N/A, No
cc04657c-1ab6-59be-86e8-87a8da3e6365 | textbox | Geschke - Initial/Date
8c0d2a99-c3db-5d25-94da-4c584b16db29 | textbox | Principal- Initial/Date
213365b9-7331-4646-9cde-0ffad4961c71 | checkpoint | Placement and compaction of backfill and material meets spec
480bef5c-cf8d-5531-89ac-18d605394787 | textbox | Material used:
d6fe4541-76d1-4637-964e-8f63521b70f3 | checkpoint | Temporary cover provided to open drain.
df043a76-ecb7-4406-8392-16f68ff61c0f | checkpoint | PVC/ Plastic caps to open ends
fc4fd624-0646-4926-b9d4-84a40c854b93 | checkpoint | As built information updated onto drawings
f6480fa7-2fb9-51cf-aef4-ff90c7782e12 | button | Drain installed as per nominated drawing | Yes,No
880a3b44-f3ad-5380-b78b-4b7eced6c33b | textbox | Comments
e5058353-1adc-4ded-a696-3109e336ed65 | checkpoint | Invert levels checked by a surveyor
125a1dbe-fe98-5010-aa21-f948ec5a8870 | note | As Built drawings to be updated as required
6823f074-7667-4c11-8061-fe0dba78f3b7 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
101777da-5639-56bd-abfe-8ffd8a448c49 | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
ab3ed195-c8a9-5609-8ef2-035a504bf91c | note | Company: Geschke Group
13879ea4-d686-5774-a2fd-261352f44696 | note | Phone: 03 9798 1619
20d7cb01-c2b7-5830-9a46-c6cf158d4b12 | note | Address: 45 Pacific Drive, Keysborough
4914f7bb-447f-4be1-8242-3097b562fb91 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
38d28082-e999-5aea-b515-42db9e36eb6e | button | Geschke Group Signature Sign-Off added below | Yes,No
89f4c6b6-d178-5412-bd6a-256ce5e1ce30 | button | Principal Sign-Off added below | Yes,No
73a31ef4-5dc9-4e31-960b-93d60599288c | checklist | QA 8.1C - Below Ground Pipework Checklist - Fire |  | QA 8.1C - Below Ground Pipework Checklist - Fire
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
128b7f20-4a6f-45c1-9d1e-862cca96ed02 | checkpoint | Principal Contractor Permits Issued
d3aba9a9-b362-4f6d-a5a6-7012fb71e7df | checkpoint | Set out trench depths and runs.
e0fd542f-fa02-5f5e-92ca-45396f3e02fc | note | Project drawing #
338af92b-aa00-5c69-a589-c4d7b78eb0a7 | note | Shop drawing #
37f7372e-1a11-4736-af05-b411264be717 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
3412a987-d484-5b9d-80e5-2c2ad721f5e1 | note | Spec#: AS3500
6f07dd7f-8a83-5702-b219-8b1b87f0ece8 | textbox | Material used
9f947c34-a3ae-5b42-a45f-4c902c0c3371 | button | Approved by Principal | Yes,No
72fca32b-75f8-4827-84f1-53637e8384fa | checkpoint | Bedding placement and compaction and material meets specification.
9c7a35b3-70d3-5bd9-81b3-b02e4715ade4 | note | Spec#: AS3500 and Hydraulic Specification
5854a3b3-4ffc-565d-a7d7-20a7c117da34 | textbox | Geschke - Initial/Date
234b9d38-3e91-51e3-8822-b4895758d0b2 | textbox | Comments
95d7be4c-db8c-4538-be0c-60eeb2787c30 | checkpoint | Jointing of pipes
649ac991-5af4-5908-a71c-42a8fe64c52c | textbox | Jointing type
9ffc8239-c15a-5b72-9a34-88627f29aa1f | textbox | Attach welding checklist if applicable
b2bbd2d8-3f1b-5de3-86fc-221d9bc5f063 | textbox | Geschke - Initial/Date
85cd78e2-9467-5267-9cd0-a9d03feae12a | textbox | Comments
99f6e450-3e6a-454b-807e-f63ed5964e66 | checkpoint | Hydrostatic tests are carried out as required.
0f99d5a4-8391-5d78-a7c1-e1d2e9195ac4 | button | GPL QA6 form completed | Yes,No
4342a18b-8989-52b7-84d5-4d84f253f583 | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
0d9f0dbc-7d44-4f22-9fb2-73d77ca91407 | checkpoint | Placement and compaction of backfill and material meets spec.
e8b77972-ce0e-52ab-9bcc-92e249e90f54 | button | Compacted backfill as per the Specification | Yes, no
0440cabe-3f1a-523c-80df-012600fc763e | note | Detectable marker tape
b2886a5a-daca-4a17-a58d-99ff711c474f | checkpoint | PVC/ Plastic caps to open ends
230a2477-5fde-4536-9478-83543b700ad1 | checkpoint | As built information updated onto drawings
65543917-92ac-529c-9096-4f7e61ebb92f | note | To be provided
3a0984af-59bd-410a-a0f4-be5a9a6a7157 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
912fd122-9fef-5af4-b3bf-d2142fac68c6 | button | Geschke Group Signature Sign-Off added below | Yes,No
47a73626-cde7-5e66-91d8-e921d6790031 | button | Builder Representative Sign-Off added below | Yes,No
9462cde6-3aa3-46cc-a519-0711f8a08c94 | checklist | QA 8.1D - Below Ground Pipework Checklist - Water |  | QA 8.1D - Below Ground Pipework Checklist - Water
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
9806b5b8-355c-4497-8435-ec3f6a7a72be | checkpoint | Principal Contractor Permits Issued
bc4959f2-2390-4ecd-ad5f-f02232076068 | checkpoint | Set out trench depths and runs.
2241d060-b5e6-54bd-92ac-d7204999798d | textbox | Project drawing #
6f08af97-a7e6-5ec2-b9e9-ba0d5f97fe82 | textbox | Shop drawing #
ac143929-0ab8-57d9-81ad-091f083b655b | textbox | Depth of the installed run
4e1d2412-b3ff-42a3-834b-de0f887ddf4d | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
78c6479e-b2ab-55eb-80ba-352228e43446 | note | Spec#: AS3500
d6f90071-9289-5584-800a-9935b7f3b6ed | textbox | Material used
e9b55c11-47a0-500a-979b-d4f3de665c9f | button | Approved by Principal | Yes,No
3924b42e-bdba-4ee0-a753-9d815345caf3 | checkpoint | Bedding placement and compaction and material meets specification.
1a1cbd12-1f17-5dcd-967a-948fff745863 | note | Spec#: AS3500 and Hydraulic Specification
02ada611-f2ec-5bfc-b0ae-f05f79d4efee | textbox | Geschke - Initial/Date
7aa74f42-280b-5ac3-a6e2-fbf963a33cb9 | textbox | Comments
9333d361-f506-4f18-a9ae-d8e38165f460 | checkpoint | Jointing of pipes
9db256ae-fcd2-5eed-848c-f87a1c9b0f3a | textbox | Jointing type
9c65737e-56e2-520f-87e7-c94ea95fc944 | textbox | Attach welding checklist if applicable
28a57a85-1307-5ab5-b3e4-b5620fadf5db | textbox | Geschke - Initial/Date
da88d218-7790-5f36-8546-7c15241920d0 | textbox | Comments
cfbd897e-b45d-40bf-a405-6d1fb595eb21 | checkpoint | Hydrostatic tests are carried out as required.
7c3711ed-66cf-556d-8178-cd03b9762079 | button | GPL QA6 form completed | Yes,No
5b181ec5-1781-560c-a053-9567ba00d0e2 | textbox | Water system tested to (kPa)
5d18f4be-875c-4174-970a-361223815788 | checkpoint | Placement and compaction of backfill and material meets spec.
4577d416-0a29-55e3-a085-01b3fd80990e | button | Compacted backfill as per the Specification | Yes, no
3b21e745-f694-54e6-bc71-d80980843cb6 | note | Detectable marker tape
a7fc24bb-01ae-4d08-a931-241ad8716dd2 | checkpoint | PVC/ Plastic caps to open ends
4679b6f3-cabb-4275-b707-0f3ba28e3fbe | checkpoint | As built information updated onto drawings
dc82f58a-c987-5e3e-ba2e-d821a9093208 | note | To be provided
84914eba-0278-4c20-8c62-4dcad726b748 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
00a6e7b7-b0df-577d-8527-aee76cbf61b6 | button | Geschke Group Signature Sign-Off added below | Yes,No
9694bddd-0b32-5f9c-af1f-b2d1ea86c880 | button | Builder Representative Sign-Off added below | Yes,No
501f8fbb-16d8-45ef-84d2-f8ef45bb05ea | checklist | QA 8.1E - Below Ground Pipework Checklist - Gas |  | QA 8.1E - Below Ground Pipework Checklist - Gas
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
67904dc5-9f8d-4d4d-8812-345970aa5452 | checkpoint | Principal Contractor Permits Issued
f5f1f896-30e9-4cc5-87d5-35ff84db6cfa | checkpoint | Set out trench depths and runs.
accb70db-e38d-595a-9d82-5a39fc83f18e | textbox | Project drawing #
c8d50271-a74d-5d6e-aa29-92bacf1050a6 | textbox | Shop drawing #
4e75980c-f49c-5ad9-a884-be63a5aff02d | textbox | Depth of the installed run
f82ccaf5-b287-4382-8af9-641839bf1e9f | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
d01e68f5-059e-5eec-b68b-5af07b3f3506 | note | Spec#:
59c172b3-1436-5b9b-8ac4-fc68ab004bd9 | textbox | Material used
029fe666-dfbc-5001-a818-f328c5289819 | button | Approved by Principal | Yes,No
0bea316c-e6e1-4a5c-be2b-5a89da5c920d | checkpoint | Bedding placement and compaction and material meets specification.
44e62258-bc1e-59b9-a051-bc89e5c47926 | note | Spec#: AS3500 and Hydraulic Specification
3677c8d6-2ae3-5b2a-a335-d6fe0adb5f2d | textbox | Geschke - Initial/Date
9cd53d26-9751-59af-aaa3-5a8a33a8d87e | textbox | Comments
5832027b-7d00-4102-8888-0e12edecb88c | checkpoint | Jointing of pipes
0e412bc1-81a6-549d-9d7d-0563e0c5e74f | textbox | Jointing type
e993445a-b023-56f5-9daa-843a02162646 | textbox | Attach welding checklist if applicable
f911e6c4-13c0-534c-9460-82b41ebb5f88 | textbox | Geschke - Initial/Date
225a7a68-ba18-53eb-ba4e-378541c107c6 | textbox | Comments
c42f8d13-50ab-468b-8c4d-b61d86a14bab | checkpoint | Hydrostatic tests are carried out as required.
c906a2b8-b73a-505e-afce-91c8f80b2193 | button | GPL QA6 form completed | Yes,No
10c5a596-f612-5a4e-96f1-fadf65633a4c | textbox | System tested to (kPa)
35788cc0-d9d8-446c-acdc-4c8a08e9c2a4 | checkpoint | Placement and compaction of backfill and material meets spec.
01dcf767-88de-5095-9248-032bd9c3173f | button | Compacted backfill as per the Specification | Yes, no
e95d5d99-257a-542b-ae8e-01f0fc13d1e6 | note | Detectable marker tape
0fa3b1d2-06a2-4d62-9578-2b6674e8a747 | checkpoint | PVC/ Plastic caps to open ends
bd083f3a-cbf0-48c6-838d-c4bbd4a22355 | checkpoint | As built information updated onto drawings
94361265-02e3-5c39-a47b-1552ef23c27b | note | To be provided
575c1116-0ef7-4865-8b6d-7a24bc6810c4 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
70fc28de-4fb8-5bc5-b308-bed48792e135 | button | Geschke Group Signature Sign-Off added below | Yes,No
745aba14-a7ea-5c02-91e5-de6f45075291 | button | Builder Representative Sign-Off added below | Yes,No
4fc9182a-7d08-4af5-9e6e-4a87800bafbc | checklist | QA 8.1F - Installation of Stormwater Pit Checklist |  | QA 8.1F - Installation of Stormwater Pit Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b69c9169-2356-4289-949f-38f782f02907 | checkpoint | Stormwater Pit Installation Report Details:
71bf98c3-973d-55f6-af0d-09d4d17157f5 | textbox | Pit Number:
198255aa-050b-5c0a-acff-db64f9df2a04 | textbox | Pit Type:
1e9ec891-49fd-5953-aa74-6a4d24278003 | textbox | Project Specification:
573ad9b4-b93f-57cb-9b66-7d53276845b3 | textbox | Drawing & Revision no.:
cf8f4a1a-1653-570a-a3f7-14e58023650d | textbox | Shop Drawings no:
5a21a85b-eed9-5e19-895e-22102054cf8b | textbox | RL of the bottom of the pit
e1e58eea-7b22-4894-9f62-48225b885a71 | checkpoint | Bedding material, placement and compaction meets specification.
77855798-082c-56c9-9ef2-c5e73cb6aaf3 | textbox | Spec#:
643f7e07-dc59-5329-bbad-2f9219739aa9 | textbox | Material used:
4a8b6a05-5834-4dc0-8de3-4328f5676cc2 | checkpoint | Pit installation
75efd2f0-5141-5cb9-bf9e-78a7082e566b | textbox | Date Installed:
cde5f1d6-4853-5b07-be07-f7fc71b761e6 | textbox | Pit Base:
de70aa3b-0975-5a64-ae53-97be425ba661 | textbox | Step Irons - GPL Initial/Date:
87746f0a-a135-542c-9ae4-53c6a80c8ea1 | textbox | Outlet IL
d239fdce-bdfd-5f6f-827d-8027364e95fe | button | Placement of cover | Yes, No
9691c132-3215-573c-bbf3-98c678e74b2e | button | Concreting of cover | Yes,No
ae1db28d-dd38-4a7a-9036-6e0855602cd7 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
aea54829-443b-52c6-91ba-d783b71f0296 | button | Geschke Group Signature Sign-Off added below | Yes,No
74e36e24-95ee-59ab-9c7c-8675afc18a51 | button | Builder Representative Sign-Off added below | Yes,No
b58f0ba1-1093-467e-a13b-7998cef4d2a4 | checkpoint | Backfill
cf6ffe5b-d40c-5568-b728-aa742f526814 | textbox | Spec#: Project Specification
f30313bb-c7d3-5f7c-8689-76a3bdbaf4e8 | textbox | Material used:
6ad69f6a-ef8c-4fea-b714-5a37508fc3a6 | checkpoint | Hand-over Photos
46d9bde7-ff68-4fa9-a519-3e782a7c7b1c | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
89efc61d-4dc7-5aa8-8109-07c8188b5851 | button | Geschke Group Signature Sign-Off added below | Yes,No
6c778669-22ac-5b41-bee7-98c74cfaed58 | button | Builder Group Signature Sign-Off added below | Yes,No
83f6c67f-7f34-4c93-824c-81730d3bc6f8 | checklist | QA 8.1G - Sewer Rising Main (Poly) |  | QA 8.1G - Sewer Rising Main (Poly)
f7b45724-2b34-4cea-b097-bc6a6b74de68 | section | Details
bfade36a-dca8-402f-8abe-0b2d2113c576 | checkpoint | Principal Contractor Permits Issued
98aea581-4c4e-4af5-930f-289789408a8e | checkpoint | Set out trench depths and runs.
d1db984d-a86e-5ebe-abff-2dc386abe56f | textbox | Project drawing #
7346c5d5-2b5d-575b-bc74-aa36000fcd13 | textbox | Shop drawing #
7e123f0a-c5e3-56a7-850c-d5d67dbdbbd6 | textbox | Depth of the installed run
0b52183a-d0b1-464f-acc2-5bd39c45bc23 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
c265d1b8-2b5a-5c13-9841-a5a81fd04d44 | note | Spec#: AS3500
ea3d92d3-1502-5b02-936a-e91cba7aa35c | textbox | Material used
a024f5ac-9ff2-528d-9544-026c0a857097 | button | Approved by Principal | Yes,No
b69e7be8-bdaf-406f-acbc-6efef92c5dae | checkpoint | Bedding placement and compaction and material meets specification.
d731decd-edd8-5ce6-a187-087a97f77b5d | note | Spec#: AS3500 and Hydraulic Specification
c5a3fe86-cf09-588a-8d4b-1fe941ddf0c0 | textbox | Geschke - Initial/Date
d46cc08e-f551-51ff-bb40-5ef091978678 | textbox | Comments
8673a3cf-8cf6-4a14-b5e7-25ac91c28567 | checkpoint | Jointing of pipes
80ccc614-3d1e-5a9f-93c4-c25237f9f3a2 | textbox | Jointing type
662daa23-cdc7-5fb3-b381-206c5a963ad6 | textbox | Attach welding checklist if applicable
e9f56a3e-fdf4-51b3-95a8-7d1cad5d0629 | textbox | Geschke - Initial/Date
a0e446b1-357c-5d2a-8a7f-aabd13fa81f0 | textbox | Comments
78605ecb-f8af-4d6a-90fa-49abedd86e0a | checkpoint | Hydrostatic tests are carried out as required.
d161ee79-037e-5a90-a440-7db1f8fb1895 | button | GPL QA6 form completed | Yes,No
51d0e46b-9e9b-5c23-ab3b-1e8e0ecce948 | textbox | Pipeline tested to (kPa)
799eba80-8659-4438-9de0-3a3dc2039a2e | checkpoint | Placement and compaction of backfill and material meets spec.
2880c1ff-e88e-5eec-8fd7-bf4ad3bc37e4 | button | Compacted backfill as per the Specification | Yes, no
f5942bd3-2ce5-5ef1-876d-3e395360f7c4 | note | Detectable marker tape
8758eae2-01c5-468a-a404-4eb398f8b4a7 | checkpoint | PVC/ Plastic caps to open ends
266cbfe6-4dbd-4cfe-bb42-42e94b2e0019 | checkpoint | As built information updated onto drawings
80399636-3e7f-5eac-b5a2-94e9bfb66693 | note | To be provided
ccd50f4c-8838-43ad-af97-add729378155 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
2a100402-2396-529a-9afb-602ec5a19c78 | button | Geschke Group Signature Sign-Off added below | Yes,No
9ac518c1-4d69-5f02-a25b-c52d16da9f29 | button | Builder Representative Sign-Off added below | Yes,No
31952566-8e8f-42f2-8261-802a50e4f548 | checklist | QA 13 - Backflow Prevention Device Test Report |  | QA 13 - Backflow Prevention Device Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
35d9e5a0-189b-4339-92fa-9cf57104c56c | checkpoint | Backflow Prevention Device Test Report Details:
96b1c0aa-e254-5ff0-8d45-42a9ede8de22 | textbox | Owner/Occupier:
5a6e0fd3-2ab2-5281-b8e3-a9a7880faca6 | textbox | Address:
3cc76b09-5d8f-5fb0-a60b-258a72eb766b | note | Licence: 50043
979d0e12-469f-53a6-9e44-13d4de364caa | button | Type of Test: | Annual Test, Installation Test
888d3098-1f8a-5393-a0e2-48a94c00c8e8 | textbox | Location of Device:
fc81ca53-0430-5d85-a355-f08c0b56f09a | textbox | Authorized Tester Name:
c824c6aa-5d6b-563f-aa52-e44d2356c0b6 | textbox | Test Kit Serial No.
1546a59b-442d-5471-926b-148678f7ceb5 | textbox | Tester Licence No.:
06269562-4753-5b8b-94dd-b16ae90601a6 | textbox | Test Kit Calibration Date:
4aa9860d-ebee-52f5-bf25-b196c4b629e9 | textbox | Date of Test:
ba6df11e-0b1c-4acb-8b9b-feba98b56755 | checkpoint | Device Details and Test Results
6832ebeb-6392-56ea-a76f-018442f15868 | button | Permission to Isolate Water Supply | No,Yes
02c8df33-061f-567e-a962-8f79d923e715 | note | Device:
4ca558c6-d976-528d-9924-6d6765e92cd6 | textbox | Make:
9d4404ec-f04d-5d3a-8985-83370d242259 | textbox | Size:
2cb1e1bf-4abc-5ecb-8df7-0f6f51efec3a | textbox | Model No.:
a87cc625-5ea2-5561-bbef-746e7efd40fe | textbox | Serial No.:
d60e427d-f242-544f-bcbc-a2e6313874ec | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
35d0455a-b07c-5e97-9fd9-bc0d7eccf303 | tickbox | Containment Protection
6d36091d-daa8-5587-a1ee-fe054fe1b516 | tickbox | Individual Protection
8d1d2355-27cb-50dc-9d14-393f6a6cff42 | tickbox | Zone Protection
62c574d2-3042-5092-8593-ed8241f90522 | button | Strainer Installed | No,Yes
d3ea971f-6f75-5f65-bc75-f846fbcbeb30 | button | Strainer Cleaned | No,Yes
bdf68c4c-bde7-5a78-a575-73ea754404a2 | button | Device Type | Double Check Valve, RPZD (Reduced Pressure Zone Device)
7291ec27-dfd1-5048-8a1d-b57cd2f6c026 | note | Valve
3825f4d7-786f-5605-adc2-9e3d007b1be4 | textbox | Check Valve 1
2471a3fd-287d-5d6b-a8bc-e81ed77cf35a | textbox | Check Valve 2
fd736bc1-76d7-507d-91bd-6f4e1e27b3aa | textbox | Relief Valve
577b9952-a5e4-5415-be06-e7dc96dac09c | note | Testing Results
b551e3fd-2d8d-5fa3-9ba8-a0b3a527a2a4 | textbox | Close tight at:
97f1ef3d-8469-5da8-b657-a1c66fee3130 | tickbox | Leaked
4350c276-5d0a-5f78-9a65-22fe8a825706 | textbox | Close tight at:
817e0391-a28c-5c65-9a6e-6bb710c1a374 | tickbox | Leaked
83248f70-a0a1-57da-b065-cd50818ca652 | textbox | Opened at:
c52ace03-d687-58f1-9240-deb05de74ceb | tickbox | Leaked
1d1772b4-8769-566c-b013-96e0cadb5637 | note | Reason for the device failure
505f51ce-c2c7-587e-8f58-5649673c249c | tickbox | Incorrect position
7d7bd471-2366-5f5e-8c2a-a0619ac33e27 | tickbox | Incorrect installation
fd4bbf85-17d6-5731-bd74-91fdb75196d9 | tickbox | Foreign material in the device
3f2222ff-9b83-5c8d-b0bc-03bd432c5eb7 | tickbox | Spring wear damage
1f6d240b-c747-55fd-8d5c-7e09f6cf3693 | tickbox | Seal or Rubber Damage
622cca24-5364-5550-8e8d-073e1a2bb2d5 | tickbox | Other
d4212740-b9e1-5f24-82d3-0f04da5fe6c7 | textbox | Other:
59706c0f-aa20-589e-8554-f1e160e05da0 | note | Test after maintenance
fa48cb65-a758-5272-b5d0-5409656c761e | textbox | Close tight at:
08949006-f6a5-58d7-9817-45cca2610732 | tickbox | Leaked
d72da8d4-ef1a-564b-970b-72bccba7f43a | textbox | Close tight at:
0b84c6ea-f7b0-57d5-a9e3-d5f41de6cdfb | tickbox | Leaked
2906b79c-3d7a-510c-a5da-4df4ff332c8e | textbox | Opened at:
7c2dd43b-e210-5b52-ad15-4a306b6f44da | tickbox | Leaked
f90d9531-5b61-5427-87de-fc90d3585e9f | button | Water turned back on | Yes, No
54a06593-7bac-5c09-a5b0-820ddc33af4b | textbox | Describe the maintenance:
8fd370f9-eb15-548b-92ed-8dc6fd03dc7e | textbox | Parts used in repair:
82b22a25-18e7-5da1-be20-1f03766ea74c | button | Is the device installed correctly | Yes, No
b50ac0f3-c7c3-476d-8792-7704a245ec60 | checkpoint | Test Result
5d101c94-73dc-5744-86a1-77dd84e66960 | textbox | Tester Name:
954850d9-e42f-576b-8071-627ef7644bfe | textbox | Date:
dbc8e51f-2814-4a0a-85dc-25b0eb9583c2 | signoff | Add Signature
beefd4de-6e64-4bf1-b486-38c244ca3c77 | checklist | QA 18 - Gasket Installation |  | QA 18 - Gasket Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6dcb2c4e-0164-4a13-9d71-89bf1514c2d7 | checkpoint | Gasket Installation:
d4105ed9-6a37-50d5-8dfd-a5620f210dd5 | textbox | Location/Identification:
d7d7ed3e-0630-52b4-b2f1-9b5e3e4b297d | textbox | Nominal Bolt Size:
47f7804f-cfbb-54ab-9019-d52564852d03 | textbox | Gasket Contact Surface Finish on Flange:
52f05d3d-488c-5b41-96de-430c41ca4c66 | textbox | Lubricant used:
7ce6fe87-35b9-5e75-b2ce-d302985daa14 | note | 1. Galvanised nuts and bolts must use good quality lubricating oil on threads
59a2ebf9-25f0-5cd0-86d6-4445d49a0c1b | note | 2. Below Ground Galvanised nuts and bolts must denzo and plastic wrap full flange and cover bolts
5bd6b1b3-3f94-5d37-8cac-3c2625ac9d3c | note | 3. Stainless steel nuts and bolts must use anti seize / molybond on threads must return 24 hrs later to tighten in sequence and required torque
4d198ce0-b986-56b7-9569-c6704e4c2c57 | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
14464e69-fad6-5881-b9f5-62016fcf0ffa | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
fece4d59-dc76-51b7-9f5a-77683d56a351 | note | 6. Zinc bolts, nuts and washers rust when used externally use galvanised
0d5cccbf-b218-4247-9f02-83857375ecbf | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
5a775aec-674e-4053-ae3d-8a530629c0ea | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
911d7a43-751c-4ba0-b9b0-c16ee0bbe7d1 | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
0f2c4ea4-3123-47f4-8b2a-aa062ee10ea3 | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
1ab2e245-842e-4ce2-b744-31ab4ec477de | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier seek from GPL foreman
c48863f9-0a08-4120-b572-272f9ac51445 | checkpoint | Check gap for uniformity.
f870c048-9395-4208-8471-dada9fc05a90 | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a Round)
e72da9e0-43ba-467b-8e96-687389d81552 | checkpoint | Final Torque
72db60ac-dc4b-5049-bf06-7ed396e98ab9 | textbox | Final torque*:
9e8ce929-1125-5b67-93fc-9eaa473d2ddb | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
c180acb4-8bd3-56fb-bec1-b822d71dad34 | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
36c04912-f29c-5358-995d-95ca1b724b72 | textbox | Round 1 Tighten to:
e2e84b4b-ca95-5a68-ad90-83e2ca7b7f7c | textbox | Round 2 Tighten to:
b1541ea8-f183-5c74-9962-a10d2a67409f | textbox | Round 3 Tighten to:
272fc3a8-70c9-5f38-ba8b-2b917f49fa4f | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
a5e586b9-1754-5885-90f6-98a2ed355899 | note | Final Rotational Round 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
1c59865c-be9d-502a-8d3d-b5c6969fa81a | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
e1e1637c-257d-5760-9ccf-ed60c49c6bee | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
fd097811-1e85-53b5-b2d7-418085c3ac71 | textbox | Other:
6435bce0-d2a4-5b17-9877-e95d965b003e | textbox | Where was torque information provided from:
4dd57391-c132-5ab0-8c58-368e752dd079 | textbox | Joint Assembler Name:
75fb7c88-6074-40b0-933a-d405cb88b8d2 | signoff | Joint Assembler Signature
f5091ac2-b260-4bf1-b03f-a01974f47556 | checklist | QA 19 - Service Cross Connection Check List Report |  | QA 19 - Service Cross Connection Check List Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c2cf1cc9-913a-44ea-acef-8bf14592108b | checkpoint | Service Cross Connection Check List Report Details:
f6f4b105-7d9b-5e80-92f8-5c201c7396d0 | textbox | Zone/Grid:
e3f181aa-69e2-5f47-8816-ac860edcbb27 | textbox | Drawing No.:
db2f857e-a0b6-5729-98c6-3ca69209d364 | textbox | Rev:
0f5834b2-e125-4521-8b1f-eb09d29a9583 | checkpoint | Service to be tested
93be06fc-c9dd-5647-8bc1-473c1ef0551a | note | Isolation of potable supply in general.
c5249302-d117-4a5e-9bcd-9d1c8d2a9f01 | checkpoint | Potable Water Supply
ed8aac6c-7421-5b17-b558-419d2b42b4f1 | note | Confirmation of service isolation at all fixtures.
b1e67cce-5f94-505e-bc24-b9df35b8f63d | note | Keep potable water turned off.
3c4a566f-344f-47d2-a349-90a2850aa24f | checkpoint | Non Potable Supply
2c9f03e2-a10c-58d4-a7e0-28e4f44f721a | note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
f1aafd17-4c5c-48f7-b8ac-5e6e253baced | checkpoint | Turn potable back on
1530f8f9-c9a7-51e8-9d7b-00960fd7fb7e | note | Potable back on
a11e865c-b6ab-45be-88f7-07d125e12c9e | checkpoint | Non potable supply
e6246f4a-1d8c-5222-85db-4f93feae8e0d | note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
30f95acf-3893-426d-b45a-3ba7d698b734 | checkpoint | Potable Supply
01b741ae-74e7-54c1-975a-7aa68e26b829 | note | Check all fixtures that receive potable water are still getting potable water.
015aeb68-0f36-42a4-9d63-815285551c07 | checkpoint | Pipe Identification
1cb8ac20-cf9f-5501-8c83-f176cf4a6c1c | note | Confirm recycled water piping is identified by colour and noteling.
8bc8b3d5-b47d-4e55-bbf9-c5ac4bfc294c | checkpoint | Other
0b7566d7-1886-4dfb-8c27-c73cea416487 | checkpoint | Conducted by
5b4d328d-529f-5016-b908-7c62ed5e98f8 | textbox | Conducted by:
6f56f155-2dca-4254-a278-29c52b3f25fe | checklist | QA 30 Fixture / Hydraulic Installation |  | QA 30 - Fixture / Hydraulic Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ad526e80-1a80-4e61-9b25-8a1f28d101c5 | checkpoint | What is being installed?
2951b49f-3a2b-5a73-b658-850e92384faf | tickbox | WC
6cade55a-7035-5424-82b6-4920374d3a6f | tickbox | Shower
95429128-f0f5-50f5-9023-a6633047a7e1 | tickbox | Basin
8187d821-b98a-5177-a79f-5452c3f3821f | tickbox | Sink
76a94152-986e-530f-89f1-20eb1ba4da86 | tickbox | Tapware
3b518082-0d11-5811-a41e-2250fe79d6fd | tickbox | Boiling Water Unit
5da0448c-b97e-510d-9c82-7d4404d392a6 | tickbox | TMV Cover
c3be2d0e-7180-5e90-8c03-60b51be75dc1 | tickbox | RPZD Cover
f8febd78-17ed-5f5b-bcf3-a79405b1b94f | tickbox | Other (Specify Below)
a8558d30-ef55-568a-a8c6-2ba582d3b4b3 | textbox | Other (Specify Below)
baab9379-2e72-41de-abb1-3a02c88f1e66 | checkpoint | Where is this fixture being installed?
8683a909-612d-507f-9fe3-614092076043 | textbox | Location
9c0ec576-fbc2-4683-b773-901a9a007949 | checkpoint | Have all parts been connected/completed and tested? - Pass = Yes / Fail = No (Detail why below)
2a6132c1-6c26-4257-b70a-44f675886ac0 | checkpoint | Photos of installation been taken and uploaded below
8cf8f4fc-e309-4546-ae37-42620ca733a1 | checklist | QA 32 - Water Services Flushing |  | QA 32 - Water Main Flushing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b406ecac-eb71-45f9-bcbd-8f63bdc8c988 | checkpoint | Water Services Flushing Details:
9842b7a2-1295-553d-a082-91206a628b0e | textbox | Zone/Pod No's:
e477d733-13fe-5c37-892d-c685b2a89708 | tickbox | Mains
737f5b85-bf2f-55e7-8369-b2beea621dde | tickbox | Cold Water
77c87980-3864-590f-bfc0-8aee9bf81f24 | tickbox | Fire Hydrant
625077ad-c5f6-5138-951d-83a611dc75ac | tickbox | RW
9d47f6b9-5a10-4a3b-a47b-d653c84efe3e | checkpoint | As built information updated onto drawings
56bcc4d7-ba64-58fc-bf9b-c49fe10bfaa5 | note | Ongoing
da10cb8c-e3a9-5fc8-93ed-d48d1e94a261 | note | To be provided
0c67a9a5-e298-4496-8f11-d8c1c159bfb2 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
490898a2-01fa-54ab-9b06-6abc43696181 | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
dfa8e955-6382-599c-8a89-720e88356d09 | note | Company: Geschke Group
b28c0394-b459-560e-96b8-6507d0d764f0 | note | Phone: 03 9798 1619
f33b082e-8614-5d81-83a8-c51e68634a98 | note | Address: 45 Pacific Drive, Keysborough
274f3aff-a35f-4bb9-ae28-a30c4976806e | checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
edba0088-6157-578e-a8dd-6c73d0d7f7b3 | button | Geschke Group Supervisor Sign-Off added below | Yes, No
a130aa6d-ee27-5c04-984f-0e1b7e8a608c | button | Principal Contractor Representative Sign-Off added below | Yes, No
53af1dda-d736-47c4-b355-92fc714c7b65 | checklist | QA 33- Installation of in-ground tank |  | QA 33 - Installation of in-ground tank
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
60ecafa6-81ff-46b9-b2ed-be18f3988a8b | checkpoint | Tank Installation Report Details:
7944efbe-02c2-5735-91d3-504baa0972c4 | textbox | Number / Name:
31490dfd-48a3-577b-a570-2ba5f0024f86 | textbox | Tank Type:
fac19df3-229d-53f4-a881-35f8afe2aefe | textbox | Drawing & Revision no.:
1848a99e-541c-5326-9ff1-429502d63915 | textbox | Shop Drawings no:
48f8da4d-e340-4da7-a7e2-484ef5304273 | checkpoint | Bedding material, placement and compaction meets specification.
cfedc526-7e87-58b6-abc1-d3e2274f76d9 | textbox | Material used:
2fb35dba-9b52-4597-b827-8fc05a1c257a | checkpoint | Tank installation
b631ed56-8875-5a2f-8b43-cb65c6b6053e | textbox | Date Installed:
b0c2ef2b-58be-522f-a364-7e97a2a73053 | textbox | Pit Base:
54e9c251-b2a3-587c-8be6-36514d1358aa | textbox | Inlet IL
5c0f6aa8-595a-50fe-a4c4-2046f7589189 | textbox | Outlet IL
e4066a70-3db3-44d6-aea8-22b0f7f66a12 | checkpoint | Backfill
80e164b9-82a0-50f6-b508-6414778fddfd | textbox | Material used:
9798c08d-7da5-489c-861c-5cc8c7edf56c | checkpoint | Hand-over Photos
2e652d09-7126-438b-ba33-3f9f66dd75d8 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
1175579e-a7a1-5cfe-90e9-83109fe0cee8 | button | Geschke Group Signature Sign-Off added below | Yes,No
9c19909c-7dde-5b01-8026-820819ea12ee | button | Builder Group Signature Sign-Off added below | Yes,No
a833642d-91f4-4a24-ad52-ec2d64da7dec | checklist | QA4 - Installation Test Sheet (Waste, Vent, Downpipes etc) |  | QA 4 - Installation Test Sheet (Waste, Vent, Downpipes etc.)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
00e0a804-b26b-42d0-83d7-2e3a49cfafd6 | checkpoint | Installation Test Sheet:
d5c412aa-7bbc-583f-8bc5-bf552b9c416c | textbox | Drawing No.:
b06f6599-6488-578c-be31-facb23efe474 | textbox | Rev.:
a4764bd3-75fc-4bbf-93ec-4cd4a44d67c6 | checkpoint | PIPE CLIP HANGERS
cf1ded90-f4b2-5310-9559-9fd9788b3180 | textbox | Details:
50fc1f51-0d98-5d4d-98b8-406ab04346c9 | textbox | Tester:
bc7aba64-733c-565a-86cb-c7a7b0e4f78c | textbox | Date:
f4827fa6-11ed-57a9-af62-a24fcf786622 | textbox | Notes:
eb7824e1-718d-420e-88d0-a9794130646f | checkpoint | MATERIAL AND SIZE
deca2f4f-12e7-5206-884e-1b85219dbe92 | textbox | Details:
07a745c6-8f71-5f1f-ad75-63cc2f4bb6fc | textbox | Tester:
0135bd48-14dc-5643-a181-1a6594e03b37 | textbox | Date:
5de56564-d4fa-5c6b-824d-776f69311a2e | textbox | Notes:
68699bee-a8eb-4b06-8665-6ec1ad4bf7ae | checkpoint | ALIGNMENT
7d281057-1493-5967-ab02-8540468eda2d | textbox | Details:
77f02ca3-a856-5b29-80a2-21d0a75c2bc7 | textbox | Tester:
ec7e5747-0cb8-58d4-82a4-32450a9e27b4 | textbox | Date:
f5be27ae-dccc-57d2-b84a-b6d448691ddb | textbox | Notes:
b4f8b3bd-eb51-4cc4-b3d6-d1d5c5807c4e | checkpoint | LABELLING AND IDENTIFICATION
d0e570fe-4e81-56a1-9ccb-6effd60d5a3c | textbox | Details:
d63da4e9-9fbc-5113-a464-ddf5d1e11ef7 | textbox | Tester:
fd79e8e6-dfd7-57ba-be21-e4ea4aaadd4c | textbox | Date:
de629678-9e88-5a2c-ba1e-e182cb132c9e | textbox | Notes:
ff70dbc7-bb7f-4cd7-b784-3225b68408b5 | checkpoint | JOINTING
b994e14a-b92a-588b-a7e4-0aa73f8e0cf8 | textbox | Details:
30149e48-f152-5510-9ce8-04c669ff89a5 | textbox | Tester:
47d3f101-8f35-5d19-893f-e638df0fd0f2 | textbox | Date:
50cdf940-1dcb-5dd5-a0ee-11a8c8156a08 | textbox | Notes:
0c25f0d7-c93f-4d98-89fb-23b01ed37bc4 | checkpoint | PENETRATION SEALING
1c1c6021-30c4-5248-bb79-8897c4b491b0 | textbox | Details:
325303f3-8535-531c-b4b5-221a86dea3c4 | textbox | Tester:
66cdc998-c1ff-5bca-8984-50c590facd1e | textbox | Date:
76060c86-959f-514e-ab7f-cab81c41081a | textbox | Notes:
9f50aefe-1148-43b3-898f-f99612ccd815 | checkpoint | FIRE STOP COLLARS
e7bfbefb-9f10-5e72-8122-c31aecb779c6 | textbox | Details:
6bce09b8-7aaa-5173-934f-f1f3f7d572bd | textbox | Tester:
4eced936-2e8a-5f80-be93-3960b6162a73 | textbox | Date:
4b998f6c-a402-5504-a95c-d43c0a938f4b | textbox | Notes:
106bd8ae-e1d1-4b4b-9c45-8853a79c7e53 | checkpoint | TESTING
71a7d695-e54e-56b0-9466-f95555cd6a59 | textbox | Details:
1c527bf2-cdae-5b98-bfd8-03178f5a98c8 | textbox | Tester:
1e6cf1fe-9ce6-50d8-8ce0-26bfacc3fce1 | textbox | Date:
cddf4463-4a4e-52b9-a596-27c9371c9a65 | textbox | Notes:
86c71726-3a18-4df3-80ca-3657d6354fdf | checkpoint | AUTHORITY INSPECTION (if applicable)
8dbfe186-9347-5b1e-9017-aaa0b7c1c65e | textbox | Details:
7102f4b5-64db-508e-a33c-7b3603580fc5 | textbox | Tester:
c899d8c1-751f-5430-ab74-66cb629f0b11 | textbox | Date:
64c2a73f-7725-5c7a-ba2f-1e26b72a2b71 | textbox | Notes:
ed15fbaf-ed1f-4f48-9064-b702c05beef0 | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
96f03fef-56c7-5c6e-9513-39def05a6eea | textbox | Details:
c7d8a8a5-aacd-593e-9d40-40d71c882185 | textbox | Tester:
d747c5be-5739-567a-ad90-c2c8adb50b78 | textbox | Date:
40fcaafa-4da0-5923-961b-3d2d09739447 | textbox | Notes:
444a554b-8a67-4bbc-a62e-a7358017b9d5 | checklist | QA5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  | QA 5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7760afa6-62b9-4704-b3cc-7bf1723a456c | checkpoint | Installation Test Sheet:
e197ed6e-6178-5518-a948-27354fc0bc32 | textbox | Drawing No.:
b7c7db3f-5eec-5429-a3e3-69228d84b3cb | textbox | Rev.:
f1a5abcb-7c60-4907-a032-339712e4f5ff | checkpoint | PIPE CLIP HANGERS
44d7272c-d366-57ea-ba1d-4a23d61a3a80 | textbox | Details:
082b902b-9256-5337-a2b2-b84276bb94ee | textbox | Tester:
0aada1f6-e1db-57d6-ab10-f55fddfa36f7 | textbox | Date:
38ada06f-9c23-52fe-b1ad-20dff3ea8416 | textbox | Notes:
30028503-2281-4259-8f92-3f24e405d906 | checkpoint | MATERIAL AND SIZE
63ca1d0e-8e13-58fb-9aaf-f4699ba41ca4 | textbox | Details:
d8b22541-284a-59ee-9627-e7d6830a0c4f | textbox | Tester:
1626fad9-4c53-55f6-945a-0e88fe2e5cab | textbox | Date:
213bdbe7-6b37-57c1-b10a-6fe7178fb731 | textbox | Notes:
1108e4ce-2457-4860-baa2-f9ffb15a34fc | checkpoint | ALIGNMENT
490061c1-04ae-5053-a077-99627c3acd88 | textbox | Details:
1b2ea711-d9b7-5ba4-8615-733bc4e0b85b | textbox | Tester:
56369c6c-fd68-5559-b95d-a4960c6e2713 | textbox | Date:
272550d8-5bb6-506a-9fd8-52c89c88a4a3 | textbox | Notes:
58d9edb7-4b73-4fd0-832c-993568bace12 | checkpoint | LABELLING AND IDENTIFICATION
045b087e-de1d-586f-89fc-9b0060eea743 | textbox | Details:
35916735-ee68-5eff-a3b0-5dae2377b15b | textbox | Tester:
1cc4b113-c177-533c-b98c-e98dd9861f49 | textbox | Date:
541a1f93-a5ff-5d6f-b0c7-c81410f7fb76 | textbox | Notes:
5dd87be9-9f2f-4199-aec1-6e9c63ba99b8 | checkpoint | JOINTING
1404d61b-8ed5-5dce-8cae-684211af34c8 | textbox | Details:
2cae843f-4206-50d2-b6dc-a4e0c0e5f35d | textbox | Tester:
17e393d4-4e8e-5f5a-a374-2b46aa3ac6f4 | textbox | Date:
c1e84c6a-d536-5520-82e3-9a711ce5c2df | textbox | Notes:
4282d56b-606f-4ca3-b1d4-5bdc0e015223 | checkpoint | PENETRATION SEALING
981fa658-0133-5fcf-8bac-6ac0255de702 | textbox | Details:
20a542b3-d064-5128-8f57-b65e9814c5e7 | textbox | Tester:
5ac69111-51b7-5887-811a-f94eac518513 | textbox | Date:
a397b0e3-13a5-5fa1-8693-3c0a15a737f1 | textbox | Notes:
b6cbf85d-9808-4ab7-94c7-f80b134e3321 | checkpoint | FIRE STOP COLLARS
dd245973-0a18-5515-a7fb-d16b9918d8d6 | textbox | Details:
09679752-77f5-50fc-ad55-f60996565727 | textbox | Tester:
527944b4-1bb4-5164-9598-49a20f28dac1 | textbox | Date:
670ec391-4c16-5fa6-8ff5-093231baa36c | textbox | Notes:
311f4bc0-d8a3-4be6-ad30-d08f4e427184 | checkpoint | PRESSURE TESTING COMPLETED (QA6)
e4b64f3d-5483-5f4c-b811-a2bec895349f | textbox | Details:
4e0c17bc-ae25-54e1-9450-f658276d9e75 | textbox | Tester:
7583de4c-367e-5276-832c-1e1815185bcc | textbox | Date:
cfffa6a8-fe9a-5371-8137-e58ea801f943 | textbox | Notes:
b0b0e4a9-ffaf-496d-bebf-67590e2662cc | checkpoint | AUTHORITY INSPECTION (if applicable)
a6cdaecb-2bc4-599f-8939-3bc716708b6a | textbox | Details:
017b3210-04bc-5543-9abe-267a7fe378de | textbox | Tester:
393518a1-9448-5439-a650-f6137fe05892 | textbox | Date:
c363398e-324c-5262-a8fa-d8ce1d9bb668 | textbox | Notes:
cb6f4d33-9a8f-4249-ad0c-b1c0dd69f72a | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
0a03d185-3750-538d-be16-10da72a5b0c4 | textbox | Details:
77387cdb-0eb1-5a05-b1f2-e5f84a18257f | textbox | Tester:
14a3551b-2f0f-528b-8e1d-baefb66c2fe6 | textbox | Date:
be5fe819-ac46-560f-938d-3a29bc8d9991 | textbox | Notes:
693efd1d-ca26-4458-876d-b6f108879ae1 | checklist | QA11 - Equipment Calibration Register |  | QA 11 - Equipment Calibration Register
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7f234d05-075f-47bf-a080-3256d5ed4190 | checkpoint | 1
117ff351-923a-510a-ad1d-028375a1b2e8 | textbox | Equipment Type:
faf0a77e-0469-5f2c-a022-60925becd3de | textbox | Manufacturer:
fd514dc6-dec9-5306-b6f9-417ba26b796a | textbox | Model and Type:
9c4f0694-acd7-5017-a569-4e0d72846793 | textbox | Serial No.:
49d7c327-f8a3-5022-ba05-93fd88b20074 | textbox | Next Service Due:
35ae4cb1-1e83-4ca7-bf2f-330f90d3bd21 | checkpoint | 2
ceba8aba-1319-58e1-9d15-78c1e5e84fc9 | textbox | Equipment Type:
4c5a60dc-9960-5ae5-90dd-252f29c8ab92 | textbox | Manufacturer:
0b6526b8-b8dc-52bb-830d-3a68f538e275 | textbox | Model and Type:
2193ef27-03d4-5331-aee1-55fa2057323d | textbox | Serial No.:
d6ca466d-f42f-5ade-9e66-23be1a85044c | textbox | Next Service Due:
55583d7e-5f95-4350-90a3-cd3f32f763c2 | checkpoint | 3
0b91487a-678f-5cf7-8225-136f55a98f6c | textbox | Equipment Type:
f147dfd4-de5d-5759-8e01-1ff491f3b567 | textbox | Manufacturer:
bb51be9c-c03f-5cbf-9bc8-946829fa6c48 | textbox | Model and Type:
c4855dd4-35fb-5592-a005-584f0c8eac7f | textbox | Serial No.:
52d00a50-d947-5350-bbfc-1fe37b4f9f3b | textbox | Next Service Due:
0b9f88f1-d2f3-4ff9-aed4-e3c0c25ea529 | checkpoint | 4
53ba1661-175b-53ba-975a-cae1cd5282d6 | textbox | Equipment Type:
04ad4531-c91a-5329-8a60-4b1497dbc604 | textbox | Manufacturer:
38519c86-b301-5c91-a2b1-62149d1e2dfd | textbox | Model and Type:
481c58fd-3a6a-5210-b5a0-087118413685 | textbox | Serial No.:
b85f452c-3bb8-59c5-900a-1c904b846dc6 | textbox | Next Service Due:
60eb3cd3-8928-4295-ac0d-55e8a22d8ad5 | checkpoint | 5
cc00efc9-4684-59dc-885f-a6e3c79b31a1 | textbox | Equipment Type:
cc39965f-33d7-5bba-8bde-fe411081600a | textbox | Manufacturer:
98a73f16-56f7-52a4-a7c9-36e41d5f4085 | textbox | Model and Type:
f6f83c9f-9aa4-50bb-8f35-70fc62bff58e | textbox | Serial No.:
4a02e740-fb6b-5597-87a0-ce8884d651f5 | textbox | Next Service Due:
c91da491-9864-46c5-a67c-58a9907a0e36 | checkpoint | 6
ad254d97-9b4b-5c41-bfb7-30617262e2ce | textbox | Equipment Type:
98e6302f-ba0a-5012-b5ea-61f6f4e14c59 | textbox | Manufacturer:
b0de04a2-a5a7-5aa7-91d6-5c77a8c179cc | textbox | Model and Type:
9e389c6d-048c-5af7-8b82-ceb1c8ce852f | textbox | Serial No.:
8075e238-ef69-5e5b-95ef-d8fa00ad8562 | textbox | Next Service Due:
2049a3a7-b38c-4025-aa3a-c47c6ad1b7d7 | checkpoint | 7
c64a8b0f-b0f6-55ab-addf-6a8a63aef7c5 | textbox | Equipment Type:
805f2901-bfc7-5fb5-98bd-2f10b36c7f2f | textbox | Manufacturer:
6ec66a3f-fd32-5c1b-bc75-6d5b6b2472d9 | textbox | Model and Type:
5aa16f6a-11ee-5497-a789-2c300020e902 | textbox | Serial No.:
52c18047-5d75-5809-847d-3c6c4cd2a9d9 | textbox | Next Service Due:
2cf39b28-5619-4a5d-8e41-2c3616994b5a | checkpoint | 8
7faa36b5-25fe-549b-9dcd-cd2e2e60ca35 | textbox | Equipment Type:
6b39da7d-0035-58ee-9134-f54cdea21d3a | textbox | Manufacturer:
e69fd37a-d1be-5ba6-9b53-407907b6cd04 | textbox | Model and Type:
7afc4837-d3c5-5d8b-84d0-5ec4386dbd4c | textbox | Serial No.:
b7f98ffb-f243-569a-be40-e1b68918d0a9 | textbox | Next Service Due:
59120d8f-63e6-40f7-80cf-0f9ddd8b3a89 | checkpoint | 9
92f3d5ae-16b4-5129-ac7d-6f00b599ad57 | textbox | Equipment Type:
e7128acb-9023-5b04-87a7-e1a4669ac33f | textbox | Manufacturer:
09d1f420-d9d3-5c9a-85f1-d64c48d047d8 | textbox | Model and Type:
f4d83570-fa11-5c07-859f-ca6dc4777a84 | textbox | Serial No.:
1c5cffbd-92a8-53d4-a13b-13502be611de | textbox | Next Service Due:
ce9ba61f-0a28-41e1-aa63-c3c422c8ed6c | checkpoint | 10
f9a4bbd5-dd03-5fd9-80b0-41f4eff951b3 | textbox | Equipment Type:
15314bbe-2df5-537a-ad4b-0ec7a90956ce | textbox | Manufacturer:
41653987-9315-5478-9b06-f8051ed2024f | textbox | Model and Type:
042500d5-6da9-5823-8580-04f42fedb1a5 | textbox | Serial No.:
093bc8e9-1161-5593-84d2-29492477d59a | textbox | Next Service Due: