## Master List Templates
Id | Type | Name | Values | Prompting Name
56382672-0691-43a4-a828-ac4b9b803bd1 | checklist | Core Sanitary Sewer & Vent |  | Core Sanitary Sewer & Vent
5a0aa8ea-056c-44fe-adff-61b3220fe083 | checkpoint | Mainline at specified grade
e9ecc96a-3a9a-49c0-80a2-e155c540f9f7 | checkpoint | Stack & Branch junctions installed
1b4bf9c8-0e43-49b9-8663-7cf7ddb1ef67 | checkpoint | 15Deg roll ups on all junctions
f1d8bbef-698f-4824-85dc-63dafa6dfbf4 | checkpoint | Expansion sockets installed every 4m
89aefee5-c1ca-4fba-a347-c7712b7f383a | checkpoint | Inspection points installed as per plan
3543c7f3-ac1a-47e7-aa73-06b88c0d6801 | checkpoint | Connection to existing pipework plumbquicks checked and secure
57d694d6-039e-4e00-ad02-dabedaa3bdc8 | checkpoint | Correct or exceded minimum fall
3205e74d-acd7-4745-b448-69df00f06102 | checkpoint | Correct Clipping & Spacing
146d9d4d-7d7e-4d02-8004-84efb47329f3 | checkpoint | Stacks vertical to venting in ceiling
8a54b916-d631-4b6f-8f62-c995dca64e99 | checkpoint | Vents graded in ceiling with clips
031cf62f-0f0d-4d21-88d9-6b59f18cebe1 | checkpoint | Vent roof penetration installed and flashed
ea25c40c-d7f2-47db-befc-07de0be7238f | checkpoint | Flood Test in accordance with ASNZ 3500
ae8e4b4b-9390-4987-841b-8183152a6559 | checkpoint | Hydrostatic test Plug Removed By
e5922454-7a2f-4f93-a1d3-212e1a661454 | checkpoint | Inspection Cover Replaced By
4f30e493-d974-406c-a1eb-8cdc183f5e1c | checkpoint | Seismic bracing for pipework, longitude & lateral
ccee43c0-dea6-40c3-9746-17a5f9ce0f03 | checkpoint | Pipe labeling
48dc767e-c63c-4ce2-b7f1-6e2dca3b806e | checkpoint | Access points for cleaning
2bd2301d-5bf2-4dd8-b3be-3e0316b578f6 | checkpoint | Acoustic lagging
8b357172-be68-4b7e-9445-9a343cb6067a | checkpoint | All pipe stubs covered or capped
5cf72998-6fb9-4658-8155-d6eb43e177cc | checkpoint | Installers name & date works completed
64789f14-b6a0-5b23-85cb-66488babdd6d | textbox | Installers name
7892000a-0ecc-507b-8aff-58e7fa848e83 | textbox | Date:
471c660b-e6b1-433b-8c85-27e06cfb9b9c | checkpoint | Tested by & date
f66cbdbc-d389-5cd8-9913-3927c5a1ef1d | textbox | Tested by:
b972ebf6-5d5a-5c50-83c3-7ad9cf222f2c | textbox | Date tested:
ab649d79-de3b-4b5d-991c-79bb9d57e026 | checkpoint | Council inspector sign off and date
3604efd8-4627-4418-aa51-26d38fb2f5a0 | checklist | Core Water |  | Core Water
770cdd2b-b1fa-486d-a156-38d95c98a72a | section | Cold water main
264f2589-db31-4ad1-ac80-caacc98c80fb | checkpoint | Connections brazed correctly
af37c1c1-351c-4c99-8f83-b81496c9e361 | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
978dbd96-af22-47d6-a000-4aae2da9784f | checkpoint | Valves fitted correctly
d2dd852a-c3b3-40d8-966b-1086c6a83c78 | section | Hot water main
0e854e4d-e7e6-4460-89d6-14caed6bd60b | checkpoint | Connections welded correctly
7f8a86d9-9463-4d4c-8667-362004037677 | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
734f77e4-5055-4086-9f30-4516e24157e8 | checkpoint | Expansion allowed for
78bfae5c-3166-41c3-9e30-af319cb9f9dc | checkpoint | Lagging installed and neat
c62f2bee-2243-4ebd-b4f2-306c452ea1eb | checkpoint | Valves fitted correctly
ebfece48-b460-4350-8a20-b3578ce01b0c | section | General
f7d4877d-5765-4d37-b890-edb914a0f3ce | checkpoint | Open ends of riser capped for testing
bb888591-5abb-4114-b3cd-03615367bcaa | checkpoint | Checked for cross over's
0ee4c57b-8013-4667-b75a-84703371ea79 | checkpoint | Tidy work areas
1fa02bdf-390a-42e8-99f0-113a88dfe79b | checkpoint | Allowance for expansion
a9db10f3-0b5f-47a3-b808-7f9216689f46 | checkpoint | Pressure test to 1500kpa for 30mins
1befb03b-3a76-4dac-b78e-dc2308930020 | checkpoint | Visual check (for leaks form valves, tees, saddles, etc)
9591b728-9c1f-4273-9dda-7d814e63b4a6 | checkpoint | Seismic bracing for pipework longitude and latitude
1a438f4a-68af-4cfb-8134-bfb43b6cb5d8 | checkpoint | Lateral labelling of pipework backflow devices fitted
3be72a97-3d52-47b5-85c5-e1568ce46b09 | checkpoint | Pre Line Inspection Passed
d12f6a61-2f90-4d68-9b63-3ce483b1d9e5 | checkpoint | Installers name & date works completed
f61002d8-c9dd-5269-ad0d-32e5de16d6a4 | textbox | Installers name
551e025c-f505-50a6-b2e8-ca7562a8bcd0 | textbox | Date:
54ae830d-1de1-4b5d-99bd-1cbb43535ed2 | checkpoint | Tested by & date
589c4303-6940-522b-8bfb-3465ebcc45da | textbox | Tested by:
40f2a074-d30b-5f8d-8262-55b4651ea227 | textbox | Date tested:
2d335f42-62f6-49f7-bfaa-1b1af1ffd23d | checkpoint | Council inspector sign off and date
34b1ec9a-aba8-43d4-b660-b45d5335a10e | checklist | Hot Water Plant Room |  | Hot Water Plant Room
12b72ce2-8ecc-4a1d-af81-829ad101ed59 | section | Hot Water Plant Electric
63ac0edc-1da7-4bf9-b987-6dd6cc422841 | checkpoint | TPR opening and closing correctly
01bfdf82-91b8-4d7f-92af-d6eb12eeb43b | checkpoint | Cold water expansion opening and correctly
b1826bdd-0da1-46d2-a35c-2b34d1ede1b5 | checkpoint | Incoming Pressure
d8bb7edc-2461-5a13-8251-cbde0e8592d7 | textbox | Pressure:
0737f1dc-7504-4029-bb63-f1523b5ec5bc | checkpoint | Thermostatic mixing valve fitted
649d88fa-74e6-4635-86fa-2fc5fe1ae133 | checkpoint | Temperature at thermostat on HWCs
3bfaf10b-af0f-5394-9c0d-460375e1a791 | textbox | Temperature:
c5f8d2d2-53f0-4f4b-9849-2f6db04bcb68 | checkpoint | TPR Pressure rating
2d07c436-187f-554d-afa0-d5099d70f0c2 | textbox | Pressure rating:
d6b09e17-43dc-442f-a4f7-ca9c93a1ecea | checkpoint | Water dump and Sludge clean out required or recommended?
839c36f4-e0c7-4270-a7d7-a17f6f6ee896 | checkpoint | Seismic strapping tight and in all three locations
66cfdf96-23cb-4a86-af4c-bf136c6181de | checkpoint | All strainers free and clean of debris
9fb6d367-d79c-4f2a-bec3-101cb733e917 | checkpoint | Pipework Free of leaks
79017807-de9b-4673-afe4-1229c7424f2c | checkpoint | Valves opening and closing freely
4edaec32-8e0f-4590-8718-76e6efdc55b9 | checkpoint | Reticulation pump operating correctly
4f3a1826-f618-4bde-a320-ac78a8579000 | checkpoint | Tray drain clean of debris, free from damage (i.e. Cracks Etc)
aa2854b7-ece2-47e8-a47b-a6c12f816e26 | checkpoint | Visual Check
31cb749c-ffdb-4ace-9f6d-651f19b22eaf | checkpoint | Additional comments & photos uploaded if necessary
626fc25f-8215-48b0-bcc7-1999990aa603 | section | Hotwater Plant Room Components - Pumps & Tempering Valves
dbd1e63c-0936-4c55-862a-a165ec3a3063 | checkpoint | Flush all lines and strainer including
46b0cc08-35eb-4ae5-a59e-f9431ca6642b | checkpoint | All safety valves installed
ccbfafa9-4c43-4608-ada4-ea965069d777 | checkpoint | Relief drains fitted
96e960d4-0597-4c66-86bb-23b7ac90992c | checkpoint | Relief drains to tundish
7d54dd3d-b132-4540-a806-be238605af1d | checkpoint | Check All Connectors For Leaks
c3d83eb9-ef2d-4088-bdb5-4e7a48e21f96 | checkpoint | Check all valves and connections for leaks
f6d907ad-290e-400a-886b-f847fff7ddfb | checkpoint | Operate cold water expansion valves / check operation
2bc9d28a-62e3-4f11-8bb6-88a48bae05ee | checkpoint | Set limiting valve
1dbb8022-bba3-4d4e-b9fe-afc6bf8d9801 | checkpoint | Check for crossovers
633889b2-2791-4f3e-8c7c-7856b243beb1 | checkpoint | Check HWC For Correct Valve Installation
261b519c-b16a-48cd-b10c-8710f662bf01 | checkpoint | Lagging completed
478e111c-cb46-4d62-becc-0d38f965b0f5 | checkpoint | Check All Hot/Cold Pipes For Correct Position
4b30196f-cded-4bb0-ac69-9d99952a7235 | checkpoint | Bleed air from circulating pump
cfa3b65d-51da-4281-9e92-8a25089f0087 | checkpoint | Set all return thermostatic balancing valves
f85bc1c7-3f43-4147-a5a9-3e6b4a9f2d17 | checkpoint | Installers name & date works completed
b56b0b9e-7165-5b35-949f-f30e72d968b7 | textbox | Installers name
7ae04966-ea2d-5b83-b110-686d63fb54ce | textbox | Date:
e3b2d8f7-f84a-4ed8-9f35-82be8cde8923 | checkpoint | Tested by & date
2895286b-6018-538a-9613-5e10020e0ccc | textbox | Tested by:
75851ae9-4a87-5abc-9588-21055bee3c53 | textbox | Date tested:
71b5d413-23d3-4c79-963b-bc95ec757692 | checkpoint | Council inspector sign off and date
2ba116cf-138a-40f3-bb00-779587e7bab7 | checklist | Pressure Test |  | Pressure Test
efe1422f-31c1-441f-bffd-864ed62d802f | section | Details
14c24c04-2031-4023-b903-41fe5f2c958a | checkpoint | Details
4baf87ec-9633-57ed-8592-abaf29574f0a | textbox | Guest room No. & Location
f1d435af-5070-4d1a-b692-798f1b2e8108 | checkpoint | Service
6a29dede-88ca-5647-8f6f-765e7f4912fe | tickbox | Soil
90c969f8-00d6-52fb-b37a-390a52bef2de | tickbox | Waste
48e470e7-eb8e-5d3e-bc11-8edb8642c126 | tickbox | Vent
9c9a4d7e-7441-5421-84f7-f623c4d01f19 | tickbox | Water
61766232-70c8-571a-b54a-3253b6a0100d | tickbox | Gas
26a4088e-dc49-5b96-90d3-ba0f068a8f7c | textbox | Other
c2b2c014-cc94-5d94-8645-b42bae9a1c1d | textbox | Pipe Work Material Identified:
e79b7e94-156f-5176-8613-45111ac21cc5 | dropdown | Test Required | Water, Air
f892987d-806d-4fc3-ac5a-1004ab780ce4 | section | Test
a0b59c8c-9008-41a2-b00c-1a1c3bb9f3f7 | checkpoint | Tested to AS/NZS
61b83c1f-8510-58c2-8f55-9d2983e4439e | textbox | If Specified:
6c691045-7c6c-5257-860a-1e00fdb61a84 | textbox | Start Time:
7047d3e2-6d25-5250-957a-cbc05588bd2b | textbox | Finish Time:
4bf168bd-8fec-5f3c-9366-9c7b7f631387 | textbox | Test Time:
46f199ce-eca0-57d6-a093-6bd847e45023 | textbox | Start Pressure:
c3e006da-3103-51a8-88a7-fa99eaa881d0 | textbox | Finish Pressure:
8b42f3f4-cb2b-487e-a7ca-f10555835ddc | checklist | Thermostatic Mixing Valves Guest Rooms |  | Thermostatic Mixing Valves Guest Rooms
77d2b4a9-b55d-474b-a379-8d848fa7a554 | checkpoint | Guest room Numbers that TMV supplys
c4711d24-9eec-55d1-a230-36a055aec686 | textbox | Guest room Numbers that TMV supplys:
f300213e-d90d-4d7e-9554-e62c8798ddc5 | checkpoint | TMV installed in accesible area
b5e9e5ca-21fc-4337-a664-96edfa6be952 | checkpoint | TMV installed in correct orientation
0b1cc2b0-34d3-4c07-8f7a-a96cfe1e797f | checkpoint | Non returns and filter gauze fitted
235902db-1399-4a78-a7a5-bf7820b2907f | checkpoint | Valves fitted to TMV
06d99b55-b6fd-48fe-8f82-55c3d490ee5a | checkpoint | Pipe tested prior to fitting valves
a505d7d3-cbde-43e3-98a0-580058764043 | checkpoint | Connections made and no leaks
6d096a7a-57c2-4759-b694-e3016f7bdc06 | checkpoint | Clips and spacing checked
19b75e2b-422a-41ac-9c3b-777c3e91a649 | checkpoint | Brazing and crox connections sound
33a96968-8b19-4d6f-a7d0-1ecc7e03cc41 | checkpoint | Seismic requiremnets achieved if applicable
a28f4234-e3fe-41a1-b94e-9312847aefb2 | checkpoint | Pipework lagged where required
741ee20c-50cd-4665-99f4-b7f84edf6d0e | checkpoint | TMV labelling
5766fba8-35b8-41a7-bdf4-f58c4a89e2ef | checkpoint | Tempreture set on TMV
f7976041-1199-43d6-9a7a-7402d6cd8f9e | checkpoint | Installers name & date works completed
c5477d30-3b04-584c-9361-d2d480407171 | textbox | Installers name
4194ecae-7fa6-5d9b-bc2e-3ad9312f2dce | textbox | Date:
2e102e3b-cc01-40e6-8488-06cdeed2e2f5 | checkpoint | Tested by & date
2aea899a-8c1f-584a-a03a-8d8f62ab9b1c | textbox | Tested by:
bf7f3036-d77d-5a05-84b5-dc1d51dc90e4 | textbox | Date tested:
74cb5434-e277-44ea-aabf-2c85d7cf9b6a | checkpoint | Council inspector sign off and date

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
5aec714a-8d0f-489e-8cf7-59ab1a5fe9b8 | checklist | Core Sanitary Sewer & Vent |  | Core Sanitary Sewer & Vent
dea52f8a-e074-490e-b8a4-d770c4f206ee | checkpoint | Mainline at specified grade
cd792f50-854b-463a-940b-ab755d8bfaa3 | checkpoint | Stack & Branch junctions installed
3e6bee64-9de4-4192-9f01-9b1c14a2a273 | checkpoint | 15Deg roll ups on all junctions
cfa6c2b8-a5dc-4b9f-965a-6f08213b205a | checkpoint | Expansion sockets installed every 4m
5efc5c6b-c7b5-4bc5-b9fb-5c119f8f2d04 | checkpoint | Inspection points installed as per plan
58701369-e6c9-4993-aa5b-91772137c316 | checkpoint | Connection to existing pipework plumbquicks checked and secure
57625927-154f-426b-beae-4ea4f79f91a7 | checkpoint | Correct or exceded minimum fall
7fc4abba-6e41-4dfb-9ae0-a9f38e36d4cf | checkpoint | Correct Clipping & Spacing
b49f6eb5-cfc4-4f81-bc10-dd881cef23c0 | checkpoint | Stacks vertical to venting in ceiling
a81d419e-8e41-40fc-9217-95cdc9bd035e | checkpoint | Vents graded in ceiling with clips
95f8b971-bd3b-4859-b19a-5a1502856b78 | checkpoint | Vent roof penetration installed and flashed
b8a73057-43ab-4c99-b56e-1cac88d3c3d5 | checkpoint | Flood Test in accordance with ASNZ 3500
092e311a-ea77-4577-bea0-e6c262224610 | checkpoint | Hydrostatic test Plug Removed By
86ad2d4c-c7a1-4d59-b2ca-1c9c97ea465e | checkpoint | Inspection Cover Replaced By
2cc34ef0-51c4-48ca-b5a3-571a722734b2 | checkpoint | Seismic bracing for pipework, longitude & lateral
4087a2f8-8958-4742-84ba-525df1d7d1a2 | checkpoint | Pipe labeling
adfbff39-6ec5-4f38-be47-cb7d3cc264f3 | checkpoint | Access points for cleaning
6fc3d6a1-27b7-4a02-8fd3-91dbfc9f0416 | checkpoint | Acoustic lagging
3e106cb7-fc8a-4912-af39-ab5d2c4c0191 | checkpoint | All pipe stubs covered or capped
e2f28c61-2946-468b-8071-89d363d79ccf | checkpoint | Installers name & date works completed
087b28e1-c393-5a06-81ce-d99385cc3bdf | textbox | Installers name
4ad97e25-971f-5ef2-9179-97ea08bdc45b | textbox | Date:
966d02b1-4068-4226-9e2e-ebbfbe7f5ec8 | checkpoint | Tested by & date
db0d5a99-45dc-57ff-b72f-51c22cf62ad9 | textbox | Tested by:
74cd2416-33e8-5164-9377-3464e32d415c | textbox | Date tested:
378873cb-18d5-411c-8925-13c46aa43f8c | checkpoint | Council inspector sign off and date
8b05db9a-a3a3-41fd-a1c1-3ec95a4385a2 | checklist | Core waste & Stormwater |  | Core waste & Stormwater
bafa68a3-59f3-4511-b466-d57edf27e779 | section | Details
1de4a638-a1fb-46e9-bd72-a07c1b4fcd61 | checkpoint | Waste Pipeout
7168301c-e5e3-43e3-82a9-acb6136b18a6 | checkpoint | Vent installed
86eefdb6-078f-4553-9a45-560b355047e1 | checkpoint | Check sewer hasn't been connected to stormwater.
4e5793c6-2d4e-479f-8af1-1c64800c981e | checkpoint | Correct or exceeded minimum fall
e6b6b649-e14e-4e4a-a80f-648c79168b5e | checkpoint | Correct Clipping
f97ebd25-e21b-4ea0-bae4-e3bc3c8a3bed | checkpoint | Flood Test in accordance with ASNZ 3500
e9928e42-c86a-4cc5-b7f2-a23c1c347e60 | checkpoint | Hydrostatic test Plug Removed By
c080600a-d0d0-45fe-98e6-d64b4664649b | checkpoint | Inspection Cover Replaced By
3a5465ac-347d-42f0-a848-4d5e374e6a87 | checkpoint | Seismic bracing for pipework, longitude & lateral
8121429f-f18d-481a-902d-3a4263a2546e | checkpoint | Pipe labeling
6b338cad-d947-4986-b7d0-dd4914aa9a3a | checkpoint | Access points for cleaning
77f2f277-7205-493f-b23b-6435945b6ad5 | checkpoint | Acoustic lagging
69f51baf-f7fe-4005-a816-8a5c4547bcc6 | checkpoint | All pipe stubs covered or capped
daf66be2-e401-4ff3-83ca-6e15981b66a7 | checkpoint | Installers name & date works completed
8a2cdfd7-9583-5dfa-8a3f-05841fa47ef8 | textbox | Installers name
545f4d3c-0cc9-5789-b36f-ef6f472bd31d | textbox | Date:
48fd3217-abc2-4009-a477-2941e76261bb | checkpoint | Tested by & date
56ea67bb-221a-5bbe-b1b7-c6ebacf3737b | textbox | Tested by:
04fdf127-4f92-5c52-963a-c47189c1bd5f | textbox | Date tested:
252a4ddf-b626-447a-8701-b0033a949962 | checkpoint | Council inspector sign off and date
b4f68355-b942-4e89-bc77-7e78a0f38c7e | checklist | Core Water |  | Core Water
326ee9c1-a23b-49d5-b1c4-d5cfae0eda2c | section | Cold water main
1b634a4d-df5d-4c2a-8d64-26446ad18336 | checkpoint | Connections brazed correctly
9ad577be-3002-4bdd-9e78-18a69b5b5b0f | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
553fb94c-6032-427f-bbf8-ae6d809155e9 | checkpoint | Valves fitted correctly
aa2cb55e-e644-459f-937f-e4f9ae82d054 | section | Hot water main
8f43af65-17d6-4221-9a0b-ee547f7abcac | checkpoint | Connections welded correctly
3c9d032c-e95d-4224-a4c7-3fa951135e80 | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
a744ecef-305c-491c-8b8b-bfee3c5849a0 | checkpoint | Expansion allowed for
cfbdc44f-7166-40b0-b286-d6b670410db4 | checkpoint | Lagging installed and neat
ba201a2b-74da-4020-a710-884fe618e459 | checkpoint | Valves fitted correctly
4fae4d49-282d-4cd0-8fa7-2a644ebd7df6 | section | General
baea8146-ffe6-4522-8079-10bb8ebe8a76 | checkpoint | Open ends of riser capped for testing
0e626ec6-f48e-4b53-b426-68885cbf765b | checkpoint | Checked for cross over's
037964f0-0297-443e-86e5-b4dd20fe6e3b | checkpoint | Tidy work areas
d840465f-1c12-4421-919a-93e55f32658d | checkpoint | Allowance for expansion
673478f5-5b31-4775-8127-5b9f352a0e66 | checkpoint | Pressure test to 1500kpa for 30mins
472b54db-3eba-4a04-b50d-3f1808dd30c7 | checkpoint | Visual check (for leaks form valves, tees, saddles, etc)
34e1a9fe-e342-4718-b0a3-64f03e7d010b | checkpoint | Seismic bracing for pipework longitude and latitude
56cd8203-f1ca-415d-8bb1-b67af44f15f1 | checkpoint | Lateral labelling of pipework backflow devices fitted
3f38e6ad-bf22-4bcc-bb07-18226a26b1a6 | checkpoint | Pre Line Inspection Passed
f6383999-0390-4d83-ba44-99c93260b087 | checkpoint | Installers name & date works completed
a7212cba-7549-53a3-872b-9e204dc07f3d | textbox | Installers name
c5068e3d-1b1e-5bc5-b302-dd5ffb70f9ce | textbox | Date:
bbc9f0e0-0ed1-4dc1-9db1-7503cfa864de | checkpoint | Tested by & date
c5224721-7ec2-5bf2-adaa-12a53365ea7c | textbox | Tested by:
675ac191-ff15-5877-8cbd-744505b921ad | textbox | Date tested:
b1b1e87e-517b-42db-bec6-e19461a45a86 | checkpoint | Council inspector sign off and date
39a67e33-1940-404b-b820-84e3963dc9be | checklist | Core Water & Gas |  | Core Water & Gas
684c0e5d-0542-4fa9-89aa-2f065c6aa683 | section | Gas Mains
bb5a48d5-b405-4527-ba3c-d9ee05990dd1 | checkpoint | Connection brazed correctly
13f56a95-5074-4e08-a00a-7899a7722a56 | checkpoint | horizontal/vertical
fd4bc5c9-f943-463a-a6ed-69ba453183d4 | checkpoint | values fitted correctly
cf89328a-a6a5-43dc-8034-4161c87f9889 | checkpoint | Drop test complete
1ea3b48b-5b3f-46a3-88c8-0c7b9a2d1422 | section | Cold water main
d0597e83-aec2-4e62-9b0f-768a8b4b32dc | checkpoint | Connections brazed correctly
8fe290fc-d0c8-49f6-8771-1c9f1f2562b3 | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
8e3ab1ae-5163-488e-9444-6438683bd914 | checkpoint | Valves fitted correctly
2d3eb938-2230-4871-abcd-c784b3889099 | section | Hot water main
c3cfff68-5e15-4acb-889b-bcf2fe6b91cc | checkpoint | Connections welded correctly
6427a9ef-365c-4c9c-9dc1-4a43d8c65926 | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
081e55eb-c145-493a-a2d2-d7e712a68271 | checkpoint | Expansion allowed for
f27689a2-61ba-4f9c-82f4-1389042a0ea4 | checkpoint | Lagging installed and neat
1ba8ce56-6998-42aa-9337-fdd77d01376c | checkpoint | Valves fitted correctly
4f0437e6-c717-4363-8675-3b8a6f413a75 | section | General
f2421e04-46f2-44ca-aa2f-ef7a216a2824 | checkpoint | Open ends of riser capped for testing
ffb844c9-91da-4380-89a4-7814f8ef23fb | checkpoint | Checked for cross over's
908573a7-f947-4403-a7e3-5d53b79a3519 | checkpoint | Tidy work areas
4a3a102c-0c5b-49b2-a8e7-2c02282bb7eb | checkpoint | Pressure test to 1500kpa for 30mins
d66e363b-cf3c-4f8d-9e6d-9720d20f9753 | checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
2d7eb0fe-0039-4cc9-9126-78c426fdd4fa | checkpoint | Seismic bracing for pipework longitude and latitude
a2aac7ad-88b1-4555-948a-3ba1f42c1c9a | checkpoint | Lateral labelling of pipework backflow devices fitted
0ebc4703-7780-4740-aef9-110dc18543ed | checkpoint | Pre Line Inspection Passed
77b455a0-452c-4397-97c5-ddd98e635802 | checkpoint | Installers name & date works completed
d12e8722-5e0e-5339-a79c-3d9ba772fe72 | textbox | Installers name
88bf8943-7805-52ad-b31e-0fbb442e012e | textbox | Date:
fd1a52e3-a59d-4036-b82f-0f4b59203338 | checkpoint | Tested by & date
a8d8662b-44bc-5ed8-9bde-0982b148ffc1 | textbox | Tested by:
a09b41b7-a931-57d9-a2a5-dc073dfb9c47 | textbox | Date tested:
7c7e7ef0-8d93-4109-beb6-3c717bda4c50 | checkpoint | Council inspector sign off and date
b61859f9-5db3-47a1-8abf-a0a93f8a28cb | checklist | Daily Pre Start/Works Checklist |  | Daily Pre Start/Works Checklist
38d5308b-d012-4648-935d-b1069a2f7dc8 | section | Details
1d213425-7841-44cd-a6f1-7c5432e8a96e | checkpoint | Daily pre start meeting completed
e5e2fb91-5750-576e-933d-078306f057a1 | textbox | Date
dd2c64b0-f9fd-5568-a083-13f9c61dc5a4 | textbox | Time
fd5bf908-df10-5554-becd-fb154be95d9f | textbox | Location of work being performed
ae5e3eb0-6ad0-4914-aaf0-dae55ad45bbf | checkpoint | Is the area clear, tidy, dry, accessible and well lit? (take multiple photos of installation area)
9ab7ce1f-77d3-40be-943f-ed8530032d21 | checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
614979c3-bb63-4cf0-9e2c-689e11afac4e | checkpoint | Does the delivery/delivery docket match the order placed? (*note: list all items not delivered)
9c334f48-a10b-4138-8850-91fa9c0e8b74 | checkpoint | Are the correct tools ready for today's tasks?
9700c03e-61c9-4ca1-a05c-f504bb61117f | checkpoint | Are Power tool batteries on charge?
3f0151cf-212c-4485-b1a2-61e3fd9fd23e | checkpoint | Is the threading machine, drop saw and pipestand set up and ready for use?
f0c8d8b3-ce79-4ccc-8e54-b63b31509377 | checkpoint | Are all leads suspended off the ground, plugged into an RCD and test & tagged in date?
99a0a2ee-0a2a-4f9e-9166-9d994b22b1c2 | checkpoint | Are the correct height ladders being used for today's tasks?
d508199f-4866-4c1b-b91c-1d97f39ba037 | checkpoint | Do you have the correct mandatory PPE on? (Hard Hat, Hi Vis shirt/jumper/jacket, Steel toe Boots, Safety Glasses, Safety gloves and Ear Plugs?
23bc914e-1fb9-5bfc-aa74-5d5737746b1d | textbox | Project Manager
b66c5a1f-e7b2-56db-9865-899d0527efc1 | textbox | Any issues from the previous day
764c2df3-2135-5eb5-a1a6-b926144cb845 | textbox | Any unfinished works from the previous day in the area of works?
c3fa7703-51b9-564b-8e2e-916f6d7a2940 | textbox | First aiders on site today
d9d7872e-cef0-56ea-b844-ce2d8042fdd6 | textbox | Who are you working with today?
5fc1958d-9098-54a5-9f9f-f6283bdaef4d | textbox | today's tasks / jobs
d74c1eac-8bd5-5a63-b843-d8b0617e6947 | textbox | Any unfinished tasks / jobs from today's items? (list the items unfinished & explain why the tasks were not finished)
87eeeed4-748f-5094-9c8a-55ed65e6e614 | textbox | Attendees
69acdbe8-b75c-4288-a54d-f10b21b1a0fc | checkpoint | Supervisor Signature
98ed0de9-27bd-45bd-ab0a-accd8dc4f6b9 | checklist | Drainage - First Fix - Checklist |  | Drainage - First Fix - Checklist
fb8349aa-a988-4ad0-9395-73552758db11 | section | Details
3dbc4c9f-bd66-4a16-ade7-5145cc17a7f9 | checkpoint | Setout and position checked and confirmed
6e630c63-492a-4125-a683-11ac1d8a8b29 | checkpoint | Trench width and lid level (attach photos)
87d46988-832a-46c1-ab18-26c655717743 | checkpoint | Gaps measured and ordered
4d488514-e1ce-4fc2-b33b-f988c4ed7c84 | checkpoint | Stockpiles & cart out confirmed
19a2243f-957c-4bc0-bfdd-d57f2228a365 | checkpoint | Pipework installed as per specification
d26feb06-c960-4477-aae2-cbba026b673a | checkpoint | Pipe test booked and test ready
0e0ba75d-4225-4197-96d1-0bde4b1c4b11 | checkpoint | As built plans complete
8e4298a4-c67c-46cf-9c8b-f4ae9ef2f6c7 | checkpoint | Clegg test on hardfill (results recorded)
8ab37cda-1526-41e3-8270-93576cf56e92 | checkpoint | Clamp ring and dome installed to outlet and overflow
3a79ef99-bf4c-4640-b3ef-331f368ce2e6 | checkpoint | Clamp ring and all through flange installed to outlet
88a436a0-595e-48ef-891d-993fec573774 | checkpoint | Stormwater riser installed to all through outlet
ee5eee3f-a822-43b8-afd0-0f7aa886bb18 | checkpoint | Pipework complete & ready for sign off
f3f1f9b3-af67-40ce-b8ea-9edd6ed690d1 | checkpoint | Area left clean and tidy
436ec468-8e3b-479b-8f53-6d7f3010fff3 | checklist | Drainage - Second Fix - Checklist |  | Drainage - Second Fix - Checklist
c2f47af1-9576-4228-8dd1-aec443637b30 | section | Details
eccba9e6-f3b6-44f8-b46d-6f6a18ad3c09 | checkpoint | Overflow terminated to underside of soffit
ea4bc244-f873-4629-8e4c-37ee120f8cb8 | checkpoint | Area left clean and tidy
a9a4c7df-e599-48d3-88ad-06232d0830a7 | checklist | Drainage Checklist |  | Drainage Checklist
e2c0e5fe-91d9-4866-85d1-dd6cf5409ce3 | section | Details
faf9581f-f517-45ad-8535-98f7e2ae0617 | checkpoint | Service
bb609138-0849-54ec-9abc-9a47da9aaff5 | tickbox | Stormwater
9b8bbee4-66af-5feb-9811-a12b524ec4cb | tickbox | Soil
a3c5034e-4e49-5d22-ba4f-09e548426775 | tickbox | Waste
3cc255be-75d7-5c4a-adf0-91ab4a7a4c64 | tickbox | Vent
9c43297c-0dd1-5400-a4eb-29303ce94e1a | tickbox | Water
f5e917ff-6623-5d4a-af72-e5537de712de | tickbox | Gas
1b0bb53c-ac12-54ef-b91a-702895bf922b | textbox | Other
66be09f3-fb88-428a-9208-4ef90c18c8dd | checkpoint | Details
fc93cdd2-7165-5cd3-9d98-8fb064f458a3 | textbox | Drawing N:
16e4c132-a10d-57c6-976c-cd9dd24ffa09 | textbox | Grid Coordinates:
22f3b93d-9d1a-5bbc-9a43-353f4f0981a4 | textbox | Issue:
6c4bec8e-47bf-5b79-b306-43268cc951bd | dropdown | Pipe Work Material Identified: | Scheduled, Specified, As Drawn
e348be71-6279-46fe-a722-ad72bae12343 | checkpoint | Drain Invert Specified
30a28a5f-a630-579d-a55d-3cdc4d513b2a | textbox | If Specified:
82cc7166-cf8f-4134-b4aa-86e6ad913cde | checkpoint | Gully Position Checked
8f0d927a-53e6-4bf5-bead-e0e974bd3622 | checkpoint | Falls Checked
98bfdb34-197a-4be2-8c59-0f5d80c37d92 | checkpoint | Drainlayer/Plumber Interface Points Established
a6f6aa68-9785-49e6-ab7c-971c0e104671 | checkpoint | Builder notified of any penetrations required to Exterior Walls, Beams etc
26cfb3cd-3e4c-4e84-88f3-aa1fd44bc62d | checkpoint | Grid lines obtained from Contractor
d8f6dc63-1905-4e97-87d7-acdcff562e61 | checkpoint | Grid lines obtained from Drawing
b2b46a87-35ea-41f7-ae5f-fb3ebca716fe | checkpoint | Invert Levels
7b40541b-1fac-56bf-a8b2-ea85c429ca57 | textbox | Start:
1fa98362-6b56-5846-8310-e6a282815233 | textbox | Finish:
962b3743-51f4-435e-a1bc-fafcc3e447a2 | checkpoint | Floor Levels established
312616f8-82c2-4489-b4b3-5c2e1ac9a34b | checkpoint | Pipe Tested for Water Tightness
cf583be7-feb0-5544-a561-b0665892b2b6 | textbox | Specify:
e31f8a1a-6089-4758-bbed-8feea34df4d5 | checkpoint | Pipe Tested
d3415f1c-2a30-528e-a8b5-fbe1b5050776 | textbox | Witnessed by:
9677bbd0-162d-4dbf-ace4-6377aa96f945 | checkpoint | Inspected by Council and Passed
c1aa2106-cbcf-4a30-8cdc-946ce115619c | checkpoint | Council certification Attached
8459d4c0-83ab-4ce4-abad-50cc871fa2c2 | checkpoint | Pipe Work Trenches reinstated
bdcc9456-fbfb-4770-92b8-39e172cad600 | checkpoint | Open Ends Pipe Work Capped Off to prevent ingress of Dirt etc
96ae8003-a540-4560-999e-2cc46b88b5dd | checkpoint | Installation to AS/NZ 3500.2.2003
66e22209-a728-426c-a949-d60ca104a56b | checklist | First Fix Plumbing - Including HWC |  | First Fix Plumbing - Including HWC
63c4cf16-ee73-4a3d-afa5-a98236adc3cc | section | Bathroom
b5700cc8-c287-485e-9cae-57bbd9e883b7 | checkpoint | W.C Supply
a6c59106-8e1a-4202-a219-1837d3b6c2fb | checkpoint | Shower waste
3dd3d0c1-edee-408e-a4b9-84d3bd6e4e9a | checkpoint | Shower mixer/check depth
19b6e571-38d5-4b80-b1db-d7cab891514d | checkpoint | Toilet waste
7950a6b7-0630-40e5-8c4b-8d52f1a82f93 | checkpoint | Vanity Waste
43aa3927-50c5-4f46-80d2-3f2a4abcb424 | checkpoint | Vanity Wingbacks
0cbc5d6a-61a7-4933-b90c-5be5bbf9c766 | checkpoint | Vanity, shower, toilet nogs
f5b5aa1b-b132-472f-ba5e-a8c0895adf07 | checkpoint | Bath mixer where applicable
b0c6cde5-abe8-4685-b066-0e01b9710941 | section | Laundry
c7753ddd-e6ef-4685-8d3e-be9cf5066540 | checkpoint | Hot and cold water
a73ff9ac-1853-4e4f-9c11-ced7f6fb2594 | checkpoint | Waste pipe
64ca8997-0077-4222-b2a3-17f515b0b429 | section | Kitchen
0158d502-f13c-4123-9d9d-44cbe50eefe3 | checkpoint | Hot and cold water
197a3e30-5ea2-46f8-a247-94c5a2670f3f | checkpoint | Waste pipe
30e3228b-eaad-4395-ac87-06004fb9c52b | section | Balcony
50548c15-ee3d-4222-ab73-5e1a1739ce6b | checkpoint | Balcony drains & pipework installed/correct screws in flange
26761984-7745-4d0f-981d-a4fabf20d4f0 | checkpoint | Correct screws in flange
4ed62386-fb57-4055-857a-d071e0cc22b5 | section | General
09079f98-f00f-4b04-9e9f-6a8cc84e7c2c | checkpoint | Pipe Work Clipped
db87913d-d2ef-4a56-adac-10cce08d5549 | checkpoint | HWC water feeds
9ee5b920-55fb-48bd-84e8-d9d86f101323 | checkpoint | HWC waste
74ab4e79-6b2c-4a77-8990-cbfa859f6877 | checkpoint | HWC nogs for strapping
71934006-d225-4b74-8c9c-b5c13883fb5e | checkpoint | Pipe Work Siliconed
b0c73825-ace0-47c2-918c-27a61898e7b8 | checkpoint | Capped Off
115980ba-0d86-4342-8348-34e821a4ce61 | checkpoint | Check for Crossovers
6fcebabb-e1de-4c71-bcbd-ec98723c7d13 | checkpoint | Double check all sefont of fixtures
66eb5437-2457-4bec-968b-a98043ce1454 | checkpoint | Acoustic lagging where required
1a00b7f1-73bf-4378-879c-6c72cf3298c6 | checkpoint | Thermal lagging to hotpipes where required
d2e2c0f5-b489-419c-be9b-2e7844b35323 | checkpoint | Floor waste flange fitted
322b9a64-b975-49da-913b-388fbd57a995 | checkpoint | Pressure Test 1500 KPA
15df7788-6c36-4306-bd46-b9953d8ee5c5 | checkpoint | Installers name & date works completed
751cdb42-243a-5308-bc21-aa8bfa7bad0e | textbox | Installers name
06ab52e0-5501-57b8-b389-ab1ff063ae44 | textbox | Date:
8614f5e3-8700-4454-9066-0844f0bd97aa | checkpoint | Tested by & date
1ced064f-2642-555a-b422-3c432843e074 | textbox | Tested by:
94be68ec-6985-587d-a341-5968be9956c8 | textbox | Date tested:
3bd0e1e1-45fb-4ce4-970c-d95128d76ef3 | checkpoint | Council inspector sign off and date
f3f54d37-1e32-4253-88b6-4e3393e4c791 | checklist | Gas |  | Gas
b4594f5f-5f8a-401b-b422-18ef9fa32e0b | section | Details
34ffd8a9-3650-407a-8ca1-ac24de12785d | checkpoint | Setout & alignment as per drawing (include revision below)
d746c7ea-57d2-5396-bae2-314cfd519c7c | textbox | Drawing & revision number(s)
bd81c613-510e-47fb-a1c5-dda22d75fa29 | checkpoint | Material type as per approved sample submission
99c2203b-4be8-4d71-a510-940dab8986c0 | checkpoint | Welding, press fittings, witness marks visually checked
162883fe-0b2d-4218-b8ef-def6d29b8d63 | checkpoint | Supports & fixings to ESV and WPD standards
a8bf3614-ccfd-404d-95db-4f98cb8e8ed9 | checkpoint | Pipework installations to ESV standards
99ef3f8a-e509-41b0-8a8b-85313abc124f | checkpoint | Penetrations, fire protection, wall sealant installed to the BCA requirements
e0bd6ced-dd08-4b59-aab3-0d26f5788d68 | checkpoint | Witness marks / labels / tiger tape / kpa signage
30bf33e6-1a60-4a3c-a1e2-127168df6052 | checkpoint | Pressure test (as per AS/NZS 5601.1)
218c6d90-a808-4b04-88f2-6ef512c58918 | checkpoint | Test appliances (as per AS/NZS 5601.1)
dd1b5592-2274-48dc-9be9-25c979a95619 | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
ced2746a-748a-5100-9624-6b134cfc33eb | note | Passing above includes Builder sign-off
20adf305-ac2c-5a11-86d5-d4e0fe95c85c | tickbox | Area clean
042ca033-ea09-44a5-935f-c7e540665194 | checklist | Gas Checklist |  | Gas Checklist
3ca9bada-a85c-4adc-8526-c1ac0f24ef16 | section | Details
a0c3d4e5-a4f7-4de1-82ab-8e77a8771db6 | checkpoint | Setout & alignment as per drawing (include revision below)
ec6f2b10-7c8d-5809-bc9a-f1d8f42131c4 | textbox | Drawing & revision number(s)
43f06ab0-e7f4-4a43-af05-56d2aee58cf8 | checkpoint | Material type as per approved sample submission
b86dd28c-d1ce-47bd-b123-ece05ab4414c | checkpoint | Welding, press fittings, witness marks visually checked
2691b8d5-fcbf-4525-825f-e7eb4d09a059 | checkpoint | Supports & fixings to ESV and WPD standards
83d61a64-3323-408a-97af-f4ff5ae6e170 | checkpoint | Pipework installations to ESV standards
9fde945c-8b74-45e1-a4bb-7afc825f8321 | checkpoint | Penetrations, fire protection, wall sealant installed to the BCA requirements
62613d6a-0aa9-44be-baa1-87ab310baf0a | checkpoint | Witness marks / labels / tiger tape / kpa signage
3ea60c2c-63f2-44bc-b00f-f0490447430e | checkpoint | Pressure test (as per AS/NZS 5601.1)
7bb629e5-dfcc-49d9-a623-5b79fa38ce94 | checkpoint | Test appliances (as per AS/NZS 5601.1)
9da3bd88-cae2-465f-b22e-8b995cec3017 | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
58d79361-cc88-5abb-982b-aa8402117fea | note | Passing above includes Builder sign-off
e8db9cbc-acc9-5401-a695-67e8be7dc40b | tickbox | Area clean
dc28780d-1bc6-4dc5-a151-d895f51a29fb | checklist | Gas Test |  | Gas Test
fd4f20ce-1f83-4d3a-b402-3b78ece48f77 | section | Details
a77746a8-72d1-4a8d-9fa8-4cc83c19745e | checkpoint | Details
8e715c89-d3ab-507c-a8f3-6f0a7e733c2a | textbox | Location
eed86805-f3e3-59c2-adfe-9ac4124d1f26 | textbox | Person Responsible
85d6afe7-92eb-4ae8-8a18-1523d12575f8 | signoff | Gas Certifier (Name, License Number and to sign off)
44dd65e6-b85b-4202-8ced-f348d8409231 | section | Pre Install
15074884-37ec-4e85-9492-2ed33807c783 | checkpoint | Service
9027bd15-c2cf-505c-9dc8-5d8906b09cf3 | tickbox | Main
503f4107-ed32-54d5-bc19-519c4c007764 | tickbox | Reticulation
93963b9c-5fb3-4e57-b7b6-4b669891991f | checkpoint | Pre-Installation
3a52fad4-766f-5fc9-a8a4-4af30c1328ee | textbox | Drawing N:
bf12bbad-950b-5419-ab54-d552812cbbb3 | textbox | Issue:
86396258-f917-59c2-9d75-59369239b760 | note | Specification ref: AS/NZS 5261;2003
22d48d43-38ed-5963-95d4-d53448dca829 | textbox | Specification Clause
c2f178ee-646b-50f1-b706-13b6b2188892 | dropdown | Pipe Work Material Identified: | Scheduled, Specified, As Drawn
835bd723-e575-51d8-8e8b-d1fdcbf25863 | dropdown | Test Required | Water, Air
08b048c5-cd22-4369-a1ec-231e46921881 | section | Test
c7d73348-eb6e-4ee2-a480-57e1ea48f9a4 | checkpoint | Tested to AS/NZS
58f91da7-e727-5a4e-86b9-8ba4ad458788 | textbox | If Specified:
65b2e87c-0be3-5c7c-b1ed-dbc0e42c96ae | textbox | Start Time:
a2f31137-de68-59ad-b928-d979a20d07dd | textbox | Finish Time:
9e97d349-e7c6-5be4-81d4-aae1f14a0040 | textbox | Test Time:
26722565-66a2-584c-b789-421f9d406323 | textbox | Start Pressure:
2b3f7087-3365-5b61-b81f-f2e6cf51b075 | textbox | Finish Pressure:
527a32df-6309-490f-a2df-534dcb4d9207 | checklist | Generic - PVC |  | Generic - PVC
d8771dfa-1769-4857-8978-453fdf468e95 | section | Details
2e029281-9bdc-4e6b-9ff5-f40049798ae4 | checkpoint | Waste Pipeout
3dd3e6c0-b2c1-42cd-b15e-aee35f7a3e05 | checkpoint | Vent installed
3021b363-3ec0-4d49-8e0d-5a0acb1b63f3 | checkpoint | Check sewer hasn't been connected to stormwater.
e0312743-bb3d-4f8a-bcda-0773795ae899 | checkpoint | Correct or exceeded minimum fall
27b6313d-901f-4933-aa4d-8bd041f38c74 | checkpoint | Correct Clipping
ba9697d3-acb9-4161-a13b-256e6ec3f999 | checkpoint | Flood Test in accordance with ASNZ 3500
9c63cbd4-cf60-4884-9bcf-21fed191e411 | checkpoint | Hydrostatic test Plug Removed By
31f5588e-3fe6-4156-959a-e643cf62bd0d | checkpoint | Inspection Cover Replaced By
1f311eb1-60df-47e4-8fcb-fb69fcff9b54 | checkpoint | Seismic bracing for pipework, longitude & lateral
95ae1b28-4b04-4417-89a1-fe49db1ffc4c | checkpoint | Pipe labeling
ef1db4a2-b785-4519-8005-ca9a40a41a3b | checkpoint | Access points for cleaning
4b87b6dc-66fe-425d-b0f4-08c1d9b8529c | checkpoint | Acoustic lagging
592dde8b-4397-4161-b82e-d75f24d01ef8 | checkpoint | All pipe stubs covered or capped
f17584f1-55d1-4ee4-a638-8c5b0999ec21 | checkpoint | Installers name & date works completed
d488ffef-13f4-5026-96c5-b58df3199da2 | textbox | Installers name
1dc3676e-c6b3-5f88-826f-c212ad24fba4 | textbox | Date:
6ce7c589-3c5b-4fb4-87ee-c17ed967f3bc | checkpoint | Tested by & date
ba51ce97-77fc-5c6b-80a7-13bb0baa171b | textbox | Tested by:
ef393b7f-2c12-5db2-ab7e-739e7375c5b2 | textbox | Date tested:
2619e157-af27-468d-8251-f010fb3e89ae | checkpoint | Council inspector sign off and date
16142d14-2032-4981-be31-6eab0b45f24e | checklist | Generic - Syphonic Stormwater |  | Generic - Syphonic Stormwater
ea4f12ce-73d8-4b06-8bc7-ff9ffd1b684f | section | Details
58129b30-4f63-4144-87b2-91b55accae33 | checkpoint | All pipework installed as per design drawings
e185ab9b-1eab-4464-86dd-3bca2b7aef95 | checkpoint | Fittings scrapped and ISO before welding
4c0b4f8f-aa18-4dfa-88cb-972e564f8edd | checkpoint | Correct fittings used
53d92c2e-048d-44c1-8c67-8fe334d1ce8e | checkpoint | Brackets and clips installed as per design
0fd110ea-bfd9-49e7-aec8-bdc6734078f1 | checkpoint | Seismic braces installed as per design
2fd9baed-3ab9-432e-b970-f69db5587715 | checkpoint | Outlets installed and syphonic grates installed
7e468284-418b-442a-b416-2b180988f17e | checkpoint | Overflow outlets fitted with riser fittings
c2bde279-4f0f-4fb8-ad85-7de3d1a8e823 | checkpoint | All rubbish removed and materials back in storage
b49c4c8a-86b1-4823-a845-abf92c518e5f | checkpoint | All pipework flood tested
10423117-651d-48c0-9276-91d3051923d2 | checkpoint | Installers name & date works completed
09cf2a61-6b67-5615-975a-d554ce93d69e | textbox | Installers name
31c6ca79-740a-5a58-9d9a-6244e2bee5a5 | textbox | Date:
95464a60-d7b2-4d7e-bedd-3bb4847bb1fd | checkpoint | Tested by & date
df32d726-8f15-5266-9295-13b8b4ea3bfe | textbox | Tested by:
1f51771f-097b-59e7-8d7d-18d5b9acefaa | textbox | Date tested:
c0ec6aaa-5a5c-4257-9093-927ca9018af4 | checkpoint | Council inspector sign off and date
983e32c8-f877-4ddc-a367-ffa8de151e6a | checklist | Guest Room - Waste PVC |  | Guest Room - Waste PVC
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
722ab1f6-86fe-4bca-99ac-0e147bcde35d | checkpoint | Details
53bf91fc-2f51-5a6e-8b7d-581afa1aa902 | textbox | Guest room Number:
ff92c04a-5757-4427-a1d6-08e232bfabda | checkpoint | Waste Pipeout
7e35d705-e2e0-4a29-b304-9f3c6ad217f5 | checkpoint | Leak control flanges installed and recessed to floor
4403db2d-4f43-447b-82d3-23e33a44f194 | checkpoint | Boss junctions drilled correctly
d7a94029-96e2-45c5-9493-10cb58ac5094 | checkpoint | Vent installed
c766fae0-8487-4535-a4ad-93b6f47c97b6 | checkpoint | Check sewer hasn’t been connected to stormwater.
fc20afb9-05f2-4484-a263-17587a264f81 | checkpoint | Correct or exceeded minimum fall
d22a16a6-8005-41b1-a62c-558549b008f4 | checkpoint | Correct Clipping
72187297-a6ae-4437-b4c2-ef64f9db2cdf | checkpoint | Flood Test in accordance with ASNZ 3500
f75786b4-fc6f-4a51-a479-69cb0e523a03 | checkpoint | Hydrostatic test Plug Removed By
03a351cf-1eb6-4847-81da-2dfa15afb07d | checkpoint | Inspection Cover Replaced By
03e23716-5fcd-41e4-b123-f72c28aa7117 | checkpoint | Seismic bracing for pipework, longitude & lateral
6ab709d1-ce77-4dca-9af3-e965f9641feb | checkpoint | Pipe labelling
23d08044-a223-47c9-aebf-9e0dbdd7c2e0 | checkpoint | Access points for cleaning
12e20a1d-d1bc-4b62-b2ab-199eb73a1959 | checkpoint | Acoustic lagging
370bb2af-e5cd-48db-a057-9983adb6e280 | checkpoint | All pipe stubs covered or capped
0f0abd9f-c8a0-44c8-8a41-66adf5f6bf0b | checkpoint | Installers name & date works completed
9ff94efc-087b-56b9-a876-1ac5c97d20fd | textbox | Installers name
00c14f25-6b38-58ac-9201-980053ab74f9 | date | Date:
59f2acd6-6623-4e01-aff4-553ed65091bf | checkpoint | Tested by & date
866bb38d-cf7b-51bb-8f21-a6fee4b1979d | textbox | Tested by:
8fe8d8ae-d222-5527-aa4f-5b2666ec80e1 | date | Date tested:
7c8f00cc-f104-4615-a083-0b7e9e34845c | checkpoint | Council inspector sign off and date
2d084520-c1c3-44b9-8177-b56d8ff4adcb | signoff | SIGN HERE OR REQUEST SIGNOFF
d2f9b665-4ae6-4be1-8df6-d4c1ed452388 | checklist | Guest Room - Water Rehau |  | Guest Room - Water Rehau
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
bb44e45b-f53e-4d66-b0b2-c50b57fd37ab | checkpoint | Details
0fa5673a-5404-5289-91b1-346abf74b960 | textbox | Guest room Number:
b9a54ac7-5c89-4db7-bfa0-a44f269636ef | checkpoint | Water Pipeout
7f1321fc-e348-4eaf-9461-d9dde459d5cc | checkpoint | Correct Pipe sizing
f41b3afd-a394-48ee-a30f-d8b7cbc19116 | checkpoint | All pipe work crimps checked
33adbe60-e444-4e6c-83c8-0fbcf9511d06 | checkpoint | No Cross connections
48b85a74-99fc-45ee-a904-8d7fd0a817a6 | checkpoint | Shower Mixer at Height & Centre
4e8d8d45-e183-4c66-8c73-649671cd455f | checkpoint | All fixings installed - Nogs
d9410a41-eb8d-44b8-b643-a3349ae606b4 | checkpoint | Toilet Inwall Cistern Fixed & Secure
d8464881-7b89-44de-ab15-45c4587f4f35 | checkpoint | Toilet waste & Flush pipe centre & at Height
57299d7e-7c04-473c-8a4f-1212729b3520 | checkpoint | Guest Room Isolation Valves Installed
8bc92e22-99b0-4520-86c7-f831d0b968f7 | checkpoint | Pipework Clips & fixings installed
3139b767-c00a-4941-8fd5-b1df221f3502 | checkpoint | Double check set outs and measurements
464db29d-d2f9-4e35-bc0a-5cb73775c599 | checkpoint | All test plugs installed or capped off
8f2a445f-c10a-4224-8d59-9bf5093f89c4 | checkpoint | Shower mixer removed for testing
98466b14-0890-4bef-abec-f2248daa2023 | checkpoint | Pressure Test 1500 KPA
520181bc-152a-46ca-9197-65aa1a383a2a | checkpoint | Re instate shower mixer into position post test
cc7a0637-ad28-45ec-9af3-08b06232442a | checkpoint | Pipework siliconed and secured
59816f77-5512-4869-8e21-3c34645cf0ba | checkpoint | Area cleaned & rubbish removed
bc684ba8-03a4-4d0e-95d5-a002315f9d65 | checkpoint | Installers name & date works completed
c56c4f00-70ff-5b4c-b8ca-8dc0c9486264 | textbox | Installers name
782de8a4-4b01-5a33-8314-e2aad79f2348 | date | Date:
23300a47-81b5-400b-bd89-f77cf33e1b98 | checkpoint | Tested by & date
4d1cfd12-4fda-5fa1-912c-98010cd0bdcd | textbox | Tested by:
c0bb7e0b-0256-5cca-b839-8b31f871341a | date | Date tested:
b8ee7d65-d37b-430b-b544-36c743e7707d | checkpoint | Council inspector sign off and date
cf71a4db-12cf-4cc0-b36a-c4fb23009a6f | signoff | SIGN HERE OR REQUEST SIGNOFF
81cf6ad5-6c20-486e-8aa5-1261782fcb79 | checklist | Hot Water Plant Gas |  | Hot Water Plant Gas
c5dbd762-d92d-46e5-8839-9c88d6388db0 | section | Details
fa144bf2-5854-4105-a6f0-3bee686ab842 | checkpoint | All strainers free and clean of debris
e2b65e1f-00cd-4ea0-a9c0-e3022b51ddbf | checkpoint | Infinity units serviced
1ca45712-90c1-4749-a281-45d3b3e3ddc5 | checkpoint | Infinity unit serviced date
548608ee-0b3f-4eed-ac1a-a47180f27f8d | checkpoint | Efficiency test
39f920e1-b2e3-54ce-8bf8-10a0029e61c9 | textbox | Result:
abf29726-1816-43af-84b3-9443d4b1e157 | checkpoint | Gas soundness test
980fefa5-731a-48a4-9400-c67314eb979e | checkpoint | Reticulation pump operating correctly
fe693e44-170e-46c3-8550-9972b25cee23 | checkpoint | TPR opening and closing correctly (replaced if 3 years old)
78f429e7-8090-4b58-88f1-3037a963dc78 | checkpoint | Cold water expansion opening and correctly
e0691a39-4f39-4f0d-a326-0c2ede5a3db5 | checkpoint | Incoming Pressure
fd02c54a-a7cd-5ae7-b6ac-8e0a438fc4f7 | textbox | Pressure:
af86fbac-6670-4b2a-8450-0840cd0daeac | checkpoint | Tempering valve if installed ok
a2a134e6-0570-482e-b2ac-89a53898f6ce | checkpoint | Temperature at thermostat and tpr
9457341c-2c00-5158-b313-0e55748c9f57 | textbox | Temperature:
9d721a97-6438-4e45-bb10-365d8f55a207 | checkpoint | Water dump and Sludge clean out required or recommended?
15bdcffa-bdc7-4861-aa62-c6985866554f | checkpoint | Seismic strapping tight
64f99dda-b8cb-4ed4-a18c-b87ffec3b234 | checkpoint | Pipework Free of leaks and corrosion build up
bdc484e8-855b-4175-9236-c96ae1715f2f | checkpoint | Ball valves opening and closing freely
a2eade46-92fa-44a7-bc1d-89c51ee466e4 | checkpoint | Tray drain clean of debris, free from damage (i.e. Cracks Etc)
00393111-9da7-494b-849d-dff28e323deb | checkpoint | Visual Check
a8fae48d-48b8-4047-a0ac-16a8b792250e | checkpoint | Additional comments & photos uploaded if necessary
24322277-86a3-55d3-8239-dfe2d7061ce3 | textbox
ee9487c7-4b86-4f02-a52a-f0f566dab482 | checklist | Hot Water Plant Room |  | Hot Water Plant Room
c2684a1c-3313-4e17-a194-6f3243acaa7f | section | Hot Water Plant Electric
395b84fc-32e6-4cc4-8597-c92a21c0d1df | checkpoint | TPR opening and closing correctly
08be9695-68b8-424c-a418-4864a78fd72d | checkpoint | Cold water expansion opening and correctly
7384f22e-0dda-4124-b8d2-26c1d97fcd91 | checkpoint | Incoming Pressure
992cef31-9b87-5a69-9233-f173ae5a6cf9 | textbox | Pressure:
f3c95cbd-a5c2-4d7b-bc9d-3618261097ae | checkpoint | Thermostatic mixing valve fitted
357e50a8-1c21-4a7b-93fd-3e5a10db993a | checkpoint | Temperature at thermostat on HWCs
767e65a3-1eed-5d2f-a60d-489e45d506d8 | textbox | Temperature:
12321af0-1e65-4d25-8cdb-4f4232a23232 | checkpoint | TPR Pressure rating
886d438a-6c1d-52b6-b5d4-9b59edc26d8c | textbox | Pressure rating:
632750fa-63c4-427d-b6c4-02edc5951496 | checkpoint | Water dump and Sludge clean out required or recommended?
165f2554-1fdb-454f-a0a2-b63b06ca714e | checkpoint | Seismic strapping tight and in all three locations
62a77fb2-858e-4e48-90a7-b5b7e7fe92c4 | checkpoint | All strainers free and clean of debris
f7424075-baec-418f-928d-a0e6bc285729 | checkpoint | Pipework Free of leaks
efd5893f-010c-4841-9c11-9980b116fc12 | checkpoint | Valves opening and closing freely
c2d188ca-1290-4fe8-b211-610e84398c08 | checkpoint | Reticulation pump operating correctly
82de0fc5-c07c-4d2f-9b82-7964835aba8d | checkpoint | Tray drain clean of debris, free from damage (i.e. Cracks Etc)
35d32f89-19a8-4b2b-84b8-83ad29dc7312 | checkpoint | Visual Check
8146aa8d-e1cc-4f23-97f6-4f26686d5ab7 | checkpoint | Additional comments & photos uploaded if necessary
9f2885fa-c8f6-400a-9d4f-22e6bbabf4a7 | section | Hotwater Plant Room Components - Pumps & Tempering Valves
ed36859a-e0aa-44f2-9afa-d6cf7ca6534b | checkpoint | Flush all lines and strainer including
3128e40d-050f-4829-8014-b8713a2fd3cd | checkpoint | All safety valves installed
eefc4c20-4317-44c2-b26c-a8e6022680ea | checkpoint | Relief drains fitted
292c58d5-6f18-45e1-82a8-56c4c5e7b2ab | checkpoint | Relief drains to tundish
3b5a80c1-6977-4b5e-96e4-c2f999467562 | checkpoint | Check All Connectors For Leaks
91548936-48da-4366-8e92-d8f3f5750cda | checkpoint | Check all valves and connections for leaks
84ba5741-abf4-4b20-b03d-afdb096d5838 | checkpoint | Operate cold water expansion valves / check operation
4e458770-5cc9-46ef-b2aa-55984d20aa0b | checkpoint | Set limiting valve
4d6a2ef3-ce2d-4e98-97e3-46975ccf5c5a | checkpoint | Check for crossovers
ec1b2217-e1b1-4278-a9e3-775946c43b30 | checkpoint | Check HWC For Correct Valve Installation
6aec8817-fc37-4ccd-b135-d89b4b5b73ee | checkpoint | Lagging completed
93bab349-cd48-4b4d-a194-ec7d491580a6 | checkpoint | Check All Hot/Cold Pipes For Correct Position
78d92264-50c5-461d-b658-2110add3c98c | checkpoint | Bleed air from circulating pump
b09f1e0c-45d8-464c-8307-767621e0e8a0 | checkpoint | Set all return thermostatic balancing valves
5dc43ad8-dde4-4b5b-95cc-d8d9c26db2d4 | checkpoint | Installers name & date works completed
9823cde0-93be-5a24-acfb-7a3d49000df8 | textbox | Installers name
bd3e23f2-50c8-5cbf-9461-2a290ddb2797 | textbox | Date:
ceb36fec-c4c6-4637-9bb4-e607cda784e9 | checkpoint | Tested by & date
0facc6ca-c797-5caf-bbe7-23b74f23c33d | textbox | Tested by:
fb3b259d-e378-5e7f-b247-224d0639c5d8 | textbox | Date tested:
3dff3e80-a849-45ff-9dec-fe61e520350c | checkpoint | Council inspector sign off and date
1e2f0a5c-7cc6-450f-bb93-09581bc829fe | checklist | In ground Watermains |  | In ground Watermains
bf1cd796-23b3-4171-a0e8-95680c9dff80 | section | Water mains
ed2bd6c7-9744-44f0-9577-d120d33ce713 | checkpoint | All fittings scrapped correctly
e39e7536-b198-46ea-9c88-6ed2ac20b190 | checkpoint | Iso used on fittings
5e8222fb-18d3-4fc5-bd85-5be70b16c00e | checkpoint | Valves fitted correctly
fea75df0-a655-41f6-b9ad-d1841279b126 | checkpoint | Fittings welded & weld indicator has popped out
bacb91d0-fb1c-4cae-ac6f-12e771ef185c | checkpoint | Trace wire and ID tape installed
da5750a6-5b7e-4abd-84f4-76639cf0e675 | checkpoint | All open ends capped
de9fae58-ba53-458f-a8c9-045a2a52a34d | checkpoint | Pipework bedded correctly
e6feb794-5cd6-43d6-abd2-f1d34413c9c7 | checkpoint | Tidy work areas
827caabe-ee4a-4bfb-98ac-3230cdc1d8ec | checkpoint | Pressure test pipework
72bcc79f-bd75-44db-aa83-aa5ce338868c | checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
11f20143-735a-4aa0-8135-929566f96fd4 | checkpoint | Backfill around pipework with fines
5c7ab1d8-1a87-49dc-9881-05c96b960e83 | checkpoint | as-built completed and photo
9f144da9-8cf6-4149-9643-61a72296782e | checkpoint | Installers name & date works completed
35d6a821-01a8-5613-b96d-233326aa9f88 | textbox | Installers name
a8323c29-7a8f-50bb-b876-20a5ed00b4e4 | textbox | Date:
53557a5f-6780-45dd-82ba-1146103d6d84 | checkpoint | Tested by & date
8002651f-9a5c-50da-9c9e-b4541d268d0c | textbox | Tested by:
e5322783-e8d4-5335-b7a9-35f35d29a848 | textbox | Date tested:
d857e51f-477b-4081-b3d6-b938a9b9c8f8 | checkpoint | Council inspector sign off and date
5a2064b7-1c97-40c7-88ad-6726a90236ac | checklist | Manhole Checklist |  | Manhole Checklist
d52931e1-7aa1-4464-8f4a-624530f5639a | section | Details
5125ecf1-655a-4e37-b148-0dd618c6f82b | checkpoint | Check Existing RL's Of Manhole
295461c4-d53e-4aeb-8ea4-a25959d309ac | checkpoint | Check Invert And Grade
68a282c1-8257-49ec-943f-04820a32227d | checkpoint | Seal Pipe Into Manhole
625939c9-1c61-46a3-b687-f4c83b4a5ca9 | checkpoint | Install Manhole Lid At Finished Height
d5740588-e810-454e-af31-bb80c1d935d6 | checkpoint | Benching To Be Complete
697036a1-1e15-4b99-992f-86e0af1976ae | checklist | Pipework Checklist |  | Pipework Checklist
368487b4-6961-4f9e-9cdd-bc8587fd80e4 | section | Details
e55735e9-26f6-48b1-ba98-b553276d1c29 | checkpoint | Bedding Put In At Correct Height
175a84d1-8123-4640-9a8d-1874336aea65 | checkpoint | Grade Right
683e1b7b-c17c-4ec5-8574-76cfb0793605 | checkpoint | Check Pipes Is All The Way In
4b0a5471-3712-4e46-b801-c88f4a1ec3ce | checkpoint | Check Pipe Connections (No Gaps)
fafe4f35-01e6-42fe-9e98-a3e24bdf6c92 | checkpoint | Compact Around Pipe
3f689ef0-ab06-4c19-a0f8-c1c0ea281347 | checklist | Plumbing & Gas - Second Fix Checklist (V2) |  | Plumbing & Gas - Second Fix Checklist (V2)
21add3fc-0cb8-408e-bfa9-2e9d5705ac3a | section | Details
574e9a5b-b18f-47e8-92f4-f3441bb8289e | checkpoint | Check all fixtures are connected or isolated
cff99de6-344a-402d-8968-04234300a7ea | checkpoint | Turn main cold on
f36d7aa6-23f7-45c5-89dd-c0e03492b805 | checkpoint | Clean out aerators
606a6622-5d3d-47cc-83d5-046d086d9b19 | checkpoint | Flush out each mixer approx 2 min
0e87bf07-6ffd-43ac-9dc7-ab0fc72b38e4 | checkpoint | Check for leaks
d1f65a59-8c45-497d-a5d0-69c7656f1865 | checkpoint | Check all flexis, croxs, traps, pans for leaks
3f48e317-07b4-44a0-bf84-d49aff9e9ed6 | checkpoint | Check temp valves for leaks
10704651-1b0d-44a8-b35c-c0580f9b4645 | checkpoint | Final check for leaks
b9c251c2-8b43-4617-9e7d-bb1a9ac01e32 | checkpoint | Silicone applied correctly where relevant
0e9809df-9695-4533-87ab-8cf7b0dfe600 | checkpoint | Check and set temperatures
68b6fa2f-df08-43ff-a3d5-86aa5ed22740 | checkpoint | HWC is seismically restrained.
4823913a-b7b5-4e71-b6f9-ffc28ca19967 | checkpoint | Electrical is connected to HWC and cylinder is on and up to temperature.
f0db9972-0bff-44f6-9a54-98662ac40ed9 | checkpoint | Photos
371c0eeb-8f94-4ceb-a0f4-3bc1ad91e6ac | checkpoint | Second Fix Complete
8f412f0f-bc94-417c-8650-0360106904f6 | checklist | Pressure Test |  | Pressure Test
e4379b3c-2e59-4d6c-a7c5-1d351a24981e | section | Details
6d789748-f37b-48d1-b858-3a9e6663b3e8 | checkpoint | Details
c734b81c-a21f-58f6-afd0-d94887eb46eb | textbox | Guest room No. & Location
515f0780-5bab-480c-9d16-c11f003d46ff | checkpoint | Service
cf083094-4f12-54fc-a264-0fad6473aad7 | tickbox | Soil
e147968e-bf99-5499-a9e7-7f8f00daaef5 | tickbox | Waste
505c22ec-b408-51f1-8a84-87c39fe8aa68 | tickbox | Vent
bf6686c6-881a-59fa-9811-8177c9c00264 | tickbox | Water
e990eb2d-3c52-5e80-b515-6ee5b3c6590a | tickbox | Gas
d8979c75-b9c3-5e37-8c6e-f6e5fd93f16d | textbox | Other
2b3f397e-2651-5891-bfbe-663719ea19e1 | textbox | Pipe Work Material Identified:
dc00c773-1e1c-5400-8ee3-0bf61e566b5e | dropdown | Test Required | Water, Air
fdd1634b-e557-4a9b-b1e1-702a64977fce | section | Test
4ec17998-e13f-4c56-a101-e1827ab3b17f | checkpoint | Tested to AS/NZS
afc29820-023b-5282-885f-d33cf5e129e7 | textbox | If Specified:
8a6de25a-048c-5a8d-ac5e-e0a995119d87 | textbox | Start Time:
bd412272-1cb8-5f62-8b2d-b966f2b64ae9 | textbox | Finish Time:
1fae7a1a-d4b3-5722-be28-9611eed4ff25 | textbox | Test Time:
29f09aeb-9ea4-5a97-b10f-92ca92046475 | textbox | Start Pressure:
84b6f9ca-8b09-5e6c-a266-8d170c0d1c89 | textbox | Finish Pressure:
fd084480-375b-4ad3-bc0d-a6b40bb98715 | checklist | QA - Plumbing Fitoff |  | QA - Plumbing Fitoff
0681b017-7731-4948-acbf-443663e8d8b4 | section | Area readiness
e4524ed7-d96a-44e5-adf4-22007f4d69de | checkpoint | Is the area ready for fitoff?
bc32d131-1611-445e-90d6-13eb515b599b | section | Wash Hand Basin
2b7e189b-1baa-4fd0-8756-d7760529e472 | checkpoint | Wash hand basin is installed
8e873d08-22e2-4d5e-8a94-47fa6a25c612 | checkpoint | Basin level and secure
d584f736-cd87-4de8-b531-613ac748d7ec | checkpoint | Waste connection watertight, plug supplied
83588e33-7137-467c-952d-029801be2c09 | checkpoint | Water connection watertight, tap secure
e2e425e4-9d30-4b24-b14a-0b620552950a | checkpoint | Hot & Cold waterflow satisfactory, no water hammer
d95c3c0b-c42d-49f7-8b8f-0cb4c375d6d6 | section | Toilet
8b04dee1-0814-4189-bd45-3a2e094f4bb3 | checkpoint | Toilet is installed
7664aaaa-dcdc-40f7-a419-0097e804e62c | checkpoint | Securely fixed, silicone at floor
d8b38202-d760-4edb-9153-56a10157e114 | checkpoint | Flush and cistern fill operation checked
4ed60f9a-c66b-4680-8ad5-eacadad13d34 | checkpoint | Water connection watertight – cold water
7158d17e-2224-4e2f-b0d4-72edc50a728b | section | Shower
5dd94d52-ba7f-40df-b2cb-de1d3da601d7 | checkpoint | Shower is installed
13acec04-6225-4d7e-9ac8-193abe6a2279 | checkpoint | Hot & Cold waterflow satisfactory, no water hammer
819f6346-90ee-4f84-ba91-9ca47b2a148d | checkpoint | Waste clear
e7a72176-45a5-4a32-b4d3-9b4f170c66a7 | checkpoint | Cover plate fixed securely
c0636fb6-83ee-4972-a8e6-b011eb77431a | section | Bath/Shower
a28bfe71-a99d-45ac-8fbf-0b7ec4cbb230 | checkpoint | Bath/shower is installed
1c224278-9638-439d-8f83-3f1d1d0f2b6e | checkpoint | Waste clear, plug installed
68754bd2-b77c-47ea-aa63-3bfc179f75f6 | checkpoint | Divertor operation working (where applicable)
87c99705-f473-454c-9112-7a049eec9cfe | checkpoint | Hot & Cold waterflow satisfactory, no water hammer
864c09da-3bbe-45e4-86fb-d4acfcf9a892 | checkpoint | Cover plate/spout fixed securely
c1ccdde2-1d4a-497f-a902-253171ada7fd | checkpoint | FWG
f0618157-d05c-4bbf-b5cb-4832193b29e2 | checkpoint | Grate flush with floor or slightly below
f8d2a347-fa3d-4a0c-9492-a62b23719441 | checkpoint | Waste clear of debris
94bd4268-fe61-4ce8-ae11-98a1d08c0dab | section | Amenity Areas / Kitchens etc.
f7eb9248-b038-4814-a613-77b92e977524 | checkpoint | Amenity areas / kitchens etc. are installed
268f1dff-f2dd-4255-ba9c-1152209dec63 | checkpoint | Hot & Cold waterflow satisfactory, no water hammer
b41e8008-6f18-4103-a680-c07188e51e4e | checkpoint | Water connection watertight, tap secure
435af419-96ba-434e-b8f7-6d475eaeda88 | checkpoint | Waste connection watertight
ec007538-2d8d-462b-9059-06e53e227536 | checkpoint | Dishwasher connection watertight
d7e9671b-044c-44c1-adde-84926872713a | checkpoint | Wastemaster connection watertight
1c39e127-13c9-4a40-8217-b8aee579499e | checkpoint | Overflow connection watertight
23e9f534-7594-4fb0-b404-04659f5a7b11 | checkpoint | Waste clear, plug installed
a98ac79f-9f8a-4201-ab4b-43ac26d17642 | section | Handover
6b6ef489-cac4-48d6-96fa-57671cde22b4 | checkpoint | Area left clean and tidy
89764629-5a9f-4d97-8e88-9c6769ae0dfd | checkpoint | Council Verification
f29af585-9873-43ce-8ddc-430f43ebe8a8 | signoff | Plumbing inspection complete and passed as satisfactory
571ba420-082d-47de-9485-8ca831c794cc | checkpoint | Main Contractor verification
8b432e37-2f6c-445d-bbba-5c304c808b40 | signoff | Plumbing Complete and ready for lining
95da9e0f-7230-439e-b6fb-d36348bbc8a7 | checklist | QA - Riser Checklist |  | QA - Riser Checklist
29e99bb4-99d7-4d7d-90f1-3b4498720046 | section | Details
286af545-7ea8-41b8-ad0e-863cfa0b7383 | checkpoint | Risers installed
c624b5fa-2d5f-4c3a-9eef-16eb18f698a3 | checkpoint | Risers securely clipped
8ebbb438-7eb3-4d19-9ba2-9c3050f46b06 | checkpoint | Meters installed
cb28872a-6475-4d7e-924b-81c3c2cd9fd5 | checkpoint | Risers insulated/lagged
65dbd208-0693-4032-ad53-e770f148d928 | checklist | QA - Sewer Risers |  | QA - Sewer Risers
e6c884bd-d645-4331-8419-ddcaff979aa2 | section | Details
4a12d55d-151e-44a5-a97e-85ad9939cca3 | checkpoint | Sewer riser installed
0f7209d0-d58f-4a9d-b1db-53d8db9ebd26 | checkpoint | Tested and passed
6dbcaaa7-ae7e-47bb-a29b-25256cf0ff8e | checklist | QA - Stormwater Risers |  | QA - Stormwater Risers
53393fbd-7ffc-4997-a03c-05e4923fd9a4 | section | Details
94ad1d87-1287-4c62-9d86-9ca3d2ec4c98 | checkpoint | Stormwater riser installed
68828312-8a21-42cb-8a79-c4bf7c6e76c3 | checkpoint | Tested and passed
ee6eb3b8-c3aa-4173-ac87-d240a8cb532c | checklist | QA - Testing (with Gas) |  | QA - Testing (with Gas)
1d75148e-33a9-4ba4-9550-e29cacc5e1ab | section | Details
11f4532e-21d6-4536-b97e-b667fedbc43f | checkpoint | Hot Water
38168c7b-3a7c-56cc-9113-025628332e11 | textbox | Specified to
4e9b7fc9-2809-5132-9b1d-d6f6c3c82462 | textbox | Test pressure
549433b2-be65-5915-b714-85da5963ddf4 | textbox | Duration
aa174c46-a3a9-4d40-a418-3fc61fb10b3f | checkpoint | Cold Water
da466950-775b-5678-a402-e939966e2993 | textbox | Specified to
27e5922c-3867-59d4-8a63-f3180fa5bc97 | textbox | Test pressure
e8c2e619-9131-543c-93f1-4c62594db348 | textbox | Duration
4a8927bd-3941-4d78-973a-5d0f192335a2 | checkpoint | Soil/Waste Pipes
a27b37dc-ef9e-5b87-967e-b4dc59107489 | textbox | Specified to
e13ead69-5a39-5009-801a-b7ebafeb9b31 | textbox | Test pressure
d5b52337-6f7b-5a19-9684-ff8eeb4915a8 | textbox | Duration
192cae1d-4164-4921-91c6-9ea4a3bf286a | checkpoint | Vent Pipes
2732ec45-71b7-500f-b7d8-ff880ae7f883 | textbox | Specified to
30583a1b-6496-500c-9158-a6b3795f3ac1 | textbox | Test pressure
7a3b4682-07e5-5688-9f4e-b6cb5da554aa | textbox | Duration
a5440f82-0671-4194-90b0-4f031d0ae6c8 | checkpoint | Gas Services
8e2a8374-eb74-58fc-84d6-8ef93fa957ec | textbox | Specified to
ec88901d-d28e-516a-9bff-39fcbc6838d7 | textbox | Test pressure
2b306d2d-0f85-54b2-ae5e-4e0d7192f1ff | textbox | Duration
d2d474db-8f1f-4df2-b314-a712b1d0b0a9 | checkpoint | Other
e9006162-79c1-5f8a-aac4-9ef54c26e914 | textbox | (specify other)
d7eef5f2-a3d5-5b85-b5ec-029f718e6899 | textbox | Specified to
7f4a2632-cdc3-5855-b5ff-c8417eba0b10 | textbox | Test pressure
b361cca4-3786-5438-a901-acba06e20cfa | textbox | Duration
e5b6ff84-bd0c-4539-92b8-08d872924129 | checklist | QA - Underslab |  | QA - Underslab
5155f2fe-6489-435d-8b09-37fb7cb1079d | section | Pipework
611b995e-f6f6-4ac2-be6b-5df605c5be69 | checkpoint | Service
134dccdc-50f9-53dc-8a02-5e1e8ece59bb | dropdown | Service being checked | Stormwater, Waste Water, Gas, Water supply, Other
e9689dee-060a-5aa5-8e58-e230ff5adb41 | textbox | (specify other)
0d4fa1cc-05a7-4715-ba82-719c56e6dae6 | checkpoint | Pipework Material as specified/scheduled/drawn
f8a59d66-8e4c-4524-bce7-cc7fd06d1fb5 | checkpoint | Grid lines and fitting dimensions confirmed
1c0e0f5b-1326-457c-87c0-42d027354d08 | checkpoint | Drain invert checked
53134df5-5e52-47e2-b296-6c5e92c226ed | checkpoint | Gully position checked
4755b066-6e4f-4694-9339-0bef3a8b437a | checkpoint | Floor levels established
12d85794-0de9-4d40-aceb-eac7ad4a5637 | checkpoint | Falls checked
dd0233c7-4159-4d7f-9f40-6e3ffc00369e | checkpoint | Drainlayer/Plumber interface Points established
66c741ae-c570-4a8b-a86c-8466a5c5d9b9 | checkpoint | Penetrations co-ordinated with main contractor
2edede9d-e7ff-4539-9005-ff1452897359 | checkpoint | Pipework backfilled correctly
dee916c5-e87e-4a83-8785-e1872d24bda7 | checkpoint | Identification strip installed if required
298b8df4-bdac-425c-9b95-bf02adff8c6e | checkpoint | Open ends of pipework capped off to prevent dirt ingress
138cfdbd-53da-4c6b-bcb8-935648c796c2 | checkpoint | Work completed and photos attached
3db670c9-8a38-45d1-832c-d10a464f3872 | section | Testing
79af7ee1-350d-496e-aee5-71f1322ee597 | checkpoint | Cold Water
e44965c7-f63e-5962-9d52-a6fe07463943 | textbox | Specified to
f400e0f2-0f8d-5bd1-8c44-5cfd92bba5cd | textbox | Test pressure
d03eb0e5-ab5f-51a0-94f4-2e704c8077ef | textbox | Duration
6f495c23-3f41-4ba3-bab7-240af9fc1ae1 | checkpoint | Waste water
e3710a6a-72db-5271-9854-183840fcd8d6 | textbox | Specified to
2577c4b1-7547-587f-8a2b-0a8949ca85ff | textbox | Test pressure
4d3dcf6b-15a2-572b-807f-7e86f472e887 | textbox | Duration
ecf73d35-afe9-4b37-aae4-efa41bd8aa57 | checkpoint | Gas Services
3d53113f-b185-5cc3-8bd2-11baaa826980 | textbox | Specified to
d6eca866-4def-5567-9f0e-afc303d1382e | textbox | Test pressure
54f6e92e-404e-5683-9acd-86429a21245f | textbox | Duration
eb67ed93-01c3-43f6-b69b-438e22493ef3 | checkpoint | Other
4ecb083f-858d-585d-8dd0-04e25b70641a | textbox | (specify other)
f9893f49-d2b4-547e-a515-9e051453359b | textbox | Specified to
ab04c82b-df51-50e2-8a9d-5316feb4b31f | textbox | Test pressure
06539f8c-1974-5387-aeb0-9181f8ce96be | textbox | Duration
70e4cc89-ecd1-4b08-98c5-dcf5a4b60db5 | section | Handover
706e6ea6-cc9b-41bc-8c90-dd34e78f5b36 | checkpoint | Area left clean and tidy
a75f8866-4c62-4780-b48a-094087d45ca8 | checkpoint | Council Verification
0284bf9e-c647-4ceb-b033-f33dc7ecc58c | signoff | Plumbing inspection complete and passed as satisfactory
1715495b-63c0-4434-8b27-f117d6ce2c38 | checkpoint | Main Contractor verification
312a91a6-7955-4fe2-93ec-e4a9071c711c | signoff | Plumbing Complete and ready for backfill/ concrete pour
e494545d-8627-4795-8f51-b13be91342d2 | checklist | QA - Water Risers |  | QA - Water Risers
ea04a21e-7c80-42df-a7b3-49858092600b | section | Details
8c9285c2-53f9-470e-b3b2-c4114aafc1ac | checkpoint | Water riser installed
de626ef2-195a-45d2-a0d1-21b2a3d36acf | checkpoint | Manifold installed
04688b12-07c7-4451-88f5-177246a29d8e | checkpoint | Tested and passed
619fb57a-d92f-4e0e-a747-b9e14c48ff41 | checklist | Rainwater |  | Rainwater
b012d38c-7b26-445d-bf06-6f1904f1a879 | section | Details
1946f8c6-bb7d-435a-85a6-5e0ba264832c | checkpoint | Setout & alignment as per drawing (include revision below)
71b68ddc-1964-528d-98e1-f3c6905355ee | textbox | Drawing & revision number(s)
6182e792-2601-4412-9158-2f2b32c88574 | checkpoint | Material type as per approved sample submission
8915fe7a-805d-4b6a-aa35-63a4788293cf | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
a7091635-bd36-475a-8d05-5fcdb9565004 | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
9e4bd53f-7505-4327-aa89-b6daf8f6195f | checkpoint | Support & fixings (acoustic / seismic / water hammer)
8e35d292-f1c9-4e76-872a-0c3ce39a3fa7 | checkpoint | Pipework Installation (as per AS 3500.1)
599f50a4-5783-43a2-a798-97af19ee018b | checkpoint | Check no cross connection
f48b14d9-94f6-45ee-a452-badd30a24761 | checkpoint | Pressure test (1500kpa pressure test)
f687e3e6-2b28-408a-bce3-39e6f4d7ec8b | checkpoint | Identifications of services
d281606c-dcc4-469b-ab95-bfd21772f95b | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
4ab15107-2f0c-544e-8d6f-0bb024c4b617 | note | Passing above includes Builder sign-off
48ec71eb-4956-5b88-a7ab-744a29433f65 | tickbox | Area clean
a110c65c-cc54-4fd3-b719-1fc582371dd0 | checklist | Shower Tray Checklist |  | Shower Tray Checklist
72b51384-62ba-4fea-b828-56f2d7a25dd7 | section | Details
b9457762-e2aa-4e56-963a-c2e8fed5bd1d | checkpoint | Wall(s) are square
c7d6ef36-b21b-4e69-8140-f73a7cf97e98 | checkpoint | Flooring is prepared and level
a506bea6-c685-47f7-ac72-04a0f52f8011 | checkpoint | Pipework sealed and flood tested
2cd2eaa1-a68e-4c29-b3f4-2d28afa36e62 | checkpoint | Easy clean connected to pipework
07bf74cb-b036-40b6-b3bc-2c8cdbc81783 | checkpoint | Tray is level
70b1495c-b427-4063-baec-92f4d1924c1d | checkpoint | Easy clean sealed
0b9b27ac-7169-4137-981e-dc0d5ec53cf4 | checkpoint | Tray flood tested
7f9d59bd-08c2-4e02-8ed2-3268af257507 | checkpoint | Shower tray protected from future construction damage
b35490b2-5849-4515-9122-620f7674c720 | checkpoint | CC Signed
4f3c023d-0f4a-4511-b799-2f92b83ccf81 | checkpoint | Witness Signed
c2f2282e-2317-443f-ba62-e745b934d207 | checklist | Site Visit Report |  | Site Visit Report
22a58bf5-b0e7-457c-9b54-c2a29352e459 | section | Details
2af30aaa-c82d-45ba-ab61-89dca3e3549d | checkpoint | Details - Site Visit
6aeca8d8-9e5c-55d5-b76e-aecbc142379b | textbox | Site/job:
3e772eb7-6a59-5d7d-9587-fd223ed8bffc | textbox | Persons on site:
3e0b4b9b-45a5-5bea-9878-2de3efad3bff | date | Date of site visit:
d4ca7378-3600-5c53-8eaf-88eb5bdaa3df | textbox | Weekly report discussed with Site Manager:
9a3fec23-0037-5b93-897a-8691bcc21e5c | textbox | Verify stage of work (provide comments):
f9f0c6bc-e629-5d9e-805d-3442104f8740 | textbox | Potential issues (provide comments):
59b3b4bd-c085-4920-b40e-2be513d139b7 | checkpoint | QA - Confirmation of quality of works completed since last site visit/QA
2d3cfce3-6474-515f-8e03-1c36da94340f | tickbox | Walk through site with Lead Hand
d6f4281e-199f-5175-a8f6-2675e4588374 | tickbox | Visual check
cc64e1ad-458f-521f-87bd-fa9713220738 | tickbox | Query the Lead Hand's Install process
973d73e2-13b9-5a9c-989f-48510e2b73b0 | tickbox | Query the site contact satisfaction with work to date
ee2b7b4c-bd72-561c-8e00-bf4b030af4f3 | textbox | Other:
f3dfd7cb-5121-4a33-8186-f28419205b3d | checkpoint | Outstanding RFIs
20d85529-1158-4592-867e-eb5c80cc2fdf | checkpoint | Outstanding VO's for approval
87105c43-c8d8-4a71-bdf8-09ddcc2ee172 | checkpoint | Labour requirements for upcoming week
c9682472-8a9c-4c33-9a56-09453ee72290 | checkpoint | Completion
d6d8706e-2095-4892-8c8e-633ab585bbb8 | signoff | Click here to signoff
fcabcfac-0137-4187-b258-c23a21545c1f | checklist | SS or SW pump QA |  | SS or SW pump QA
f843ac3b-5921-487d-af0b-7d70c46812d9 | section | Pumpset mainfold
b8c4691c-cab8-44c8-9cdc-029df425f1ba | checkpoint | Connections welded correctly
e0d745e0-b2dd-4187-8f5d-5f4da173c707 | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
4d4dcfbd-f36d-40bf-860d-8fb5ba507889 | checkpoint | Valves fitted correctly
81d2531b-cb9f-4f9b-829c-b25fdeabc947 | checkpoint | Line strainer fitted between pump & tank
f4248b35-80ad-4619-9e6f-3fd2443c5449 | section | Pumps
e3443b22-a28a-4b05-8ac1-75b95f74781c | checkpoint | Pump 1 Startup KPA
cbdacdbf-ca30-4b70-9044-312900315587 | checkpoint | Pump 1 kick out pressure KPA
8a0344d2-d23d-4549-8caf-0a257c6c7afa | checkpoint | Pump 2 Startup KPA
a02725c4-c30d-48cc-aaea-278587ffc3df | checkpoint | Pump 2 kick out pressure KPA
92c2bad2-2a67-45c9-910e-3d9312b80195 | checkpoint | Pressure vessel pressure
85452f41-8c12-4752-8bb2-4a50ef9b8c73 | section | General
d0231009-0639-46a2-9bd6-6364538bbe5c | checkpoint | Mains water change over
7564af43-f2fb-42af-aa20-cfe142ae949b | checkpoint | Flow test pump
8a896250-f0dc-4efe-9421-9e8a16e5c566 | checkpoint | Pressure tests pipework
24667680-5198-431a-8933-80b0b3496bd1 | checkpoint | Visual check (for leaks from valves, tees, saddles, etc)
a73b5732-b9e2-4908-85a3-2900b5290761 | checkpoint | Non return valves fitted
120b4fb7-c347-496a-b59e-31bc0d494a67 | checkpoint | Installers name & date works completed
c7d53a13-d224-5106-b610-7a96c6f58a8c | textbox | Installers name
f1db5e87-4ac4-5e3f-a682-c843d52cf959 | textbox | Date:
b0ee37e8-c15e-425f-92d3-284d5c1a2d83 | checkpoint | Tested by & date
5097dfbc-eae8-5a9a-b9ab-4373c99a1d33 | textbox | Tested by:
f5b62974-0881-5c06-83a6-c9b7eb8d2cf4 | textbox | Date tested:
7f982e5f-c2fc-4c32-835b-984415f7d7e6 | checkpoint | Council inspector sign off and date
21f4ba53-b598-40e6-8734-a99e5b411de9 | checklist | Stormwater AG |  | Stormwater AG
4e6b1f86-00b5-4eb5-95e0-51e07ffaba72 | section | Details
48c6f25f-12bc-4f4b-ade1-30976b6ca0ea | checkpoint | Setout & alignment as per drawing (include revision below)
19d52f6a-6272-5224-ab27-cb733c2d1df4 | textbox | Drawing & revision number(s)
e8105a59-e47f-4401-8f82-0442c9221185 | checkpoint | Grades (as per AS:3500)
9f166a79-46c5-4a25-be95-90745798754e | checkpoint | Location (as per hydraulic drawing)
033b264a-cca9-5f61-b46b-3aa6bbbe99d1 | textbox | Location
6b104c51-3363-454e-9d4b-41cdc6078404 | checkpoint | Fixings - Securely fixed (As per Standards)
7f5981e2-f44a-41de-adc2-4ca111ec2a3c | checkpoint | Fittings Joints ETC (as per AS 3500)
5d5359cc-03bf-40f7-8034-e0a6c27e6d16 | checkpoint | Inspection prior to closure
c9b768f2-275e-40b1-9626-8e5473b684aa | checkpoint | Operation of pumps (Commissioning report) if Applicable
00cfe5da-f045-45d4-8f17-a86e93c90d42 | checkpoint | Test water and discharge requirements are met
6006da51-e11a-4faa-b18e-a227718930c8 | checkpoint | Correct invert level AS per AS 3500
eefe80f5-3e25-4357-b56d-948fae656ede | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
28c83e41-caaf-53f6-9cc3-97ad298c1cb6 | note | Passing above includes Builder sign-off
ed157c41-b456-5e42-ac99-d5a6ee2b50c1 | tickbox | Area clean
8ca751f0-0d71-4ad9-844d-94fe047af278 | checklist | Stormwater BG |  | Stormwater BG
a02282ca-4858-47a1-8a79-fdc809e4c677 | section | Details
189c1a8b-6c82-408c-9015-6929528f25b9 | checkpoint | Employee trained for task
75b0fa9f-dc85-4fa1-87bb-7dcf4a8672bf | checkpoint | Setout & alignment as per drawing (include revision below)
a309031e-e8ce-533b-9599-3f46bc7ca169 | textbox | Drawing & revision number(s)
f7078255-354a-4562-8dfa-5f4d7ec17dc9 | checkpoint | Correct material as per sample register
c04f72d3-fc83-400a-af80-23221cfdf6aa | checkpoint | Excavation undertaken & no issues (Any issues comment below)
c0937dd2-fe7e-4765-8a9e-2ad29955b426 | checkpoint | Pipe bedding material (as per AS 500)
d65de55a-015f-4d60-beb5-04166b680a79 | checkpoint | Grades, fittings & joints installed to standards
6a30a05d-cd33-4eee-afe1-8d68447811a2 | checkpoint | Pipe clean out via water flush
19e17088-21e1-4d0f-bea5-9a2eb6231dc6 | checkpoint | Inspection and Testing Prior to Concealment to AS 3500.2 section 13
063b7052-fb07-42c7-b7f8-29e0cc9721ab | checkpoint | Seal open ends with caps & high light to avoid damage
230aa5fa-1249-4760-8b5d-16e3f3b6c5e7 | checkpoint | Backfill & compact trenches to code requirements including correct cover over pipe
d64c53fc-d5e5-4368-a8da-e1d91510c929 | checkpoint | CCTV on completion & record results (If applicable)
dd718d68-29e2-4f77-a2c5-29c545ff0f00 | checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
01ee235d-78f0-5f8b-ba33-496a95d92618 | note | Passing above includes Builder sign-off
46ea2ced-58d2-5d28-bda4-e11cdd36f794 | tickbox | Area clean
05be6f8f-ecc9-41b2-b519-bfefd93e4383 | checklist | Testing |  | Testing
ebe984ff-00ea-474b-8195-43ca91dde4a5 | section | Details
4e3e06de-de73-426d-a4d4-8e4679f9e2b6 | checkpoint | Hot Water
b09c6b0f-7106-5c70-94d4-d2d4842e5050 | textbox | Specified to
154e01b4-058a-5d41-8553-a8bd8eb04243 | textbox | Test pressure
dabb77ae-8fd2-573c-98cb-0b665f0a2a14 | textbox | Duration
6faa8d66-b081-4f33-b631-2073884eb022 | checkpoint | Cold Water
08dffd22-31d5-56dd-b0d7-a80863c268e7 | textbox | Specified to
0380b6d3-ff90-519b-bb58-2a2b63c3372c | textbox | Test pressure
6efa262d-d390-5f76-a0ff-90629a5f6e11 | textbox | Duration
38d94053-11b3-4282-aa0b-8289a62cdc03 | checkpoint | Soil/Waste Pipes
8c04b90b-d56a-56d9-b7a2-1a4c0922eb98 | textbox | Specified to
c435f733-c434-537f-a070-5f4e2e4c92eb | textbox | Test pressure
c89b64fe-87b8-5b01-968a-6cd5310d2e53 | textbox | Duration
3fec85b1-c6e1-42dd-a7f0-03b11f76f02c | checkpoint | Other
f26f4da8-6101-5c9e-946d-7e6ad4e65653 | textbox | (specify other)
96fae376-62ae-5421-b2ce-1c82f212f11a | textbox | Specified to
252e6760-f52b-59a3-9c4f-44146f3d3eb6 | textbox | Test pressure
1d0e39e6-2a19-597d-a429-c3ec155458aa | textbox | Duration
e0bf3db5-7ad2-430e-99a7-2b1a7a1f8d52 | checklist | Thermostatic Mixing Valves Guest Rooms |  | Thermostatic Mixing Valves Guest Rooms
4949d6f2-8e1f-4139-bbe7-e7671c3ea327 | checkpoint | Guest room Numbers that TMV supplys
d3353082-988e-54de-aeb0-fb0d463d1fab | textbox | Guest room Numbers that TMV supplys:
45ea9367-40d1-426c-af22-892105335fc6 | checkpoint | TMV installed in accesible area
4dec74a5-faaa-4db0-bdb4-c1c8757c42eb | checkpoint | TMV installed in correct orientation
6bb3542f-40e0-43ef-919a-ca35abaa6e14 | checkpoint | Non returns and filter gauze fitted
a35a7f3f-ab70-490e-94ac-531500d7d03e | checkpoint | Valves fitted to TMV
cdec0bce-df8a-4527-a79a-7896af198db4 | checkpoint | Pipe tested prior to fitting valves
56126d79-d3a6-42d0-8c8c-25ffe6305c9f | checkpoint | Connections made and no leaks
f8a8a2f8-ee08-4487-b4eb-60937675d01f | checkpoint | Clips and spacing checked
84432ac3-0918-431c-b24a-7cd187b31c19 | checkpoint | Brazing and crox connections sound
c4ad6f84-a46b-4d78-992c-a0262d7ee01b | checkpoint | Seismic requiremnets achieved if applicable
f5104d8f-baaa-400b-9178-2e9620e8b9bc | checkpoint | Pipework lagged where required
ae99eb83-fdcc-4e98-bb4b-71a887af9c10 | checkpoint | TMV labelling
22292ea6-df9e-49af-a267-22ec4a23f97d | checkpoint | Tempreture set on TMV
214ec4bc-9ebb-406d-9141-64ccd0262908 | checkpoint | Installers name & date works completed
bff7a797-87c4-5483-91ef-18d02cc0f636 | textbox | Installers name
bfea960c-9284-5fef-8737-691a3e42bcb3 | textbox | Date:
45d68f2c-f9f4-45ed-b4e3-0bd7b28b2420 | checkpoint | Tested by & date
ac0fda7e-0fa3-55c0-aced-283199560a0d | textbox | Tested by:
2ddcf8f9-0358-52f4-b201-a680450a9447 | textbox | Date tested:
8cde80a5-2e8a-46cd-842f-90fc1c1cb49a | checkpoint | Council inspector sign off and date
42943126-56f3-4172-bd4b-51fae2df8e8e | checklist | Underslab |  | Underslab
a8b40e83-b4ec-4e46-880a-7e03bb95b6b1 | section | Details
9e19eb23-7876-49a4-9155-c19c06c8e191 | checkpoint | Area ready for works
5a38ce10-d71f-4d78-908f-4364f64fe6ce | checkpoint | Dimensioned Slab Set Out Drawings
291e13d6-7eec-4f35-8fa0-5fbd9e629533 | checkpoint | Minimum Or More Fall Achieved on Slab Piping
b6cadfff-56bb-4ebc-9494-ba38745e9f34 | checkpoint | Under Slab Piping In Slab
bda0e115-f6b1-436d-bcf9-76db7896d9b7 | checkpoint | Called For Underslab Inspection To Be Booked
5429b003-0763-437b-849e-3d8924833840 | checkpoint | Mains Water Supply In Slab
a7730655-9123-454e-9b1d-0479d7c2b9ef | checkpoint | Water Supplies installed incoming / island bench
7f3e35c7-bba5-4964-8f7f-cd96a5141bc7 | checkpoint | Gas supply
e9b72dd3-bb42-4696-aa71-f325e05caa31 | checkpoint | Test Plug Removed From Pipe System by:
cc08655d-9b22-41bf-8f60-9d7661001b40 | checkpoint | As-Built Drawings
9a3f9b4d-e708-48e5-b0f8-6bde23926559 | checkpoint | 25mm Protection Around Pipes Penetrating Slab
4b6c7206-5e5c-4f03-8b81-5bbaec4e4c86 | checkpoint | All Measurements Double Checked
cc001956-4bb0-4987-a61f-50cc4be0fa43 | checkpoint | Boxing For Shower Wastes
bab7f9f6-63ec-4883-be50-4464dcffbfa5 | checkpoint | Lagging and trace wire to greasy wastes
b8548b3a-ef51-43f2-bc85-800a384e3b32 | checkpoint | Haunching & Bedding
06bc15d1-1c2d-44c0-9d13-c72e6406b2bd | checkpoint | Concrete Under Gully
18132997-e2c4-44f9-9d4c-2e36844e14f2 | checkpoint | Drawing Number And Revision
58e7800e-4e4d-46bd-b6cc-528f73af5b34 | checkpoint | As built drawing complete
6cc3a1b4-3fa8-46da-8e6a-f37fbc497191 | checkpoint | All upstands capped
bad136d1-cf79-435e-a21c-d70c324bcd1f | checkpoint | Installers name & date works completed
3c4bd372-35f1-5d9b-8a39-9d25424d6c57 | textbox | Installers name
4f7c8b64-2008-5bb7-a974-8c143eabae38 | textbox | Date:
1e93f5c4-ea31-4473-ac6c-5799cbdcf587 | checkpoint | Tested by & date
aa6731e2-9bc7-504c-b1ff-f1185fc4ecb8 | textbox | Tested by:
2cf14be3-4caf-5d2c-a72e-2f61d42610a1 | textbox | Date tested:
03a4d2eb-8b84-48cc-a1bc-5d32fdfc0db5 | checkpoint | Council inspector sign off and date
9b5e0844-8b46-4ea9-8882-caa8e3a31ebd | checklist | Water Pump Commissioning |  | Water Pump Commissioning
ff3b3df1-2db5-4dd4-8c3d-6e33984292fb | section | Pump setup
3ac6e3c7-642f-4cab-b5b3-80c251274976 | checkpoint | Connections welded correctly
cae9802e-fc0c-430e-9f29-246128a759ea | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
51713120-7e3e-4248-b852-aeedae1af7ec | checkpoint | Valves fitted correctly
c25c64cf-70c3-4bc4-a173-2591ccf42adb | section | Pumps
8488ad29-ff0e-40f7-8a48-ac026409253d | checkpoint | Pump 1 Startup level
7c35be4e-edac-45b0-9b9e-d0ceb8da69f7 | checkpoint | Pump 2 Startup level
6608e9cb-f67d-466e-9eb9-dadd9efd2e41 | checkpoint | Pump 1 kick out level
dcf1bf5d-87d9-45b9-96cd-a3733a56f9b3 | checkpoint | Pump 2 kick out level
0d66f4b4-0530-4c64-8b45-a4c19040eb42 | section | General
0a645dc6-9341-4c99-95ac-951c9faf3e2c | checkpoint | low level alarm test
636d3680-260c-4ced-9473-733b96ddf14a | checkpoint | Tanks clear of debris
2cfccf28-4c42-4feb-86a0-957cb022fae2 | checkpoint | Low level pump shut off
9dfe0587-f32c-44a4-affa-dc006f75acbc | checkpoint | Impeller clear and free
b3d14c35-4697-4318-b4d3-db3bfb583b13 | checkpoint | Installers name & date works completed
5dda77bb-98db-55d6-ae87-3188e05b0b75 | textbox | Installers name
f94cbe0d-0e5e-571e-ae66-3a7087ccedee | textbox | Date:
694a3452-18cf-48ec-86d8-15adfd2f810b | checkpoint | Tested by & date
b73ef865-c7c6-5ba0-9a23-34bb12f77e95 | textbox | Tested by:
cba8888a-990c-5091-98f7-bf92b1fb772b | textbox | Date tested:
da760289-ba47-4305-b530-ae8b670b1674 | checkpoint | Council inspector sign off and date