## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Prefix | Postfix | Resource Id
0dc4e203-08f7-4c87-81ea-c1cf21ee20f3 | checklist | ITR-E-19 HV Cable Install |  | ITR-E-19 HV Cable Install
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
90ad256a-cc82-47b2-be68-9a9ef3ab8b3d | checkpoint | HV Cable Install
cc29fa55-5fe5-542d-aae6-b5a317818561 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
3733b5ca-b64f-54bd-ba7c-aed07846a861 | button | Check dressing / cleating, cable undamaged | Yes,N/A
2bbb5df0-4010-557e-b31d-498f09f1e5ce | button | Check cable cores correctly identified and labelled. | Yes,N/A
3cf74f56-d88c-5ab3-8481-56c37a833142 | button | Check cable is terminated correctly | Yes,N/A
b7192934-0b91-5863-a040-df3cc234946a | button | Cable has been installed as per client specification | Yes,N/A
db79cc67-bcee-5799-9eb7-63146f45bafc | button | No visible damage to sheath | PASS,FAIL
429d748c-2b60-5309-9d6f-cc4108496a9c | dropdown | Cable Voltage | 11kV,33kV
1d3abe04-a329-541d-ba46-ea69fd91659a | textbox | Temperature:
1b9d8cb2-e175-5a88-878b-c5f1b97638f3 | textbox | Cable Point to Point:
7591ec71-d9d8-40f4-9572-07a1a6b71781 | checkpoint | Electrical Tests
a598796e-f8b5-560f-8616-052299e798ea | note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ. Please insert photo of test results.
b23c38ff-795d-555a-9db5-6b118428b720 | textbox | R-WBE |  |  |  | GΩ
b58fc05a-668d-5951-9d0a-e0aa26497667 | textbox | W-RBE |  |  |  | GΩ
d3aee404-6d4b-545e-8f34-01439b4d5763 | textbox | B-RWE |  |  |  | GΩ
d920a905-8990-5944-98ae-7117035d7879 | textbox | One Core |  |  |  | GΩ
e522260b-45be-4509-97a6-67cc2cb9a311 | checkpoint-no-value | Sheath Integrity Test
a83836d2-51e2-5b6d-bcbf-973658a28930 | textbox | Test Duration:
ff9b4409-cb93-5d68-bb8a-2f8ec1f70f82 | textbox | Test Voltage: |  |  |  | GΩ
01dafb52-67d2-56bb-95ea-97d522e08cec | textbox | Result (GΩ):
17ec1322-89c4-48fa-8d02-aed878f0ef01 | checkpoint-no-value | Test Equipment Details
01c20c58-3ecd-59fd-b3f2-5af833fc28e4 | dropdown | Make | PHENIX
23d953f4-0d53-5dcc-9e1a-6456cb5f82cc | dropdown | Model | PM10A
d97c7ddc-da00-5bf1-aed1-7ae042f0ca07 | dropdown | Serial No | 20-4331
ad61610c-21d8-57dd-9641-37d7310f5550 | textbox | Calibration Expiry Date
db024b07-edc6-49ca-bee7-7aeaad1efdad | checkpoint-no-value | Installer Sign-off
4997561d-fb4f-4a8a-998f-ad8ecb55915c | signoff | Installed by: