## Structure
Tier 1 | Tier 2 | Tier 3 | Checklist Template
Site QA | Inground Works
Site QA | Inground Works | Fibre Lead In Duct | Inground Services
Site QA | Switchboards
Site QA | Switchboards | DB - Block 9 | Switchboard
Site QA | 1st Fix Interior
Site QA | 1st Fix Interior | Classroom 9 | 1st Fix
Site QA | 1st Fix Interior | Breakout Room 1 | 1st Fix
Site QA | 1st Fix Interior | Classroom 10 | 1st Fix
Site QA | 1st Fix Interior | Classroom 11 | 1st Fix
Site QA | 1st Fix Interior | Breakout Room 2 | 1st Fix
Site QA | 1st Fix Interior | Classroom 12 | 1st Fix
Site QA | 1st Fix Interior | Boys Toilets | 1st Fix
Site QA | 1st Fix Interior | Girls Toilets | 1st Fix
Site QA | 1st Fix Interior | Staff Toilet | 1st Fix
Site QA | 1st Fix Interior | Resource Room | 1st Fix
Site QA | 1st Fix Interior | Corridor | 1st Fix
Site QA | 2nd Fix Interior
Site QA | 2nd Fix Interior | Classroom 9 | 2nd Fix
Site QA | 2nd Fix Interior | Breakout Room 1 | 2nd Fix
Site QA | 2nd Fix Interior | Classroom 10 | 2nd Fix
Site QA | 2nd Fix Interior | Classroom 11 | 2nd Fix
Site QA | 2nd Fix Interior | Breakout Room 2 | 2nd Fix
Site QA | 2nd Fix Interior | Classroom 12 | 2nd Fix
Site QA | 2nd Fix Interior | Boys Toilets | 2nd Fix
Site QA | 2nd Fix Interior | Girls Toilets | 2nd Fix
Site QA | 2nd Fix Interior | Staff Toilet | 2nd Fix
Site QA | 2nd Fix Interior | Resource Room | 2nd Fix
Site QA | 2nd Fix Interior | Corridor | 2nd Fix
Site QA | 1st Fix & 2nd Fix Exterior
Site QA | 1st Fix & 2nd Fix Exterior | Exterior Lights (on Toilet Block) | 1st & 2nd Fix Exterior

## Checklist Templates
Type | Name
checklist | Cable Tray
checkpoint | Area ready to start work
checkpoint | Unistrutt Filed & Painted
checkpoint | Hangers Spaced as Specified
checkpoint | Correct Size Tray Installed
checkpoint | Tray Joined Correctly
checkpoint | Hangers Seismically Restrained as per Design
checkpoint | Tray Fastened to Hangers
checkpoint | Correct Anchors used fixing to Ceiling
checkpoint | Cable Tray Bonded
checkpoint | Photos
checklist | Inground Services
section | Ducts and Conduits
checkpoint | Area ready to start work
checkpoint | Correct size installed
checkpoint | Magslab installed for MD Ducts / Conduits, 75mm above
checkpoint | Warning Tape installed at half the depth of cover
checkpoint | Start and finish locations correct as per plan
checkpoint | separation from other services
checkpoint | Clean inside and in good condition
checkpoint | Draw Wires Installed
checkpoint | Photos
section | Electrical Pits
checkpoint | Area ready to start work
checkpoint | Set out correct
checkpoint | Correct size installed
checkpoint | Duct entry holes sealed / water proofed
checkpoint | Pits installed to correct height and level
checkpoint | Clean inside and in good condition
checkpoint | Photos
checklist | 1st Fix
checkpoint | Area ready to start work
section | Flushboxes
checkpoint | Height as per plan
checkpoint | Location as per plan
checkpoint | Fire rated boxes installed where necessary
checkpoint | Acoustic boxes installed where necessary
checkpoint | Flushboxes not back to back on Acoustic / Fire Walls
checkpoint | Intumescent Pad in Place
section | Cat Wires
Checkpoint | 300mm Seperation Between Power & Data
Checkpoint | Supported every 6 Meters or Adequately to avoid Sagging
Checkpoint | Correctly Secured at Each End
Checkpoint | Turn Buckle Installed and Accessible
checkpoint | Number of cables per cat wire. 8 maximum or as per electrical spec
checkpoint | Separation between other services maintained
checkpoint | All cables secured via cable ties with ends cut
section | Cabling
checkpoint | Power cables installed correctly incl. correct type & size
checkpoint-no-status | Details
text | Type & Size
checkpoint | Lighting cables installed correctly incl. correct type & size
checkpoint-no-status | Details
text | Type & Size
checkpoint | Switching / Control cables installed correctly
checkpoint | Circuits clearly labelled
checkpoint | Separation between Data and Power at 300mm or as specified
section | Cable Tray
checkpoint | Minimum 25% spare capacity left on cable tray
section | QA - Lights
checkpoint | Setout Correct
checkpoint | General Lighting Cabling installed and in correct locations
checkpoint | Dali Cabling installed and in correct locations
checkpoint | PIR Sensor Cabling Installed and in correct locations
checkpoint | Emergency/ Exit Lighting Cabling Installed and in correct locations
checkpoint | Nogging installed for surface mounted fittings if required
section | Photos
checkpoint | Photos
checklist | 2nd Fix
checkpoint | Area ready to start work
section | Power Outlets
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Outlet Installed level
checkpoint | Circuit Tested and results recorded
checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
checkpoint | Photos
section | Light Switches
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Light switch Installed level
checkpoint | Circuit Tested and results recorded
checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
checkpoint | Photos
section | Light Fixtures & PIR Sensors
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Tested for operation
checkpoint | Seismic Braces Installed as per design
checkpoint | Photos
checklist | Switchboard
checkpoint | Area ready to start work
checkpoint | Spatial certificate signed if required
checkpoint | Fixings installed in wall correctly if board is wall mounted
checkpoint | All clearances sighted to ensure location is compliant
checkpoint | All cables correctly installed in protection device and earth and neutral bars and fully secured
checkpoint | Cables neatly dressed
checkpoint | Phase tabs on chassy covered
checkpoint | All earths and neutrals labelled to match phase numbers
checkpoint | Switchboard is clean on the inside and outside
checkpoint | Masking blanks installed
checkpoint | DB legend installed
checkpoint | Feisst label on the door installed
checkpoint | Photos
checklist | 1st & 2nd Fix Exterior
checkpoint | Area ready to start work
section | Cabling
checkpoint | Lighting cables installed correctly incl. correct type & size
checkpoint-no-status | Details
text | Type & Size
checkpoint | Circuits clearly labelled
checkpoint | Photos
section | Light Poles & Light Pole Fitting
checkpoint | Correct Light Pole & Light Fitting type installed
checkpoint | Light Pole is Level
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Insulation removed from poles & fittings
checkpoint | Tested for operation
checkpoint | Circuit Tested and results recorded
checkpoint | Photos
section | Drive Thru Island Equipment
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Circuit Tested and results recorded
checkpoint | Photos
checklist | Mains Submains
checkpoint | Area ready to start work
checkpoint | Correct Size and Type Installed
checkpoint-no-status | Details
text | Type & Size
checkpoint | Cable Clearly Labelled / Marked on both ends
checkpoint | Trefoil Formation maintained throughout length of run and cables fixed in place with cleats
checkpoint | Photos