## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Inground Works
| Scope |  |  | Site QA | Inground Works
Rows
|  | Inground Works | dynamic | Inground Works | Site QA
Columns
|  | Ducts & Conduits - Area ready to start work |  | Area ready to start work | Ducts and Conduits
|  | Ducts & Conduits - Correct size installed |  | Correct size installed | Ducts and Conduits
|  | Ducts & Conduits - Magslab installed for MD Ducts/Conduits, 75mm above |  | Magslab installed for MD Ducts / Conduits, 75mm above | Ducts and Conduits
|  | Ducts & Conduits - Warning Tape installed at half the depth of cover |  | Warning Tape installed at half the depth of cover | Ducts and Conduits
|  | Ducts & Conduits - Start & finish locations correct as per plan |  | Start and finish locations correct as per plan | Ducts and Conduits
|  | Ducts & Conduits - separation from other services |  | separation from other services | Ducts and Conduits
|  | Ducts & Conduits - Clean inside & in good condition |  | Clean inside and in good condition | Ducts and Conduits
|  | Ducts & Conduits - Draw Wires Installed |  | Draw Wires Installed | Ducts and Conduits
|  | Ducts & Conduits - Photos |  | Photos | Ducts and Conduits
|  | Electrical Pits - Area ready to start work |  | Area ready to start work | Electrical Pits
|  | Electrical Pits - Set out correct |  | Set out correct | Electrical Pits
|  | Electrical Pits - Correct size installed |  | Correct size installed | Electrical Pits
|  | Electrical Pits - Duct entry holes sealed/water proofed |  | Duct entry holes sealed / water proofed | Electrical Pits
|  | Electrical Pits - Pits installed to correct height & level |  | Pits installed to correct height and level | Electrical Pits
|  | Electrical Pits - Clean inside & in good condition |  | Clean inside and in good condition | Electrical Pits
|  | Electrical Pits - Photos |  | Photos | Electrical Pits
Switchboards
| Scope |  |  | Site QA | Switchboards
Rows
|  | Switchboards | dynamic | Switchboards | Site QA
Columns
|  | Area ready to start work |  | Area ready to start work
|  | Spatial certificate signed if required |  | Spatial certificate signed if required
|  | Fixings installed in wall correctly if board is wall mounted |  | Fixings installed in wall correctly if board is wall mounted
|  | All clearances sighted to ensure location is compliant |  | All clearances sighted to ensure location is compliant
|  | All cables correctly installed in protection device & earth & neutral bars & fully secured |  | All cables correctly installed in protection device and earth and neutral bars and fully secured
|  | Cables neatly dressed |  | Cables neatly dressed
|  | Phase tabs on chassy covered |  | Phase tabs on chassy covered
|  | All earths & neutrals labelled to match phase numbers |  | All earths and neutrals labelled to match phase numbers
|  | Switchboard is clean on the inside & outside |  | Switchboard is clean on the inside and outside
|  | Masking blanks installed |  | Masking blanks installed
|  | DB legend installed |  | DB legend installed
|  | Feisst label on the door installed |  | Feisst label on the door installed
|  | Photos |  | Photos
1st Fix Interior
| Scope |  |  | Site QA | 1st Fix Interior
Rows
|  | 1st Fix Interior | dynamic | 1st Fix Interior | Site QA
Columns
|  | Area ready to start work |  | Area ready to start work | Details
|  | Flushboxes - Height as per plan |  | Height as per plan | Flushboxes
|  | Flushboxes - Location as per plan |  | Location as per plan | Flushboxes
|  | Flushboxes - Fire rated boxes installed where necessary |  | Fire rated boxes installed where necessary | Flushboxes
|  | Flushboxes - Acoustic boxes installed where necessary |  | Acoustic boxes installed where necessary | Flushboxes
|  | Flushboxes - Flushboxes not back to back on Acoustic/Fire Walls |  | Flushboxes not back to back on Acoustic / Fire Walls | Flushboxes
|  | Flushboxes - Intumescent Pad in Place |  | Intumescent Pad in Place | Flushboxes
|  | Cat Wires - 300mm Seperation Between Power & Data |  | 300mm Seperation Between Power & Data | Cat Wires
|  | Cat Wires - Supported every 6 Meters or Adequately to avoid Sagging |  | Supported every 6 Meters or Adequately to avoid Sagging | Cat Wires
|  | Cat Wires - Correctly Secured at Each End |  | Correctly Secured at Each End | Cat Wires
|  | Cat Wires - Turn Buckle Installed & Accessible |  | Turn Buckle Installed and Accessible | Cat Wires
|  | Cat Wires - Number of cables per cat wire. 8 maximum or as per electrical spec |  | Number of cables per cat wire. 8 maximum or as per electrical spec | Cat Wires
|  | Cat Wires - Separation between other services maintained |  | Separation between other services maintained | Cat Wires
|  | Cat Wires - All cables secured via cable ties with ends cut |  | All cables secured via cable ties with ends cut | Cat Wires
|  | Cabling - Power cables installed correctly incl. correct type & size |  | Power cables installed correctly incl. correct type & size | Cabling
|  | Cabling - Power cables - Type & Size | Type & Size | Details | Cabling
|  | Cabling - Lighting cables installed correctly incl. correct type & size |  | Lighting cables installed correctly incl. correct type & size | Cabling
|  | Cabling - Lighting cables - Type & Size | Type & Size | Details | Cabling
|  | Cabling - Switching/Control cables installed correctly |  | Switching / Control cables installed correctly | Cabling
|  | Cabling - Circuits clearly labelled |  | Circuits clearly labelled | Cabling
|  | Cabling - Separation between Data & Power at 300mm or as specified |  | Separation between Data and Power at 300mm or as specified | Cabling
|  | Cable Tray - Minimum 25% spare capacity left on cable tray |  | Minimum 25% spare capacity left on cable tray | Cable Tray
|  | QA - Lights - Setout Correct |  | Setout Correct | QA - Lights
|  | QA - Lights - General Lighting Cabling installed & in correct locations |  | General Lighting Cabling installed and in correct locations | QA - Lights
|  | QA - Lights - Dali Cabling installed & in correct locations |  | Dali Cabling installed and in correct locations | QA - Lights
|  | QA - Lights - PIR Sensor Cabling Installed & in correct locations |  | PIR Sensor Cabling Installed and in correct locations | QA - Lights
|  | QA - Lights - Emergency/ Exit Lighting Cabling Installed & in correct locations |  | Emergency/ Exit Lighting Cabling Installed and in correct locations | QA - Lights
|  | QA - Lights - Nogging installed for surface mounted fittings if required |  | Nogging installed for surface mounted fittings if required | QA - Lights
|  | Photos |  | Photos | Photos
2nd Fix Interior
| Scope |  |  | Site QA | 2nd Fix Interior
Rows
|  | 2nd Fix Interior | dynamic | 2nd Fix Interior | Site QA
Columns
|  | Area ready to start work |  | Area ready to start work | Details
|  | Power Outlets - Correct type installed |  | Correct type installed | Power Outlets
|  | Power Outlets - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Power Outlets
|  | Power Outlets - Outlet Installed level |  | Outlet Installed level | Power Outlets
|  | Power Outlets - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Power Outlets
|  | Power Outlets - Description Labelled on the outlet face with vivid & with dymo labeller on cover plate & ensure label is level |  | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level | Power Outlets
|  | Power Outlets - Photos |  | Photos | Power Outlets
|  | Light Switches - Correct type installed |  | Correct type installed | Light Switches
|  | Light Switches - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Light Switches
|  | Light Switches - Light switch Installed level |  | Light switch Installed level | Light Switches
|  | Light Switches - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Light Switches
|  | Light Switches - Description Labelled on the outlet face with vivid & with dymo labeller on cover plate & ensure label is level |  | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level | Light Switches
|  | Light Switches - Photos |  | Photos | Light Switches
|  | Light Fixtures & PIR Sensors - Correct type installed |  | Correct type installed | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Tested for operation |  | Tested for operation | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Seismic Braces Installed as per design |  | Seismic Braces Installed as per design | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Photos |  | Photos | Light Fixtures & PIR Sensors
1st Fix & 2nd Fix Exterior
| Scope |  |  | Site QA | 1st Fix & 2nd Fix Exterior
Rows
|  | 1st Fix & 2nd Fix Exterior | dynamic | 1st Fix & 2nd Fix Exterior | Site QA
Columns
|  | Details - Area ready to start work |  | Area ready to start work | Details
|  | Cabling - Lighting cables installed correctly incl. correct type & size |  | Lighting cables installed correctly incl. correct type & size | Cabling
|  | Cabling - Lighting cables Type & Size | Type & Size | Details | Cabling
|  | Cabling - Circuits clearly labelled |  | Circuits clearly labelled | Cabling
|  | Cabling - Photos |  | Photos | Cabling
|  | Light Poles & Light Pole Fitting - Correct Light Pole & Light Fitting type installed |  | Correct Light Pole & Light Fitting type installed | Light Poles & Light Pole Fitting
|  | Light Poles & Light Pole Fitting - Light Pole is Level |  | Light Pole is Level | Light Poles & Light Pole Fitting
|  | Light Poles & Light Pole Fitting - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Light Poles & Light Pole Fitting
|  | Light Poles & Light Pole Fitting - Insulation removed from poles & fittings |  | Insulation removed from poles & fittings | Light Poles & Light Pole Fitting
|  | Light Poles & Light Pole Fitting - Tested for operation |  | Tested for operation | Light Poles & Light Pole Fitting
|  | Light Poles & Light Pole Fitting - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Light Poles & Light Pole Fitting
|  | Light Poles & Light Pole Fitting - Photos |  | Photos | Light Poles & Light Pole Fitting
|  | Drive Thru Island Equipment - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Drive Thru Island Equipment
|  | Drive Thru Island Equipment - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Drive Thru Island Equipment
|  | Drive Thru Island Equipment - Photos |  | Photos | Drive Thru Island Equipment
FEL SM Weekly Site Progress
| Scope |  |  | FEL SM Weekly Site Checklist
Rows
|  | FEL SM Weekly Site Checklist | dynamic | FEL SM Weekly Site Checklist
Columns
|  | Prestart Meeting with Team |  | Prestart Meeting with Team
|  | Review Tasks for the week |  | Review Tasks for the week
|  | Identify Targets Including Hours |  | Identify Targets Including Hours
|  | Approve hours by 9AM for previous week |  | Approve hours by 9AM for previous week
|  | Review SWMS |  | Review SWMS
|  | Site Toolbox Meeting |  | Site Toolbox Meeting
|  | SSSP in Order |  | SSSP in Order
|  | Materials organized for week ahead |  | Materials organized for week ahead
|  | Plans printed with any relevant notes added |  | Plans printed with any relevant notes added
|  | Submit Toolbox minutes to main contractor and FEL office |  | Submit Toolbox minutes to main contractor and FEL office
|  | Job Cards up to date and submitted |  | Job Cards up to date and submitted
|  | Team tasks for week ahead filled out on whiteboard |  | Team tasks for week ahead filled out on whiteboard