## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Project Details
section | Details
checkpoint-no-status | Project Details:
textbox | Project Number:
textbox | Builder:
textbox | Project Manager:
checklist | SWMS
section | Details
checkpoint | SWMS & Safety Plan submitted
checklist | Toolbox Meetings (Site Meetings)
section | Details
checkpoint | Site Meetings
checklist | Working Permits
section | Details
checkpoint | Please take a photo of work permit
textbox | Description of Permit
textbox | Work Area
checklist | Delivery Docket
section | Details
checkpoint | Please take photo of delivery docket
textbox | Date
textbox | Work Area
textbox | Material
textbox | Supplier/Subcontractor
checklist | Installation Overview
section | Details
checkpoint | Installation progress - Weekly Photo's of highlighted plans required
checklist | Cassette Rough In
section | Rough In
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | vibration mounts installed
checkpoint | Condensate drain installed including hose clamps
checkpoint | Refrigeration pipework installed including insulation over flare nuts
checkpoint | (Fit-Off) Fascia fitted square and plugged loom connected
checklist | Cassette Commissioning
section | Commissioning.
checkpoint | check drain fitted of at tundish with air break
checkpoint | Check Operation of unit heat/cool & louvre operation
checklist | CHW FCU Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | vibration mounts installed
checkpoint | CHW pipework roughed in and connected to unit
checkpoint | Condensate drains installed to tundish/waste point provided and hose clamps fitted
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | All cushion heads installed, including flexible connections, and set out as per the drawing layout
checkpoint | (Fit-Off) Grilles/louvres installed
checkpoint | (Fit-Off) Filters installed and are removable
checkpoint | (Fit-Off) Check drain fitted off at tundish with air break
checklist | CHW FCU Commissioning
section | Commissioning.
checkpoint | Check Operation of unit
checkpoint | Check for noise and vibration
checklist | BulkHead Ducted Unit Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework roughed in
checkpoint | Condensate drains installed to tundish/waste point provided and hose clamps fitted
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | (Fit-Off) Grilles/louvres installed
checkpoint | (Fit-Off) Filters installed and are removable
checkpoint | (Fit-Off) Condensate drains installed and terminated to correct location and tested
checklist | BulkHead Ducted Unit Commissioning
section | Commissioning.
checkpoint | Check Operation of unit
checkpoint | Check for noise and vibration
checklist | AC Ducted Unit Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework roughed in
checkpoint | Condensate drains installed to tundish/waste point provided and hose clamps fitted
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | All cushion heads installed, including flexible connections, and set out as per the drawing layout
checkpoint | (Fit-Off) Grilles/louvres installed
checkpoint | (Fit-Off) Filters installed and are removable
checkpoint | (Fit-Off) Condensate drains installed and terminated to correct location and tested
checklist | AC Ducted Unit Commissioning
section | Commissioning.
checkpoint | Check Operation of unit
checkpoint | Check for noise and vibration
checklist | AC High wall mounted Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Refrigeration pipework roughed in to correct location
checkpoint | Condensate drains installed to tundish/waste point provided
checkpoint | (Fit-Off) The wall mount was fitted off and checked for level
checkpoint | (Fit-Off) Condensate drains terminated at tundish and tested
checklist | AC Outdoor unit (Stand Alone) Fit Off
section | Fit Off.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Condensate drains installed to tundish/waste point provided
checkpoint | System pressure tested to 400PSI
checklist | AC Outdoor unit (Stand Alone) Commissioning
section | Commissioning.
checkpoint | System evacuated and valves opened
checkpoint | Operation checked
checklist | AC Branch Box Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Model Number correct & Labelled
checkpoint | Vibration mounts installed
checklist | Branch Box Pipe & Drains
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Refrigeration pipework roughed in
checkpoint | Condensate drain pipework installed and hose clamps fitted
checklist | Fans Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | All cushion heads installed, including flexible connections, and set out as per the drawing layout
checkpoint | (Fit-Off) Filters installed and are removable
checkpoint | (Fit-Off) Grilles/louvres installed
checklist | Fan Commissioning
section | Commissioning.
checkpoint | Check for noise and vibration
checklist | Evap Cooler Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Water connection complete
checkpoint | Drain to point of discharge installed
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | (Fit-Off) Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | (Fit-Off) All cushion heads installed, including flexible connections, and set out as per the drawing layout
checklist | Evap Commissioning
section | Commissioning.
checkpoint | Unit Operational, checked for vibration and noise
checklist | AHU Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework roughed in
checkpoint | Condensate drains installed to tundish/waste point provided and hose clamps fitted
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | All cushion heads installed, including flexible connections, and set out as per the drawing layout
checkpoint | (Fit-Off) Grilles/louvres installed
checkpoint | (Fit-Off) Filters installed and are removable
checkpoint | (Fit-Off) Condensate drains terminated at tundish and tested
checklist | AHU Commissioning
section | Commissioning.
checkpoint | Unit Operational, checked for vibration and noise
checklist | ERV Rough In
section | Rough In.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework roughed in
checkpoint | Condensate drains installed to tundish/waste point provided and hose clamps fitted
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | Cowls installed
checkpoint | All cushion heads installed, including flexible connections, and set out as per the drawing layout
checkpoint | (Fit-Off) Grilles/louvres installed
checkpoint | (Fit-Off) Filters installed and are removable
checkpoint | (Fit-Off) Check drain fitted of at tundish with air break
checklist | ERV Commissioning
section | Commissioning.
checkpoint | Unit Operational, checked for vibration and noise
checklist | MSSB Checklist
section | Details
checkpoint | MSSB mounted in position
checkpoint | MSSB Fitted off
checkpoint | Main power connected to MSSB
checklist | Fire Damper & Pipework Penetration Checklist
section | Details
checkpoint | Fire treatment was installed correctly as per the Drawing, sealed and labelled with Photo on both sides.
checklist | CHW & HHW Pipework
section | Details
checkpoint | Pipework installed as per Shop Drawings & Schematic
checkpoint | Pipework Pressure Tested
checkpoint | Pipework checked for leaks & Labelled correctly
checkpoint | Pipework lagging and cladding complete
checklist | Refrigeration Pipe
section | Details
checkpoint | Pipework installed as per Schematic and Shop Drawings
checkpoint | Actual Pipe Meters Recorded on schematic
checkpoint | Pipework Pressure Tested @400 psi
checklist | Demo
section | Details
checkpoint | All flexible connections & cushion heads Demo as per drawing.
checkpoint | All Rubbish Removed Area Clean And Tidy
checklist | Demo & Decommission
section | Details
checkpoint | Electrical isolated and made safe
checkpoint | All Rubbish Removed Area Clean And Tidy
checklist | Radiators (HHW) Rough In
section | Rough In.
checkpoint | backing plate installed prior to plaster
checklist | Radiators (HHW) Fit Off
section | Fit Off.
checkpoint | (Fit-Off) Radiator Installed c/w pipework covers
checkpoint | (Fit-Off) Checked for leaks
checkpoint | (Fit-Off) Low temperature cover installed (As Applicable)
checklist | Boiler
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Pipework connected and no leaks
checkpoint | Gas connected and leak tested
checkpoint | Flue installed
checkpoint | Operation tested
checklist | Pumps
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework connected and no leaks
checkpoint | Operation tested
checklist | Chiller
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework connected and no leaks
checkpoint | Operation tested
checklist | Expansion Tank
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Pipework connected and no leaks
checklist | Auto Refill Units
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Pipework connected and no leaks
checklist | Defect
section | Details
checkpoint | Defect rectified
checklist | VAV
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | VAV installed, Model Number correct & unit Labelled
checklist | AC Outdoor unit (VRF) Fit Off
section | Fit Off.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Condensate drains installed to tundish/waste point provided
checkpoint | System pressure tested to 400PSI
checklist | AC Outdoor unit (VRF) Commissioning
section | Commissioning.
checkpoint | System evacuated and valves opened - Photo of vac stat required
checkpoint | Operation checked
checklist | AC Outdoor unit (VRV) Fit Off
section | Fit Off.
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | Condensate drains installed to tundish/waste point provided
checkpoint | System pressure tested to 400PSI
checklist | AC Outdoor unit (VRV) Commissioning
section | Commissioning.
checkpoint | System evacuated and valves opened - Photo of vac stat required
checkpoint | Operation checked
checklist | Package Unit
section | Details
checkpoint | Unit Model Number correct & Labelled with a clear photo of Both Model & Serial Numbers
checkpoint | Vibration mounts installed
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | Overflashings installed
checkpoint | Drains installed to waste point
checkpoint | Operation tested
checklist | Roof Cowl (RC)
section | Details
checkpoint | RC Model Number correct, installed & RC Labelled
checklist | Flexible Connection & Cushin Heads
section | Details
checkpoint | All flexible connections & cushion heads are Installed s per drawings, including ductwork connections.
checklist | Ductwork/Fire Damper
section | Details
checkpoint | All solid ductwork installed as per drawings.
checkpoint | FireDamper installed
checkpoint | Grilles/louvres installed
checklist | Ductwork
section | Details
checkpoint | All solid ductwork installed as per drawings.
checkpoint | Blank end installed
checkpoint | Grilles/louvres installed
checklist | AC Ducted Unit Ductwork
section | Details
checkpoint | All solid ductwork installed as per drawings, including flexible connections
checkpoint | Grilles/louvres installed
checklist | Ductwork Rough In
section | Rough In.
checkpoint | All weatherproof louvre installed as per drawings, including sealed & cleaned
checkpoint | All solid ductwork installed as per drawings, including flexible / Spiral Duct connections
checkpoint | Dampers installed (NRD, VC, FD, MVCD) and all fully opened
checkpoint | (Fit-Off) Duct Blank Connected, as per drawing
checklist | Rangehood Rough In
section | Rough In.
checkpoint | All weatherproof louvre installed as per drawings, including sealed & cleaned
checkpoint | All solid ductwork installed as per drawings, including flexible / Spiral Duct connections
checkpoint | All flexible ductwork installed
checklist | Low Profile PVC Ducting
section | Details
checkpoint | All PVC ductwork installed as per drawings, including flexible connections.