## Site QA Sheet
Date
Project | Work Elements | Building Levels | Checklists pulled from (Master Checklists Tab)
Folder Tier - 1 | Folder Tier - 2 | Folder Tier - 3 | Folder Tier - 4
Site QA
z | z | z | z | z | z

## MCL Index
| Type | Name | Values | Prefix | Postfix
1 | checklist | Add New Task
2 | checklist | Installation Drainage (In-ground)
3 | checklist | Installation Stack & Vent
4 | checklist | Installation Waste & Vent
5 | checklist | Installation Cast-in Waste & Vent
6 | checklist | Installation Downpipe & Overflow
7 | checklist | Installation Pump Line
8 | checklist | Installation Suction Line
9 | checklist | Installation Authority Main to Meter
10 | checklist | Installation Water Service (In-ground)
11 | checklist | Installation Water Service (Mains/Risers)
12 | checklist | Installation Water Service (Rough-ins)
13 | checklist | Installation Backflow Prevention Device
14 | checklist | Installation Water Meter
15 | checklist | Installation Gas Service (In-ground)
16 | checklist | Installation Gas Service (Mains/Risers)
17 | checklist | Installation Gas Service (Rough-ins)
18 | checklist | Installation Penetration
19 | checklist | Fit-off Toilet & Cistern
20 | checklist | Fit-off Urinal & Cistern
21 | checklist | Fit-off Wash Basin & Tapware
22 | checklist | Fit-off Shower & Tapware
23 | checklist | Fit-off Bath & Tapware
24 | checklist | Fit-off Kitchen Sink & Tapware
25 | checklist | Fit-off Dishwasher
26 | checklist | Fit-off Laundry Trough & Tapware
27 | checklist | Fit-off Washing Machine Stops
28 | checklist | Fit-off Tundish
29 | checklist | Fit-off Hose Tap
30 | checklist | Fit-off Gas Appliance
31 | checklist | Fit-off Cleaners Sink & Tapware
32 | checklist | Installation Hot Water Plant/Unit
33 | checklist | Installation Water Pressure Pump Set
34 | checklist | Installation Pump Station
35 | checklist | Installation Water Storage Tank
36 | checklist | Installation Waste Water Tank
37 | checklist | Testing Drainage Pipework (Air Test)
38 | checklist | Testing Drainage Pipework (Water Test)
39 | checklist | Testing Potable Water Pipework
40 | checklist | Testing Recycled Water Pipework
41 | checklist | Testing Gas Pipework (7kPa or Less)
42 | checklist | Testing Gas Pipework (Above 7kPa)
43 | checklist | Commission Drainage Pump Station
44 | checklist | Commission Water Pressure Pump Set
45 | checklist | Commission Rain Water Pressure Pump Set
46 | checklist | Commission Water Storage Tank
47 | checklist | Commission Hot Water Generating Plant
48 | checklist | Commission Rain Water Diversion Valve
49 | checklist | Commission Thermostatic Mixing Valves
50 | checklist | Commission Reduced Pressure Zone Device
51 | checklist | Commission Fixture Group

## Master Checklists V5
| Type | Project Name | Values | Prefix | Postfix
Checklist Resources V5 - Updated 14/02/2024
1 | checklist | Add New Task
1 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
1 | checkpoint | New task checked off (Add brief description of this task and take photos) | yes, no, n/a
1
2 | checklist | Installation Drainage (In-ground)
2 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
2 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
2 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
2 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
2 | checkpoint | Check for damage & leaks | yes, no, n/a
2 | checkpoint | Check materials & joining methods | yes, no, n/a
2 | checkpoint | Check alignments & levels | yes, no, n/a
2 | checkpoint | Check bedding & clearances | yes, no, n/a
2 | checkpoint | Check connections to pits, tanks, & pump stations, etc | yes, no, n/a
2 | checkpoint | Check covers, venting, & electrical conduits, etc | yes, no, n/a
2 | checkpoint | Check pipework & traps are clear of debris | yes, no, n/a
2 | checkpoint | Check inspection openings | yes, no, n/a
2 | checkpoint | Check open ends are sealed | yes, no, n/a
2 | checkpoint | Check pipe trench marking tape (if specified) | yes, no, n/a
2 | checkpoint | Check trench backfill & compaction | yes, no, n/a
2
3 | checklist | Installation Stack & Vent
3 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
3 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
3 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
3 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
3 | checkpoint | Check for damage & leaks | yes, no, n/a
3 | checkpoint | Check materials & joining methods | yes, no, n/a
3 | checkpoint | Check alignments & levels | yes, no, n/a
3 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
3 | checkpoint | Check expansion joints and anchor points | yes, no, n/a
3 | checkpoint | Check inspection openings | yes, no, n/a
3 | checkpoint | Check pipework is clear of debris | yes, no, n/a
3 | checkpoint | Check open ends are sealed | yes, no, n/a
3 | checkpoint | Check acoustic insulation (if specified) | yes, no, n/a
3 | checkpoint | Check pipe labelling | yes, no, n/a
3 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
3 | checkpoint | Check vents are run to atmosphere and weather proofing is complete | yes, no, n/a
3
4 | checklist | Installation Waste & Vent
4 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
4 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
4 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
4 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
4 | checkpoint | Check for damage & leaks | yes, no, n/a
4 | checkpoint | Check materials & joining methods | yes, no, n/a
4 | checkpoint | Check alignments & levels | yes, no, n/a
4 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
4 | checkpoint | Check expansion joints and anchor points | yes, no, n/a
4 | checkpoint | Check in-wall fixture mounting brackets & concealed cisterns (if specified) | yes, no, n/a
4 | checkpoint | Check in-wall waste pipes & vents | yes, no, n/a
4 | checkpoint | Check inspection openings | yes, no, n/a
4 | checkpoint | Check pipework & traps are clear of debris | yes, no, n/a
4 | checkpoint | Check open ends are sealed | yes, no, n/a
4 | checkpoint | Check acoustic insulation (if specified) | yes, no, n/a
4 | checkpoint | Check pipe labelling | yes, no, n/a
4 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
4 | checkpoint | Check vents are run to atmosphere and weather proofing is complete | yes, no, n/a
4
5 | checklist | Installation Cast-in Waste & Vent
5 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
5 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
5 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
5 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
5 | checkpoint | Check for damage & leaks | yes, no, n/a
5 | checkpoint | Check materials & joining methods | yes, no, n/a
5 | checkpoint | Check alignments & levels | yes, no, n/a
5 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
5 | checkpoint | Check pipework & traps are clear of debris | yes, no, n/a
5 | checkpoint | Check pipe expansion lagging | yes, no, n/a
5 | checkpoint | Check open ends are sealed | yes, no, n/a
5
6 | checklist | Installation Downpipe & Overflow
6 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
6 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
6 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
6 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
6 | checkpoint | Check for damage & leaks | yes, no, n/a
6 | checkpoint | Check materials & joining methods | yes, no, n/a
6 | checkpoint | Check alignments & levels | yes, no, n/a
6 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
6 | checkpoint | Check expansion joints and anchor points | yes, no, n/a
6 | checkpoint | Check connection to roof & floor outlets | yes, no, n/a
6 | checkpoint | Check inspection openings | yes, no, n/a
6 | checkpoint | Check pipework is clear of debris | yes, no, n/a
6 | checkpoint | Check open ends are sealed | yes, no, n/a
6 | checkpoint | Check acoustic insulation (if specified) | yes, no, n/a
6 | checkpoint | Check pipe labelling | yes, no, n/a
6 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
6
7 | checklist | Installation Pump Line
7 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
7 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
7 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
7 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
7 | checkpoint | Check for damage & leaks | yes, no, n/a
7 | checkpoint | Check materials & joining methods | yes, no, n/a
7 | checkpoint | Check alignments & levels | yes, no, n/a
7 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
7 | checkpoint | Check pipework is clear of debris | yes, no, n/a
7 | checkpoint | Check open ends are sealed | yes, no, n/a
7 | checkpoint | Check pipe labelling | yes, no, n/a
7 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
7
8 | checklist | Installation Suction Line
8 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
8 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
8 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
8 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
8 | checkpoint | Check for damage & leaks | yes, no, n/a
8 | checkpoint | Check materials & joining methods | yes, no, n/a
8 | checkpoint | Check alignments & levels | yes, no, n/a
8 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
8 | checkpoint | Check pipework is clear of debris | yes, no, n/a
8 | checkpoint | Check open ends are sealed | yes, no, n/a
8 | checkpoint | Check pipe labelling | yes, no, n/a
8 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
8
9 | checklist | Installation Authority Main to Meter
9 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
9 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
9 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
9 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
9 | checkpoint | Check for damage & leaks | yes, no, n/a
9 | checkpoint | Check materials & joining methods | yes, no, n/a
9 | checkpoint | Check alignments & levels | yes, no, n/a
9 | checkpoint | Check bedding & clearances | yes, no, n/a
9 | checkpoint | Check valve connections | yes, no, n/a
9 | checkpoint | Check pipework is clear of debris | yes, no, n/a
9 | checkpoint | Check pipe trench marking tape (if specified) | yes, no, n/a
9 | checkpoint | Check trench backfill & compaction | yes, no, n/a
9 | checkpoint | Check water meter assemblies | yes, no, n/a
9 | checkpoint | Check RPZD assemblies (if specified) | yes, no, n/a
9 | checkpoint | Check pipe labelling | yes, no, n/a
9
10 | checklist | Installation Water Service (In-ground)
10 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
10 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
10 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
10 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
10 | checkpoint | Check for damage & leaks | yes, no, n/a
10 | checkpoint | Check materials & joining methods | yes, no, n/a
10 | checkpoint | Check alignments & levels | yes, no, n/a
10 | checkpoint | Check bedding & clearances | yes, no, n/a
10 | checkpoint | Check valve connections | yes, no, n/a
10 | checkpoint | Check pipework is clear of debris | yes, no, n/a
10 | checkpoint | Check open ends are sealed | yes, no, n/a
10 | checkpoint | Check pipe colour coding | yes, no, n/a
10 | checkpoint | Check pipe trench marking tape (if specified) | yes, no, n/a
10 | checkpoint | Check trench backfill & compaction | yes, no, n/a
10
11 | checklist | Installation Water Service (Mains/Risers)
11 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
11 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
11 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
11 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
11 | checkpoint | Check for damage & leaks | yes, no, n/a
11 | checkpoint | Check crimp fittings | yes, no, n/a
11 | checkpoint | Check materials & joining methods | yes, no, n/a
11 | checkpoint | Check alignments & levels | yes, no, n/a
11 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
11 | checkpoint | Check expansion joints and anchor points | yes, no, n/a
11 | checkpoint | Check isolation & pressure reduction valves & meter assemblies | yes, no, n/a
11 | checkpoint | Check hot water pipe clips & thermal insulation (if specified) | yes, no, n/a
11 | checkpoint | Check pipework is clear of debris | yes, no, n/a
11 | checkpoint | Check for cross connections | yes, no, n/a
11 | checkpoint | Check open ends are sealed | yes, no, n/a
11 | checkpoint | Check pipe labelling | yes, no, n/a
11 | checkpoint | Check pipe colour coding | yes, no, n/a
11 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
11
12 | checklist | Installation Water Service (Rough-ins)
12 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
12 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
12 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
12 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
12 | checkpoint | Check for damage & leaks | yes, no, n/a
12 | checkpoint | Check pipework can not be holed by plaster screws | yes, no, n/a
12 | checkpoint | Check crimp fittings | yes, no, n/a
12 | checkpoint | Check for cross connections | yes, no, n/a
12 | checkpoint | Check alignment & levels | yes, no, n/a
12 | checkpoint | Check materials & joining methods | yes, no, n/a
12 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
12 | checkpoint | Check TMV/TV | yes, no, n/a
12 | checkpoint | Check in-wall mixer bodies & lugged elbows | yes, no, n/a
12 | checkpoint | Check in-wall fixture mounting brackets & concealed cisterns (if specified) | yes, no, n/a
12 | checkpoint | Check noggins for future fixture | yes, no, n/a
12 | checkpoint | Check sharp edge pipe protection | yes, no, n/a
12 | checkpoint | Check heat trace (if specified) | yes, no, n/a
12 | checkpoint | Check hot water pipe clips & thermal insulation (if specified) | yes, no, n/a
12 | checkpoint | Check pipe colour coding | yes, no, n/a
12 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
12
13 | checklist | Installation Backflow Prevention Device
13 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
13 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
13 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
13 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
13 | checkpoint | RPZD Details: | yes, no, n/a
13 | text | RPZD Serial Number:
13 | text | RPZD Location:
13 | text | RPZD Size:
13 | dropdown |  | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
13 | checkpoint | Check for damage & leaks | yes, no, n/a
13 | checkpoint | Check materials & joining methods | yes, no, n/a
13 | checkpoint | Check alignments & levels | yes, no, n/a
13 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
13 | checkpoint | Check pressure relief pipe to tundish | yes, no, n/a
13
14 | checklist | Installation Water Meter
14 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
14 | checkpoint | Water Meter Details: | yes, no, n/a
14 | text | Meter Type:
14 | text | Meter Number:
14 | text | Meter Location:
14 | text | Meter Size:
14 | dropdown |  | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
14 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
14 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
14 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
15 | checkpoint | Check for damage & leaks | yes, no, n/a
15 | checkpoint | Check materials & joining methods | yes, no, n/a
15 | checkpoint | Check alignments & levels | yes, no, n/a
14
15 | checklist | Installation Gas Service (In-ground)
15 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
15 | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
15 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
15 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
15 | checkpoint | Check for damage & leaks | yes, no, n/a
15 | checkpoint | Check materials & joining methods | yes, no, n/a
15 | checkpoint | Check alignments & levels | yes, no, n/a
15 | checkpoint | Check bedding & clearances | yes, no, n/a
15 | checkpoint | Check valve connections | yes, no, n/a
15 | checkpoint | Check pipework is clear of debris | yes, no, n/a
15 | checkpoint | Check open ends are sealed | yes, no, n/a
15 | checkpoint | Check pipe colour coding | yes, no, n/a
15 | checkpoint | Check pipe trench marking tape (if specified) | yes, no, n/a
15 | checkpoint | Check trench backfill & compaction | yes, no, n/a
15
16 | checklist | Installation Gas Service (Mains/Risers)
16 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
16 | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
16 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
16 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
16 | checkpoint | Check for damage & leaks | yes, no, n/a
16 | checkpoint | Check materials & joining methods | yes, no, n/a
16 | checkpoint | Check crimp fittings | yes, no, n/a
16 | checkpoint | Check alignments & levels | yes, no, n/a
16 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
16 | checkpoint | Check valves & meter assemblies | yes, no, n/a
16 | checkpoint | Check valves & meter assemblies fixings & brackets | yes, no, n/a
16 | checkpoint | Check pipework is clear of debris | yes, no, n/a
16 | checkpoint | Check for cross connections | yes, no, n/a
16 | checkpoint | Check open ends are sealed | yes, no, n/a
16 | checkpoint | Check pipe colour coding | yes, no, n/a
16 | checkpoint | Check pipe labelling | yes, no, n/a
16 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
16
17 | checklist | Installation Gas Service (Rough-ins)
17 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
17 | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
17 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
17 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
17 | checkpoint | Check for damage & leaks | yes, no, n/a
17 | checkpoint | Check pipework can not be holed by plaster screws | yes, no, n/a
17 | checkpoint | Check crimp fittings | yes, no, n/a
17 | checkpoint | Check for cross connections | yes, no, n/a
17 | checkpoint | Check alignment & levels | yes, no, n/a
17 | checkpoint | Check materials & joining methods | yes, no, n/a
17 | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation) | yes, no, n/a
17 | checkpoint | Check lugged elbows | yes, no, n/a
17 | checkpoint | Check noggings for future fixture | yes, no, n/a
17 | checkpoint | Check sharp edge pipe protection | yes, no, n/a
17 | checkpoint | Check pipe colour coding | yes, no, n/a
17 | checkpoint | Check floor/wall penetration fire proofing | yes, no, n/a
17
18 | checklist | Installation Penetration
18 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
18 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
18 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
18 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
18 | checkpoint | Check for damage & missing penos | yes, no, n/a
18 | checkpoint | Check penetration sizes, locations & finished levels are correct | yes, no, n/a
18 | checkpoint | Check fire collars types & ratings are correct | yes, no, n/a
18 | checkpoint | Check blank sleeves are correct | yes, no, n/a
18 | checkpoint | Check cast-in outlets location & finished levels are correct | yes, no, n/a
18 | checkpoint | Check open ends are sealed | yes, no, n/a
18
19 | checklist | Fit-off Toilet & Cistern
19 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
19 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
19 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
19 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
19 | checkpoint | Check for damage or leaks | yes, no, n/a
19 | checkpoint | Check fixing points are secure | yes, no, n/a
19 | checkpoint | Check level & alignment | yes, no, n/a
19 | checkpoint | Check mini stops | yes, no, n/a
19 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
19 | checkpoint | Check special DDA accessories (if applicable) | yes, no, n/a
19 | checkpoint | Check all functions, controls & remote sensors for correct operation | yes, no, n/a
19 | checkpoint | Check trap is clear of debris | yes, no, n/a
19 | checkpoint | Check caulking | yes, no, n/a
19
20 | checklist | Fit-off Urinal & Cistern
20 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
20 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
20 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
20 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
20 | checkpoint | Check for damage or leaks | yes, no, n/a
20 | checkpoint | Check fixing points are secure | yes, no, n/a
20 | checkpoint | Check level & alignment | yes, no, n/a
20 | checkpoint | Check mini stops | yes, no, n/a
20 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
20 | checkpoint | Check button assembly | yes, no, n/a
20 | checkpoint | Check all functions, controls & remote sensors for correct operation | yes, no, n/a
20 | checkpoint | Check trap is clear of debris | yes, no, n/a
20 | checkpoint | Check caulking is correct | yes, no, n/a
20
21 | checklist | Fit-off Wash Basin & Tapware
21 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
21 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
21 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
21 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
21 | checkpoint | Check for damage or leaks | yes, no, n/a
21 | checkpoint | Check fixing points are secure | yes, no, n/a
21 | checkpoint | Check level & alignment | yes, no, n/a
21 | checkpoint | Check mini stops | yes, no, n/a
21 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
21 | checkpoint | Check special DDA accessories (if applicable) | yes, no, n/a
21 | checkpoint | Check waste & trap connections | yes, no, n/a
21 | checkpoint | Check all functions, controls & remote sensors for correct operation | yes, no, n/a
21 | checkpoint | Check trap is clear of debris | yes, no, n/a
21 | checkpoint | Check caulking | yes, no, n/a
21 |  |  | yes, no, n/a
22 | checklist | Fit-off Shower & Tapware
22 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
22 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
22 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
22 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
22 | checkpoint | Check for damage or leaks | yes, no, n/a
22 | checkpoint | Check fixing points are secure | yes, no, n/a
22 | checkpoint | Check level & alignment | yes, no, n/a
22 | checkpoint | Check wall plates, mixers & diversion valves | yes, no, n/a
22 | checkpoint | Check outlets, wall rails & hand showers | yes, no, n/a
22 | checkpoint | Check special DDA accessories (if applicable) | yes, no, n/a
22 | checkpoint | Check waste & trap connections | yes, no, n/a
22 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
22 | checkpoint | Check floor grate level & alignment | yes, no, n/a
22 | checkpoint | Check trap is clear of debris | yes, no, n/a
22 | checkpoint | Check caulking | yes, no, n/a
22
23 | checklist | Fit-off Bath & Tapware
23 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
23 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
23 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
23 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
23 | checkpoint | Check for damage or leaks | yes, no, n/a
23 | checkpoint | Check fixing points are secure | yes, no, n/a
23 | checkpoint | Check level & alignment | yes, no, n/a
23 | checkpoint | Check wall plates, mixers & diversion valves | yes, no, n/a
23 | checkpoint | Check outlets, wall rails & hand showers | yes, no, n/a
23 | checkpoint | Check special DDA accessories (if applicable) | yes, no, n/a
23 | checkpoint | Check waste & trap connections | yes, no, n/a
23 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
23 | checkpoint | Check floor grate level & alignment | yes, no, n/a
23 | checkpoint | Check trap is clear of debris | yes, no, n/a
23 | checkpoint | Check caulking | yes, no, n/a
23
24 | checklist | Fit-off Kitchen Sink & Tapware
24 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
24 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
24 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
24 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
24 | checkpoint | Check for damage or leaks | yes, no, n/a
24 | checkpoint | Check fixing points are secure | yes, no, n/a
24 | checkpoint | Check level & alignment | yes, no, n/a
24 | checkpoint | Check mini stops | yes, no, n/a
24 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
24 | checkpoint | Check waste & trap connections | yes, no, n/a
24 | checkpoint | Check dishwasher waste & water connections | yes, no, n/a
24 | checkpoint | Check stop valves for future connections are capped | yes, no, n/a
24 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
24 | checkpoint | Check trap is clear of debris | yes, no, n/a
24 | checkpoint | Check caulking | yes, no, n/a
24
25 | checklist | Fit-off Dishwasher
25 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
25 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
25 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
25 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
25 | checkpoint | Check for damage or leaks | yes, no, n/a
25 | checkpoint | Check fixing points are secure | yes, no, n/a
25 | checkpoint | Check level & alignment | yes, no, n/a
25 | checkpoint | Check isolation valves & non-return valves | yes, no, n/a
25 | checkpoint | Check pressure reduction valve (if specified) | yes, no, n/a
25 | checkpoint | Check flexible waste & water hoses are not twisted or kinked | yes, no, n/a
25 | checkpoint | Check flexible waste hose height under cabinet | yes, no, n/a
25 | checkpoint | Check waste connection to trap | yes, no, n/a
25 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
25
26 | checklist | Fit-off Laundry Trough & Tapware
26 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
26 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
26 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
26 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
26 | checkpoint | Check for damage or leaks | yes, no, n/a
26 | checkpoint | Check fixing points are secure | yes, no, n/a
26 | checkpoint | Check level & alignment | yes, no, n/a
26 | checkpoint | Check mini stops | yes, no, n/a
26 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
26 | checkpoint | Check waste & water connections | yes, no, n/a
26 | checkpoint | Check stop valves for future connections are capped | yes, no, n/a
26 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
26 | checkpoint | Check trap is clear of debris | yes, no, n/a
26 | checkpoint | Check caulking | yes, no, n/a
26
27 | checklist | Fit-off Washing Machine Stops
27 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
27 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
27 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
27 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
27 | checkpoint | Check for damage or leaks | yes, no, n/a
27 | checkpoint | Check level & alignment | yes, no, n/a
27 | checkpoint | Check stops hose connections are capped off | yes, no, n/a
27 |  |  | yes, no, n/a
28 | checklist | Fit-off Tundish
28 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
28 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
28 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
28 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
28 | checkpoint | Check for damage or leaks | yes, no, n/a
28 | checkpoint | Check fixing points are secure | yes, no, n/a
28 | checkpoint | Check level & alignment | yes, no, n/a
28 | checkpoint | Check waste & trap connections | yes, no, n/a
28 | checkpoint | Check trap is clear of debris | yes, no, n/a
28
29 | checklist | Fit-off Hose Tap
29 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
29 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
29 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
29 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
29 | checkpoint | Check for damage or leaks | yes, no, n/a
29 | checkpoint | Vacuum breaker fitted | yes, no, n/a
29 | checkpoint | Check pipe colour coding | yes, no, n/a
29
30 | checklist | Fit-off Gas Appliance
30 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
30 | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
30 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
30 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
30 | checkpoint | Check for damage or leaks | yes, no, n/a
30 | checkpoint | Check fixing points are secure | yes, no, n/a
30 | checkpoint | Check level & alignment is correct | yes, no, n/a
30 | checkpoint | Check surrounding wall material is fire rated | yes, no, n/a
30 | checkpoint | Check distance from cook-top to range hood complies with manufacturer specification | yes, no, n/a
30 | checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification | yes, no, n/a
30 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
30 | checkpoint | Check gas isolation valve | yes, no, n/a
30 | checkpoint | Check gas pressure regulator | yes, no, n/a
30 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
30
31 | checklist | Fit-off Cleaners Sink & Tapware
31 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
31 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint) | yes, no, n/a
31 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
31 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
31 | checkpoint | Check for damage or leaks | yes, no, n/a
31 | checkpoint | Check fixing points are secure | yes, no, n/a
31 | checkpoint | Check level & alignment | yes, no, n/a
31 | checkpoint | Check tapware for fit & function | yes, no, n/a
31 | checkpoint | Check wall brackets & fixings | yes, no, n/a
31 | checkpoint | Check bucket grate | yes, no, n/a
31 | checkpoint | Check waste & trap connections | yes, no, n/a
31 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
31 | checkpoint | Check trap is clear of debris | yes, no, n/a
31 | checkpoint | Check caulking | yes, no, n/a
31
32 | checklist | Installation Hot Water Plant/Unit
32 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
32 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
32 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
32 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
32 | checkpoint | Check for damage or leaks | yes, no, n/a
32 | checkpoint | Check level & alignment | yes, no, n/a
32 | checkpoint | Check safe tray (if specified) | yes, no, n/a
32 | checkpoint | Check isolation valves & non-return valves | yes, no, n/a
32 | checkpoint | Check pressure reduction valve (if specified) | yes, no, n/a
32 | checkpoint | Check flexible connections are not twisted or kinked | yes, no, n/a
32 | checkpoint | Check waste & water connections | yes, no, n/a
32 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
32 | checkpoint | Check water temperatures are as specified | yes, no, n/a
32 | checkpoint | Check electrical power is available | yes, no, n/a
32 | checkpoint | Check solar panels & mounting brackets | yes, no, n/a
32 | checkpoint | Check solar connecting pipework & fittings | yes, no, n/a
32 | checkpoint | Check solar pump operation | yes, no, n/a
32
33 | checklist | Installation Water Pressure Pump Set
33 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
34 | checkpoint | Pump Set Details: | yes, no, n/a
34 | text | Pump Set Type:
34 | dropdown |  | Potable Cold Water,Potable Hot Water,Recycled Rain Water,Non-Potable Water,Other
33 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
33 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
33 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
33 | checkpoint | Check for damage or leaks | yes, no, n/a
33 | checkpoint | Check fixing points are secure | yes, no, n/a
33 | checkpoint | Check level & alignment | yes, no, n/a
33 | checkpoint | Check isolation valves & non-return valves | yes, no, n/a
33 | checkpoint | Check feed & delivery pipe connections | yes, no, n/a
33 | checkpoint | Check back-up water supply by-pass (if specified) | yes, no, n/a
33 | checkpoint | Check Control Panel | yes, no, n/a
33 | checkpoint | Check all functions & controls for correct operation | yes, no, n/a
33 | checkpoint | Check electrical power is available | yes, no, n/a
33 | checkpoint | Check BMS is available | yes, no, n/a
33
34 | checklist | Installation Pump Station
34 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
34 | checkpoint | Pump Station Details: | yes, no, n/a
34 | text | Pump Station Type:
34 | dropdown |  | Sewer Above Ground,Stormwater Above Ground,Sewer In-ground,Stormwater In-ground,Other
34 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
34 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
34 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
34 | checkpoint | Check for damage & leaks | yes, no, n/a
34 | checkpoint | Check materials & joining methods | yes, no, n/a
34 | checkpoint | Check alignments & levels | yes, no, n/a
34 | checkpoint | Check bedding & clearances | yes, no, n/a
34 | checkpoint | Check inlet/outlet connections & vents | yes, no, n/a
34 | checkpoint | Check covers, venting, & electrical conduits, etc | yes, no, n/a
34 | checkpoint | Check pipework & traps are clear of debris | yes, no, n/a
34 | checkpoint | Check inspection openings | yes, no, n/a
34 | checkpoint | Check open ends are sealed | yes, no, n/a
34 | checkpoint | Check trench backfill & compaction | yes, no, n/a
34
35 | checklist | Installation Water Storage Tank
35 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
35 | checkpoint | Tank Details: | yes, no, n/a
35 | text | Tank Type:
35 | dropdown |  | Potable Water Above Ground,Rain Water Above Ground,Potable Water In-ground,Rain Water In-ground,Fire Water Above Ground,Other
35 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
35 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
35 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
35 | checkpoint | Check for damage & leaks | yes, no, n/a
35 | checkpoint | Check materials & joining methods | yes, no, n/a
35 | checkpoint | Check alignments & levels | yes, no, n/a
35 | checkpoint | Check bedding & clearances | yes, no, n/a
35 | checkpoint | Check inlet/outlet connections & vents | yes, no, n/a
35 | checkpoint | Check covers, venting, & electrical conduits, etc | yes, no, n/a
35 | checkpoint | Check pipework & traps are clear of debris | yes, no, n/a
35 | checkpoint | Check inspection openings | yes, no, n/a
35 | checkpoint | Check open ends are sealed | yes, no, n/a
35 | checkpoint | Check trench backfill & compaction | yes, no, n/a
35
36 | checklist | Installation Waste Water Tank
36 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints | yes, no, n/a
36 | checkpoint | Tank Details: | yes, no, n/a
36 | text | Tank Type:
36 | dropdown |  | Grease Interceptor,Neutralizing Pit,POI Interceptor,SW Detention Tank,SW Filtration Pit,Other
36 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint) | yes, no, n/a
36 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
36 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
36 | checkpoint | Check for damage & leaks | yes, no, n/a
36 | checkpoint | Check materials & joining methods | yes, no, n/a
36 | checkpoint | Check alignments & levels | yes, no, n/a
36 | checkpoint | Check bedding & clearances | yes, no, n/a
36 | checkpoint | Check inlet/outlet connections & vents | yes, no, n/a
36 | checkpoint | Check covers, venting, & electrical conduits, etc | yes, no, n/a
36 | checkpoint | Check pipework & traps are clear of debris | yes, no, n/a
36 | checkpoint | Check inspection openings | yes, no, n/a
36 | checkpoint | Check open ends are sealed | yes, no, n/a
36 | checkpoint | Check trench backfill & compaction | yes, no, n/a
36 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 | yes, no, n/a
36 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
36 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
36 | checkpoint | Check installation is clean and ready for testing | yes, no, n/a
36 | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
36
37 | checklist | Testing Drainage Pipework (Air Test)
37 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 | yes, no, n/a
37 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
37 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
37 | checkpoint | Testing kit & equipment have current certification | yes, no, n/a
37 | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
37
38 | checklist | Testing Drainage Pipework (Water Test)
38 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 | yes, no, n/a
38 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
38 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
38 | checkpoint | Testing kit & equipment have current certification | yes, no, n/a
38 | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
38
39 | checklist | Testing Potable Water Pipework
39 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 | yes, no, n/a
39 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
39 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
39 | checkpoint | Check installation is clean and ready for testing | yes, no, n/a
39 | checkpoint | Check all valves, mixers, meters, etc , in the test zone are rated for the test pressure required | yes, no, n/a
39 | checkpoint | Testing kit & equipment have current certification | yes, no, n/a
39 | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
39
40 | checklist | Testing Recycled Water Pipework
40 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 | yes, no, n/a
40 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
40 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
40 | checkpoint | Check installation is clean and ready for testing | yes, no, n/a
40 | checkpoint | Are all valves, meters, etc , rated for the test pressure required | yes, no, n/a
40 | checkpoint | Testing kit & equipment have current certification | yes, no, n/a
40 | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
40 | checkpoint | R3 certification has taken place (Provide photo of or attach PDF copy of the Authority acceptance report) | yes, no, n/a
40
41 | checklist | Testing Gas Pipework (7kPa or Less)
41 | checkpoint | Installation complies with latest revision of AS/NZS-5601 | yes, no, n/a
41 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
41 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
41 | checkpoint | Testing kit & equipment have current certification | yes, no, n/a
41 | checkpoint | Apply test as per latest revision of AS/NZS-5601 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
41
42 | checklist | Testing Gas Pipework (Above 7kPa)
42 | checkpoint | Installation complies with latest revision of AS/NZS-5601 | yes, no, n/a
42 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
42 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
42 | checkpoint | Testing kit & equipment have current certification | yes, no, n/a
42 | checkpoint | Apply test as per latest revision of AS/NZS-5601 (Note: Start & Finish testing photos to be taken only within this Checkpoint) | yes, no, n/a
42
43 | checklist | Commission Drainage Pump Station
43 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
43 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
43 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
43 | checkpoint | Check lifting rails & chains | yes, no, n/a
43 | checkpoint | Check water level sensor set points | yes, no, n/a
43 | checkpoint | Check pump motor rotation | yes, no, n/a
43 | checkpoint | Check dry pump fault | yes, no, n/a
43 | checkpoint | Check low water level fault | yes, no, n/a
43 | checkpoint | Check high water level fault | yes, no, n/a
43 | checkpoint | Check auto pump roll-over | yes, no, n/a
43 | checkpoint | Check pump package operational set points | yes, no, n/a
43 | checkpoint | Check control panel display & set points | yes, no, n/a
43 | checkpoint | Check fault warning alarms | yes, no, n/a
43 | checkpoint | Check BMS connection as specified | yes, no, n/a
43 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint | yes, no, n/a
43
44 | checklist | Commission Water Pressure Pump Set
44 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
44 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
44 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
44 | checkpoint | Check water supply fault | yes, no, n/a
44 | checkpoint | Check pump motor rotation | yes, no, n/a
44 | checkpoint | Check dry pump fault | yes, no, n/a
44 | checkpoint | Check auto pump roll-over | yes, no, n/a
44 | checkpoint | Check pump package operational set points | yes, no, n/a
44 | checkpoint | Check control panel display & set points | yes, no, n/a
44 | checkpoint | Check fault warning alarms | yes, no, n/a
44 | checkpoint | Check BMS connection as specified | yes, no, n/a
44 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint | yes, no, n/a
44
45 | checklist | Commission Rain Water Pressure Pump Set
45 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
45 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
45 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
45 | checkpoint | Check water supply fault | yes, no, n/a
45 | checkpoint | Check pump motor rotation | yes, no, n/a
45 | checkpoint | Check dry pump fault | yes, no, n/a
45 | checkpoint | Check auto pump roll-over | yes, no, n/a
45 | checkpoint | Check ultra violet lamps | yes, no, n/a
45 | checkpoint | Check filters & backwash | yes, no, n/a
45 | checkpoint | Check back-up water supply | yes, no, n/a
45 | checkpoint | Check pump package operational set points | yes, no, n/a
45 | checkpoint | Check control panel display & set points | yes, no, n/a
45 | checkpoint | Check fault warning alarms | yes, no, n/a
45 | checkpoint | Check BMS connection as specified | yes, no, n/a
45 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint | yes, no, n/a
45
46 | checklist | Commission Water Storage Tank
46 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
46 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
46 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
46 | checkpoint | Check valves are fully open | yes, no, n/a
46 | checkpoint | Check water level sensor set points | yes, no, n/a
46 | checkpoint | Check tank fill valve | yes, no, n/a
46 | checkpoint | Check low level fault | yes, no, n/a
46 | checkpoint | Check high level fault | yes, no, n/a
46 | checkpoint | Check passive over-flow | yes, no, n/a
46 | checkpoint | Check statutory warning signage | yes, no, n/a
46 | checkpoint | Check control panel display & set points | yes, no, n/a
46 | checkpoint | Check BMS connection as specified | yes, no, n/a
46 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint | yes, no, n/a
46
47 | checklist | Commission Hot Water Generating Plant
47 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS-5601 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
47 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
47 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
47 | checkpoint | Check valves are fully open | yes, no, n/a
47 | checkpoint | Check water filters are clean | yes, no, n/a
47 | checkpoint | Check gas supply | yes, no, n/a
47 | checkpoint | Check circulating pumps | yes, no, n/a
47 | checkpoint | Check flue operation | yes, no, n/a
47 | checkpoint | Check system auto start | yes, no, n/a
47 | checkpoint | Check flow & return temperatures | yes, no, n/a
47 | checkpoint | Check control panel display & set points | yes, no, n/a
47 | checkpoint | Check BMS connection (if specified) | yes, no, n/a
47 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint | yes, no, n/a
47
48 | checklist | Commission Rain Water Diversion Valve
48 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
48 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
48 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
48 | checkpoint | Check valve operation | yes, no, n/a
48 | checkpoint | Check valve defaults to storm-water if no power or tank full | yes, no, n/a
48 | checkpoint | Check control panel display & set points | yes, no, n/a
48 | checkpoint | Check BMS connection as specified | yes, no, n/a
48 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint | yes, no, n/a
48
49 | checklist | Commission Thermostatic Mixing Valves
49 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
49 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
49 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
49 | checkpoint | Check water temperature does not exceed 45°C | yes, no, n/a
49
50 | checklist | Commission Reduced Pressure Zone Device
50 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
50 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
50 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
50 | checkpoint | RPZD Details: | yes, no, n/a
50 | text | RPZD Serial Number:
50 | text | RPZD Location:
50 | text | RPZD Size:
50 | dropdown |  | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
50 | checkpoint | Check valves are fully open | yes, no, n/a
50 | checkpoint | Check inlet water pressure does not exceed manufacturer specification | yes, no, n/a
50 | checkpoint | Check outlet water pressure is as per manufacturer specification | yes, no, n/a
50 | checkpoint | Check exhaust tundish drain sized to accept a full flush | yes, no, n/a
50 | checkpoint | Provide the commissioning report & all plant documentation to this checkpoint | yes, no, n/a
50
51 | checklist | Commission Fixture Group
51 | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS-5601 (Note: Commissioning photos to be taken only within this Checkpoint) | yes, no, n/a
51 | checkpoint | Installation complies with current drawings & specifications | yes, no, n/a
51 | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | yes, no, n/a
51 | checkpoint | Check for any damage, leaks or missing components | yes, no, n/a
51 | checkpoint | Check level & alignment of all fixtures | yes, no, n/a
51 | checkpoint | Check all fixtures, seats & covers are securely fastened | yes, no, n/a
51 | checkpoint | Check all valves are fully open | yes, no, n/a
51 | checkpoint | Check all flexible connections are not twisted or kinked | yes, no, n/a
51 | checkpoint | Check for water for cross connections | yes, no, n/a
51 | checkpoint | Check fixture wastes & connections | yes, no, n/a
51 | checkpoint | Check pipework & all traps are clear of debris | yes, no, n/a
51 | checkpoint | Check AAV is installed to correct height | yes, no, n/a
51 | checkpoint | Check future connection water valves are securely capped | yes, no, n/a
51 | checkpoint | Check TV do not exceed 50°C | yes, no, n/a
51 | checkpoint | Check TMV do not exceed 45°C | yes, no, n/a
51 | checkpoint | Check dishwasher function | yes, no, n/a
51 | checkpoint | Check gas valves & regulators | yes, no, n/a
51 | checkpoint | Check all gas burner functions | yes, no, n/a
51 | checkpoint | Check balcony hose tap | yes, no, n/a
51 | checkpoint | Check balcony floor grate & downpipe | yes, no, n/a
51 | checkpoint | Check all fixtures & tapware are operating as specified | yes, no, n/a
51 | checkpoint | Confirm area has been left clean | yes, no, n/a
51
| z | z | z | z | z