## zres_siteapp2
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Installation Hot Water Unit |  |  |  |  | Yes | Installation Hot Water Unit | 06d0d903-5cc5-449b-bd3e-8dc752131fcb
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with current AS/NZS-3500
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check safe tray (if specified)
checkpoint-status |  |  | checkpoint | Check isolation valves & non-return valves
checkpoint-status |  |  | checkpoint | Check pressure reduction valve (if specified)
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check waste & water connections
checkpoint-status |  |  | checkpoint | Check operation & controls
checkpoint-status |  |  | checkpoint | Check water temperatures are as specified
checkpoint-status |  |  | checkpoint | Check electrical power is available
checkpoint-status |  |  | checkpoint | Check solar connecting pipework & fittings
checkpoint-status |  |  | checkpoint | Check solar pump operation
checkpoint-status |  |  | checkpoint | Check solar panels & mounting brackets
checkpoint-status |  |  | checkpoint | Must provide photo
checklist-sectioned |  |  | checklist | Fit-off Urinal & Cistern |  |  |  |  | Yes | Fit-off Urinal & Cistern | c6e1ff5c-3a26-4b6e-be4a-f5b572103e93
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check mini stops
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check button assembly
checkpoint-status |  |  | checkpoint | Check all functions, controls & remote sensors for correct operation
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking is correct
checklist-sectioned |  |  | checklist | Installation Waste & Vent |  |  |  |  | Yes | Installation Waste & Vent | 9e4e9015-a20c-4a9f-b33a-a047f75de1e5
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check expansion joints and anchor points
checkpoint-status |  |  | checkpoint | Check in-wall fixture mounting brackets & concealed cisterns (if specified)
checkpoint-status |  |  | checkpoint | Check in-wall waste pipes & vents
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check acoustic insulation (if specified)
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checkpoint-status |  |  | checkpoint | Check vents are run to atmosphere and weather proofing is complete
checklist-sectioned |  |  | checklist | Installation Suction Line |  |  |  |  | Yes | Installation Suction Line | f9196259-17e5-4c53-ab22-f2a7b90187f9
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Testing Potable Water Pipework |  |  |  |  | Yes | Testing Potable Water Pipework | 24e28451-9a06-40a4-882e-e3a414abc593
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check installation is clean and ready for testing
checkpoint-status |  |  | checkpoint | Check all valves, mixers, meters, etc , in the test zone are rated for the test pressure required
checkpoint-status |  |  | checkpoint | Testing kit & equipment have current certification
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
checklist-sectioned |  |  | checklist | Commission Rain Water Pressure Pump Set |  |  |  |  | Yes | Commission Rain Water Pressure Pump Set | 281dda57-8b54-48d5-8f13-a175da212fdf
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check water supply fault
checkpoint-status |  |  | checkpoint | Check pump motor rotation
checkpoint-status |  |  | checkpoint | Check dry pump fault
checkpoint-status |  |  | checkpoint | Check auto pump roll-over
checkpoint-status |  |  | checkpoint | Check ultra violet lamps
checkpoint-status |  |  | checkpoint | Check filters & backwash
checkpoint-status |  |  | checkpoint | Check back-up water supply
checkpoint-status |  |  | checkpoint | Check pump package operational set points
checkpoint-status |  |  | checkpoint | Check control panel display & set points
checkpoint-status |  |  | checkpoint | Check fault warning alarms
checkpoint-status |  |  | checkpoint | Check BMS connection as specified
checkpoint-status |  |  | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Fit-off Toilet & Cistern |  |  |  |  | Yes | Fit-off Toilet & Cistern | ff038281-2cb3-49d7-83e1-9fb919fc7970
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check mini stops
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check special DDA accessories (if applicable)
checkpoint-status |  |  | checkpoint | Check all functions, controls & remote sensors for correct operation
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Installation Drainage (In-ground) |  |  |  |  | Yes | Installation Drainage (In-ground) | 0fb399f7-05cf-45cd-bc21-6ee3d52fc364
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check connections to pits, tanks, & pump stations, etc
checkpoint-status |  |  | checkpoint | Check covers, venting, & electrical conduits, etc
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe trench marking tape (if specified)
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checklist-sectioned |  |  | checklist | Fit-off Tundish |  |  |  |  | Yes | Fit-off Tundish | 7460b090-c31f-4db1-8c9a-ae3c347865a2
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check waste & trap connections
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checklist-sectioned |  |  | checklist | Commission Thermostatic Mixing Valves |  |  |  |  | Yes | Commission Thermostatic Mixing Valves | 2e0f6af0-8d4c-4274-abf2-c7e2f71298a9
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check water temperature does not exceed 45°C
checklist-sectioned |  |  | checklist | Fit-off Gas Appliance |  |  |  |  | Yes | Fit-off Gas Appliance | 8354c1bc-4442-4699-a4f0-f9dcd8a932e9
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment is correct
checkpoint-status |  |  | checkpoint | Check surrounding wall material is fire rated
checkpoint-status |  |  | checkpoint | Check distance from cook-top to range hood complies with manufacturer specification
checkpoint-status |  |  | checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check gas isolation valve
checkpoint-status |  |  | checkpoint | Check gas pressure regulator
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checklist-sectioned |  |  | checklist | Testing Gas Pipework (Above 7kPa) |  |  |  |  | Yes | Testing Gas Pipework (Above 7kPa) | 59546074-f202-493e-85e9-341380b25565
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-5601
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Testing kit & equipment have current certification
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-5601 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
checklist-sectioned |  |  | checklist | Fit-off Dishwasher |  |  |  |  | Yes | Fit-off Dishwasher | 5c05a66d-78ba-4f48-b1b4-4df4fc333459
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check isolation valves & non-return valves
checkpoint-status |  |  | checkpoint | Check pressure reduction valve (if specified)
checkpoint-status |  |  | checkpoint | Check flexible waste & water hoses are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check flexible waste hose height under cabinet
checkpoint-status |  |  | checkpoint | Check waste connection to trap
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checklist-sectioned |  |  | checklist | Fit-off Washing Machine Stops |  |  |  |  | Yes | Fit-off Washing Machine Stops | 61a43617-3217-4b05-b1f9-b3eb30f3d856
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check stops hose connections are capped off
checklist-sectioned |  |  | checklist | Commission Fixture Group |  |  |  |  | Yes | Commission Fixture Group | ba5a25aa-0821-4d17-aa68-ee22cb57f8ba
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS-5601 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for any damage, leaks or missing components
checkpoint-status |  |  | checkpoint | Check level & alignment of all fixtures
checkpoint-status |  |  | checkpoint | Check all fixtures, seats & covers are securely fastened
checkpoint-status |  |  | checkpoint | Check all valves are fully open
checkpoint-status |  |  | checkpoint | Check all flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check for water for cross connections
checkpoint-status |  |  | checkpoint | Check fixture wastes & connections
checkpoint-status |  |  | checkpoint | Check pipework & all traps are clear of debris
checkpoint-status |  |  | checkpoint | Check AAV is installed to correct height
checkpoint-status |  |  | checkpoint | Check future connection water valves are securely capped
checkpoint-status |  |  | checkpoint | Check TV do not exceed 50°C
checkpoint-status |  |  | checkpoint | Check TMV do not exceed 45°C
checkpoint-status |  |  | checkpoint | Check dishwasher function
checkpoint-status |  |  | checkpoint | Check gas valves & regulators
checkpoint-status |  |  | checkpoint | Check all gas burner functions
checkpoint-status |  |  | checkpoint | Check balcony hose tap
checkpoint-status |  |  | checkpoint | Check balcony floor grate & downpipe
checkpoint-status |  |  | checkpoint | Check all fixtures & tapware are operating as specified
checkpoint-status |  |  | checkpoint | Confirm area has been left clean
checklist-sectioned |  |  | checklist | Installation Water Service (Mains/Risers) |  |  |  |  | Yes | Installation Water Service (Mains/Risers) | aaf71683-ecd1-4dfa-8165-ffe2aed51234
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check crimp fittings
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check expansion joints and anchor points
checkpoint-status |  |  | checkpoint | Check isolation & pressure reduction valves & meter assemblies
checkpoint-status |  |  | checkpoint | Check hot water pipe clips & thermal insulation (if specified)
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check for cross connections
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Installation Plant & Equipment |  |  |  |  | Yes | Installation Plant & Equipment | dc297e22-6108-4c20-b06c-80d23a065db2
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Plant & Equipment Installation checked off as below
checkpoint-status |  |  | checkpoint | Installation complies with current AS/NZS-3500 & AS/NZS-5600
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check tundishes are correct
checkpoint-status |  |  | checkpoint | Check electrical power is available
checkpoint-status |  |  | checkpoint | Check BMS is available
checkpoint-status |  |  | checkpoint | Must provide photo
checklist-sectioned |  |  | checklist | Commission Hot Water Generating Plant |  |  |  |  | Yes | Commission Hot Water Generating Plant | 85c9180f-ca28-429c-b86e-493f560af4c3
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS-5601 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check valves are fully open
checkpoint-status |  |  | checkpoint | Check water filters are clean
checkpoint-status |  |  | checkpoint | Check gas supply
checkpoint-status |  |  | checkpoint | Check circulating pumps
checkpoint-status |  |  | checkpoint | Check flue operation
checkpoint-status |  |  | checkpoint | Check system auto start
checkpoint-status |  |  | checkpoint | Check flow & return temperatures
checkpoint-status |  |  | checkpoint | Check control panel display & set points
checkpoint-status |  |  | checkpoint | Check BMS connection (if specified)
checkpoint-status |  |  | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Commission Reduced Pressure Zone Device |  |  |  |  | Yes | Commission Reduced Pressure Zone Device | 061df98d-1c0f-4737-89c8-0ede4c0f8c61
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | RPZD Details:
text | d7ca90c7-008e-5369-a1a7-7c4540d72953 |  | textbox | RPZD Serial Number:
text | 4b7cc0ea-c1b3-53c6-b662-3a63abc77882 |  | textbox | RPZD Location:
select | 35e4ceff-f4cb-5455-8f15-31464e541550 |  | dropdown | RPZD Size: | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
checkpoint-status |  |  | checkpoint | Check valves are fully open
checkpoint-status |  |  | checkpoint | Check inlet water pressure does not exceed manufacturer specification
checkpoint-status |  |  | checkpoint | Check outlet water pressure is as per manufacturer specification
checkpoint-status |  |  | checkpoint | Check exhaust tundish drain sized to accept a full flush
checkpoint-status |  |  | checkpoint | Provide the commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Installation Stack & Vent |  |  |  |  | Yes | Installation Stack & Vent | cfc9afe3-8adc-4a22-8efb-083454fce9a3
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check expansion joints and anchor points
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check acoustic insulation (if specified)
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checkpoint-status |  |  | checkpoint | Check vents are run to atmosphere and weather proofing is complete
checklist-sectioned |  |  | checklist | Testing Drainage Pipework (Hydrostatic Test) |  |  |  |  | Yes | Testing Drainage Pipework (Hydrostatic Test) | 800c0ba6-f4e4-4e2f-bd80-76051af401ef
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with current AS/NZS-3500
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check installation is clean and ready for testing
checkpoint-status |  |  | checkpoint | Apply water pressure test as per AS/NZS-3500
checkpoint-status |  |  | checkpoint | Must provide test start & finish photos
checklist-sectioned |  |  | checklist | Installation Downpipe & Overflow |  |  |  |  | Yes | Installation Downpipe & Overflow | 49d6764f-60cb-4eb6-ba65-7c159c110013
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check expansion joints and anchor points
checkpoint-status |  |  | checkpoint | Check connection to roof & floor outlets
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check acoustic insulation (if specified)
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Commission Rain Water Diversion Valve |  |  |  |  | Yes | Commission Rain Water Diversion Valve | 3cc3a618-2042-4a3a-a75e-8d0904539b88
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check valve operation
checkpoint-status |  |  | checkpoint | Check valve defaults to storm-water if no power or tank full
checkpoint-status |  |  | checkpoint | Check control panel display & set points
checkpoint-status |  |  | checkpoint | Check BMS connection as specified
checkpoint-status |  |  | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Fit-off Laundry Trough & Tapware |  |  |  |  | Yes | Fit-off Laundry Trough & Tapware | 6371715d-0604-447c-a678-20b9f89665d5
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check mini stops
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check waste & water connections
checkpoint-status |  |  | checkpoint | Check stop valves for future connections are capped
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Commission Drainage Pump Station |  |  |  |  | Yes | Commission Drainage Pump Station | f275e65e-ddef-4e07-a351-9892ee647584
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check lifting rails & chains
checkpoint-status |  |  | checkpoint | Check water level sensor set points
checkpoint-status |  |  | checkpoint | Check pump motor rotation
checkpoint-status |  |  | checkpoint | Check dry pump fault
checkpoint-status |  |  | checkpoint | Check low water level fault
checkpoint-status |  |  | checkpoint | Check high water level fault
checkpoint-status |  |  | checkpoint | Check auto pump roll-over
checkpoint-status |  |  | checkpoint | Check pump package operational set points
checkpoint-status |  |  | checkpoint | Check control panel display & set points
checkpoint-status |  |  | checkpoint | Check fault warning alarms
checkpoint-status |  |  | checkpoint | Check BMS connection as specified
checkpoint-status |  |  | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Installation Penetration |  |  |  |  | Yes | Installation Penetration | ffaa1afb-aabe-4725-893a-f91a5e5f2af9
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & missing penos
checkpoint-status |  |  | checkpoint | Check penetration sizes, locations & finished levels are correct
checkpoint-status |  |  | checkpoint | Check fire collars types & ratings are correct
checkpoint-status |  |  | checkpoint | Check blank sleeves are correct
checkpoint-status |  |  | checkpoint | Check cast-in outlets location & finished levels are correct
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checklist-sectioned |  |  | checklist | Testing Recycled Water Pipework |  |  |  |  | Yes | Testing Recycled Water Pipework | 9e0df204-2d66-46b2-9851-f25f7ce862f4
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check installation is clean and ready for testing
checkpoint-status |  |  | checkpoint | Are all valves, meters, etc , rated for the test pressure required
checkpoint-status |  |  | checkpoint | Testing kit & equipment have current certification
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | R3 certification has taken place (Provide photo of or attach PDF copy of the Authority acceptance report)
checklist-sectioned |  |  | checklist | Testing Drainage Pipework (Air Test) |  |  |  |  | Yes | Testing Drainage Pipework (Air Test) | c5fa065b-d737-41a9-9937-2086b0c716b8
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Testing kit & equipment have current certification
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
checklist-sectioned |  |  | checklist | Fit-off Hose Tap |  |  |  |  | Yes | Fit-off Hose Tap | b77ddc62-88e9-4c21-ae27-27179582f887
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Vacuum breaker fitted
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checklist-sectioned |  |  | checklist | Installation Water Meter |  |  |  |  | Yes | Installation Water Meter | 9f8a4d7f-d472-4167-abbe-a071ecb62227
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Water Meter Details:
text | cfe26dbb-19c5-556b-aff5-d5a049ba0725 |  | textbox | Meter Type:
text | cd821c70-f9f9-5dd8-984b-06bb99a8bfa9 |  | textbox | Meter Number:
text | 346bc941-5b73-5396-9c8e-a63e4c192e6f |  | textbox | Meter Location:
select | 673eb70f-07f6-5222-9121-c139d0d97f22 |  | dropdown | Meter Size: | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checklist-sectioned |  |  | checklist | Installation Authority Main to Meter |  |  |  |  | Yes | Installation Authority Main to Meter | ef3b12da-0543-47aa-9c01-b0919f9457d1
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check valve connections
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check pipe trench marking tape (if specified)
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checkpoint-status |  |  | checkpoint | Check water meter assemblies
checkpoint-status |  |  | checkpoint | Check RPZD assemblies (if specified)
checkpoint-status |  |  | checkpoint | Check pipe labelling
checklist-sectioned |  |  | checklist | Testing Gas Pipework (7kPa or Less) |  |  |  |  | Yes | Testing Gas Pipework (7kPa or Less) | aaf66933-4ded-44d4-b87a-f448db361fff
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-5601
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Testing kit & equipment have current certification
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-5601 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
checklist-sectioned |  |  | checklist | Installation Pump Station or Tank (In-ground) |  |  |  |  | Yes | Installation Pump Station or Tank (In-ground) | b20f6f43-1fc3-421d-98ea-b79e2301b0fe
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Plant & Equipment Installation checked off as below
checkpoint-status |  |  | checkpoint | Installation complies with current AS/NZS-3500
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check connections to pits, tanks, & pump stations, etc
checkpoint-status |  |  | checkpoint | Check covers, venting, & electrical conduits, etc
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | If trench is to be left open, make ensure pipe can not float
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checkpoint-status |  |  | checkpoint | Must provide photo
checklist-sectioned |  |  | checklist | Installation Gas Service (Mains/Risers) |  |  |  |  | Yes | Installation Gas Service (Mains/Risers) | 7fd687e5-479b-4744-bf3a-938b1aaba0f4
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check crimp fittings
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check valves & meter assemblies
checkpoint-status |  |  | checkpoint | Check valves & meter assemblies fixings & brackets
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check for cross connections
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Installation Water Service (In-ground) |  |  |  |  | Yes | Installation Water Service (In-ground) | c3d84c5f-c1c3-4538-91b5-25aef5531dcf
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check valve connections
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checkpoint-status |  |  | checkpoint | Check pipe trench marking tape (if specified)
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checklist-sectioned |  |  | checklist | Fit-off Bath & Tapware |  |  |  |  | Yes | Fit-off Bath & Tapware | bd65e7d9-fde3-4d9e-8bd1-a0362ff84669
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check wall plates, mixers & diversion valves
checkpoint-status |  |  | checkpoint | Check outlets, wall rails & hand showers
checkpoint-status |  |  | checkpoint | Check special DDA accessories (if applicable)
checkpoint-status |  |  | checkpoint | Check waste & trap connections
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check floor grate level & alignment
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Fit-off Shower & Tapware |  |  |  |  | Yes | Fit-off Shower & Tapware | e3175fa3-c8d4-4449-ae17-1e9d6acaaacb
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check wall plates, mixers & diversion valves
checkpoint-status |  |  | checkpoint | Check outlets, wall rails & hand showers
checkpoint-status |  |  | checkpoint | Check special DDA accessories (if applicable)
checkpoint-status |  |  | checkpoint | Check waste & trap connections
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check floor grate level & alignment
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Installation Gas Service (In-ground) |  |  |  |  | Yes | Installation Gas Service (In-ground) | 0b25031d-5bc8-43b0-a986-7865b37e3b69
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check valve connections
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checkpoint-status |  |  | checkpoint | Check pipe trench marking tape (if specified)
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checklist-sectioned |  |  | checklist | Fit-off Kitchen Sink & Tapware |  |  |  |  | Yes | Fit-off Kitchen Sink & Tapware | e7306d5c-2b8f-4212-b025-930b7fe7c869
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check mini stops
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check waste & trap connections
checkpoint-status |  |  | checkpoint | Check dishwasher waste & water connections
checkpoint-status |  |  | checkpoint | Check stop valves for future connections are capped
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Installation Pump Line |  |  |  |  | Yes | Installation Pump Line | 2d89a2ec-889d-4c93-8f5d-ed9ec3351e62
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check pipework is clear of debris
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check pipe labelling
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Commission Water Pressure Pump Set |  |  |  |  | Yes | Commission Water Pressure Pump Set | 794ce08f-764e-4f3f-930a-637da057f996
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check water supply fault
checkpoint-status |  |  | checkpoint | Check pump motor rotation
checkpoint-status |  |  | checkpoint | Check dry pump fault
checkpoint-status |  |  | checkpoint | Check auto pump roll-over
checkpoint-status |  |  | checkpoint | Check pump package operational set points
checkpoint-status |  |  | checkpoint | Check control panel display & set points
checkpoint-status |  |  | checkpoint | Check fault warning alarms
checkpoint-status |  |  | checkpoint | Check BMS connection as specified
checkpoint-status |  |  | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Commission Water Storage Tank |  |  |  |  | Yes | Commission Water Storage Tank | a041d98f-8177-486e-95c8-41ad5f35325d
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check valves are fully open
checkpoint-status |  |  | checkpoint | Check water level sensor set points
checkpoint-status |  |  | checkpoint | Check tank fill valve
checkpoint-status |  |  | checkpoint | Check low level fault
checkpoint-status |  |  | checkpoint | Check high level fault
checkpoint-status |  |  | checkpoint | Check passive over-flow
checkpoint-status |  |  | checkpoint | Check statutory warning signage
checkpoint-status |  |  | checkpoint | Check control panel display & set points
checkpoint-status |  |  | checkpoint | Check BMS connection as specified
checkpoint-status |  |  | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checklist-sectioned |  |  | checklist | Installation Water Service (Rough-ins) |  |  |  |  | Yes | Installation Water Service (Rough-ins) | ffb4ed9c-7d9d-4ba4-a9d7-a5f0c13a2472
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check pipework can not be holed by plaster screws
checkpoint-status |  |  | checkpoint | Check crimp fittings
checkpoint-status |  |  | checkpoint | Check for cross connections
checkpoint-status |  |  | checkpoint | Check alignment & levels
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check TMV/TV
checkpoint-status |  |  | checkpoint | Check in-wall mixer bodies & lugged elbows
checkpoint-status |  |  | checkpoint | Check in-wall fixture mounting brackets & concealed cisterns (if specified)
checkpoint-status |  |  | checkpoint | Check noggins for future fixture
checkpoint-status |  |  | checkpoint | Check sharp edge pipe protection
checkpoint-status |  |  | checkpoint | Check heat trace (if specified)
checkpoint-status |  |  | checkpoint | Check hot water pipe clips & thermal insulation (if specified)
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Fit-off Wash Basin & Tapware |  |  |  |  | Yes | Fit-off Wash Basin & Tapware | 037806b3-d1ea-4e6b-8df8-922e721225c0
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check mini stops
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check special DDA accessories (if applicable)
checkpoint-status |  |  | checkpoint | Check waste & trap connections
checkpoint-status |  |  | checkpoint | Check all functions, controls & remote sensors for correct operation
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Cast-in Waste & Vent |  |  |  |  | Yes | Cast-in Waste & Vent | 1fbf393a-b814-47d1-8b55-e12e5ed714b1
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check pipe expansion lagging
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checklist-sectioned |  |  | checklist | Fit-off Cleaners Sink & Tapware |  |  |  |  | Yes | Fit-off Cleaners Sink & Tapware | 5c784e05-6f9f-4e32-adf8-383ebfa3de1a
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check tapware for fit & function
checkpoint-status |  |  | checkpoint | Check wall brackets & fixings
checkpoint-status |  |  | checkpoint | Check bucket grate
checkpoint-status |  |  | checkpoint | Check waste & trap connections
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check trap is clear of debris
checkpoint-status |  |  | checkpoint | Check caulking
checklist-sectioned |  |  | checklist | Installation Backflow Prevention Device |  |  |  |  | Yes | Installation Backflow Prevention Device | 34aa9f8c-612d-4fe4-93d2-73ff51c5849c
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | RPZD Details:
text | 211bbd3d-a453-517c-8b72-dce8c005cf44 |  | textbox | RPZD Serial Number:
text | ab345092-20ae-55f4-a0de-df8856b63a41 |  | textbox | RPZD Location:
select | 178f0064-1eea-5f8d-8353-1713fbe6487a |  | dropdown | RPZD Size: | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check pressure relief pipe to tundish
checklist-sectioned |  |  | checklist | Installation Gas Service (Rough-ins) |  |  |  |  | Yes | Installation Gas Service (Rough-ins) | d4cb82de-6671-4a7b-943c-2f8e6a124e86
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check pipework can not be holed by plaster screws
checkpoint-status |  |  | checkpoint | Check crimp fittings
checkpoint-status |  |  | checkpoint | Check for cross connections
checkpoint-status |  |  | checkpoint | Check alignment & levels
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
checkpoint-status |  |  | checkpoint | Check lugged elbows
checkpoint-status |  |  | checkpoint | Check noggings for future fixture
checkpoint-status |  |  | checkpoint | Check sharp edge pipe protection
checkpoint-status |  |  | checkpoint | Check pipe colour coding
checkpoint-status |  |  | checkpoint | Check floor/wall penetration fire proofing
checklist-sectioned |  |  | checklist | Installation Hot Water Plant/Unit |  |  |  |  | Yes | Installation Hot Water Plant/Unit | ed552afd-b058-48fe-be33-40ebdf0e30fd
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check safe tray (if specified)
checkpoint-status |  |  | checkpoint | Check isolation valves & non-return valves
checkpoint-status |  |  | checkpoint | Check pressure reduction valve (if specified)
checkpoint-status |  |  | checkpoint | Check flexible connections are not twisted or kinked
checkpoint-status |  |  | checkpoint | Check waste & water connections
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check water temperatures are as specified
checkpoint-status |  |  | checkpoint | Check electrical power is available
checkpoint-status |  |  | checkpoint | Check solar panels & mounting brackets
checkpoint-status |  |  | checkpoint | Check solar connecting pipework & fittings
checkpoint-status |  |  | checkpoint | Check solar pump operation
checklist-sectioned |  |  | checklist | Installation Water Pressure Pump Set |  |  |  |  | Yes | Installation Water Pressure Pump Set | 5e688d30-78b8-4380-bbe1-9cb9719d7b0e
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Pump Set Details:
select | dbb13c7b-78da-5575-b79c-e2ba3c1332f6 |  | dropdown | Pump Set Type: | Potable Cold Water,Potable Hot Water,Recycled Rain Water,Non-Potable Water,Other
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage or leaks
checkpoint-status |  |  | checkpoint | Check fixing points are secure
checkpoint-status |  |  | checkpoint | Check level & alignment
checkpoint-status |  |  | checkpoint | Check isolation valves & non-return valves
checkpoint-status |  |  | checkpoint | Check feed & delivery pipe connections
checkpoint-status |  |  | checkpoint | Check back-up water supply by-pass (if specified)
checkpoint-status |  |  | checkpoint | Check Control Panel
checkpoint-status |  |  | checkpoint | Check all functions & controls for correct operation
checkpoint-status |  |  | checkpoint | Check electrical power is available
checkpoint-status |  |  | checkpoint | Check BMS is available
checklist-sectioned |  |  | checklist | Installation Pump Station |  |  |  |  | Yes | Installation Pump Station | c9b5c128-9d56-46e1-9ef2-417860afc502
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Pump Station Details:
select | 21fbf836-4d5d-5ba4-aad0-386cb8f69d1a |  | dropdown | Pump Station Type: | Sewer Above Ground,Stormwater Above Ground,Sewer In-ground,Stormwater In-ground,Other
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check inlet/outlet connections & vents
checkpoint-status |  |  | checkpoint | Check covers, venting, & electrical conduits, etc
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checklist-sectioned |  |  | checklist | Installation Water Storage Tank |  |  |  |  | Yes | Installation Water Storage Tank | 48ae6775-d581-46a5-8cc6-600b1b6055fb
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Tank Details:
select | d4db202b-c5da-5bd9-bc38-0c989d145786 |  | dropdown | Tank Type: | Potable Water Above Ground,Rain Water Above Ground,Potable Water In-ground,Rain Water In-ground,Fire Water Above Ground,Other
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check inlet/outlet connections & vents
checkpoint-status |  |  | checkpoint | Check covers, venting, & electrical conduits, etc
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checklist-sectioned |  |  | checklist | Installation Waste Water Tank |  |  |  |  | Yes | Installation Waste Water Tank | e30ba22e-2191-498e-abe6-417a0c2bd545
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
checkpoint-status |  |  | checkpoint | Tank Details:
select | a3e2d56c-ba15-58b5-8c8e-8177203a7cf3 |  | dropdown | Tank Type: | Grease Interceptor,Neutralizing Pit,POI Interceptor,SW Detention Tank,SW Filtration Pit,Other
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check for damage & leaks
checkpoint-status |  |  | checkpoint | Check materials & joining methods
checkpoint-status |  |  | checkpoint | Check alignments & levels
checkpoint-status |  |  | checkpoint | Check bedding & clearances
checkpoint-status |  |  | checkpoint | Check inlet/outlet connections & vents
checkpoint-status |  |  | checkpoint | Check covers, venting, & electrical conduits, etc
checkpoint-status |  |  | checkpoint | Check pipework & traps are clear of debris
checkpoint-status |  |  | checkpoint | Check inspection openings
checkpoint-status |  |  | checkpoint | Check open ends are sealed
checkpoint-status |  |  | checkpoint | Check trench backfill & compaction
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Check installation is clean and ready for testing
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
checklist-sectioned |  |  | checklist | Testing Drainage Pipework (Water Test) |  |  |  |  | Yes | Testing Drainage Pipework (Water Test) | b07de643-c38d-4ec9-a3cb-5b13afea8720
checkpoint-group |  |  | section | Details:
checkpoint-status |  |  | checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
checkpoint-status |  |  | checkpoint | Installation complies with current drawings & specifications
checkpoint-status |  |  | checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint-status |  |  | checkpoint | Testing kit & equipment have current certification
checkpoint-status |  |  | checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)