## ITP Cover Page
Watermain PVC Inspection Test Plan
Project: Peacocke Whatukooruru Drive
Number and Revision: DN1205 - 104 - Rev C
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Peacocke Whatukooruru Drive |  |  |  |  | ITP Number: |  |  | 104
Project Number: |  |  | DN1205 |  |  |  |  | ITP Status: |  |  | Draft For Approval
ITP Description: |  |  | WATERMAIN- PVC |  |  |  |  | Revision: | 1000 |  | C
Contract Number: |  |  | Peacocke Whatukooruru Drive |  |  |  |  | Drawing Sets: |  |  | 146000-002A-2400 to 146000-002A-2496
Customer: |  |  | Hamilton City Council |  |  |  |  | Specification: |  |  | Project Specification and Appendices.
Quality Specified: |  |  | NZTA Z/1
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  |  | Responsibilities Key
A | Draft for Review | 2023-01-11 |  | Craig Lingard |  | First revision for internal review & approval |  |  |  | A | Action |  |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  |  | CR | Customer Rep
B | Draft for Approval | 2023-01-17 |  | BBO |  | Second revision for Engineer's approval |  |  |  | C | Check |  |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  |  | PM | Project Manager
C | Draft for Approval | 2023-01-27 |  | BBO |  | Changes made as per Consultant Advice Notice 003 |  |  |  | E | Examine |  |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  |  | SE | Site Engineer
[10 empty] | O | Operation |  |  | QE | Quality Engineer
[10 empty] | R | Review |  |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  |  | SV | Surveyor
[10 empty] | V | Visual Verification |  |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  |  | Signature: |  |  | Date:
Downer PM | [7 empty] | Downer PM
Downer QM | [7 empty] | Downer QM
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Watermain PVC Inspection Test Plan
Project: Peacocke Whatukooruru Drive
Number and Revision: DN1205 - 104 - Rev C
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity
[6 empty] | Activity | By
SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
1.1 | Extent of Line Setout | Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Watermain drawings Identify any clashes before construction. | Design Drawings | ITP Sign Off | Prior to Construction & Every Revision of IFC Drgs / Data | M | PE
1.2 | Environmental Protection | Install Erosion Sediment Control measures in line with PWRBSS ESCP plans Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events | Project ESCP Plans | ITP Sign Off | Prior to Construction Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events | M | PE
1.3 | Stakeholder | Inform stakeholders of upcoming works Agree plans for maintaining access to properties during construction with landowners | Project Stakeholder Management Plan | ITP Sign Off | Prior to Construction with continue updates throughout the works | M | PE
1.4 | Permits | Permit to Dig must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip. Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections. All known services must be clearly marked on site and briefed to the workforce . | Section 2.2.10 Project Specification | Ground Disturbance Permit DN-ZH-FM043.1 | Prior to Construction Reviewed and Reissued weekly or when site conditions change | H | PE
SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
2.1 | Pipes & Fittings | Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes/fittings are correct and in good condition and compliant. |  | Delivery Dockets | Each Delivery to Site | S | PE
2.2 | Bedding/Overlay | Confirm material grading and density of pit sand or other approved material |  | IANZ Lab Test Reports | 1 Test per 1000m3 | H | PE
2.3 | Backfill Material Compliance | Confirm material grading and density of pit sand or other approved material Use selected native soils in berm |  | IANZ Lab Test Reports | 1 Test per 1000m3 | H | PE
2.4 | Undercut Backfill Material | Engineer to Specify Material to meet specifications dependant on mateial selected |  | IANZ Lab Test Reports | 1 Test per 1000m3 | HP | ENG
2.5 | Geotextile/Geogrid | NZTA F/07 Strength Class C & Filter Class 1 geotextile is to be used in the undercut. Geotextile or Geogrid that is used in the undercut is to be documented / marked up on drawing | Project Specification | Certification Photos of Delivery Dockets | Material Used | C | PE
2.6 | Warning Tape | Obtain Warning Tape from supplier |  | Delivery Dockets | Each Delivery to Site | S | PE
SECTION 3 – CONSTRUCTION ACTIVITY
3.1 | Trench Excavation | Excavate trench to design height, placing spoil in approved area and benching as required Visual Inspection to any hard stones or rocks to be removed Any archaeological finds to be reported Inspections to any formation of soft spots | Project Specification 4.3 | Scala test result | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.2 | Foundation Compliance | Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa | Project Specification 4.3 | Scala test result | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.3 | Undercut Backfill Compliance | NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD | Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002 | IANZ Lab Test Report | Based on Undercut Section | H | QE
3.4 | Bedding Compaction Testing | HS2 Bedding under pavement H2 Bedding outside pavement NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD | Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002 | IANZ Lab Test Report | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.5 | Overlay Compaction Testing Overlay zone shall extend from top of Side Zone to 600mm above the top of the pipe. 2 lifts of 300mm should be placed. | NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD | Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007 | IANZ Lab Test Report | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.6 | Backfill Inspection | Inspection of pipes prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the pipeline. | Project Specification 4.3 | Photographs | Continous | S | PE
3.7 | Install Warning Tape | For open trenching, detector tape shall be placed approximately 200mm below final ground level and metallic ‘detector’ tape coloured blue, stipulating ‘Danger – Water Main Below’ (or similar) shall be laid. | RITS | Photographs | Continous | S | PE
3.8 | Survey | All Water Mains shall be laid in a straight line or following street layout. The deviation from approved design alignment permitted either in plan or elevation shall be: Open Cut – ± 50mm on straight and 100mm in curves All pipes, fitting and thrust blocks to be as built prior to backfilling | Vertical tolerance +/- 50mm Horizontal Between Structures +/- 100mm | Survey Data | Continous | C | SV
3.9 | Backfill Compaction Testing | NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC. | RITS | IANZ Lab Test Report | Every 20m along trench 1 test every 5m² at driveways and footpaths | H | QE
3.1 | Pressure Testing | At least one working day advance notice shall be given to council for pressure testing of pipelines. All pipelines shall be pressure tested and backfilled after anchor blocks, specials and fittings are completed, but with joints and connections visible. The final tests are to be witnessed by Council prior to the pipe being connected to the ‘live’ network. No further connections will be permitted after this stage. Refer to NZS 4404 Appendix C3 for the requirements or if this not available, the pipe manufacturer’s procedure. | 6.3.10 RITS | Visual Inspection & Report | Completion of Works | S | PE
3.11 | Disinfection & Flushing | Appendix D of NZS 4404 – Water Supply Disinfection Specification shall apply Discharge of Testing or Chlorinated Water from pipelines may require a resource consent from the regional council | 6.3.11 RITS | Visual Inspection & Report | Completion of Works | S | PE
3.12 | Bacteriological Test | In commissioning new pipelines, Council shall be given 24 hours’ notice as to when sampling for bacteriological tests is to be carried out. Water in the pipeline shall be sampled between 12 hours and 48 hours after postchlorination flushing and the samples tested for the presence of E.coli, Coliforms and Heterotrophic Plate Count by a Ministry of Health Approved laboratory with IANZ accreditation for this type of test. The number of samples shall be at least one for projects involving less than 100m of pipe, two for projects up to 200m length, etc. “A satisfactory result is s <1 MPN/100ml for E.coli and Total Coliforms and less than 20 CFU/ml for Heterotrophic Plate Counts.” If E.coli is detected the pipeline shall be swabbed, flushed, disinfected, flushed again and then the bacteriological tests repeated. The process shall be repeated until such time a clear test is recorded. Note: There are high risks of test failure due to sample contamination so it is recommended that the testing laboratory is also involved in collecting the sample. | 6.3.11.2 RITS | Visual Inspection & Report | Completion of Works | S | PE
3.13 | Reinstatement | Quality Check on New Works | Reinstate and Tie into existing surrounds | Photographs | Continous | S | PE
SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
4.01.01 | Survey As-Builts | Quality Check on New Works based on the tolerances in RITS | Project Specification | Survey Data As Built Drawings Photographs | Post Works Completion | H | SV