## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Watermain PVC |  |  |  |  | Yes | ITP - Watermain PVC | 32e6b2e5-b60f-4e12-88ad-ddd4a32c832c
section | 1. Pre-construction (P&G / Establishment)
checkpoint | 1.1 - Extent of Line Setout
note | Acceptance / Conformance Criteria - Ensure line and level of Stormwater has been marked out and agreed with Engineer in accordance with Watermain drawings Identify any clashes before construction.
note | Standard / Specification - Design Drawings
note | Verifying Document - ITP Sign Off
note | Frequency - Prior to Construction & Every Revision of IFC Drgs / Data
note | Activity - M
note | By - PE
checkpoint | 1.2 - Environmental Protection
note | Acceptance / Conformance Criteria - Install Erosion Sediment Control measures in line with PWRBSS ESCP plans Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events
note | Standard / Specification - Project ESCP Plans
note | Verifying Document - ITP Sign Off
note | Frequency - Prior to Construction Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events
note | Activity - M
note | By - PE
checkpoint | 1.3 - Stakeholder
note | Acceptance / Conformance Criteria - Inform stakeholders of upcoming works Agree plans for maintaining access to properties during construction with landowners
note | Standard / Specification - Project Stakeholder Management Plan
note | Verifying Document - ITP Sign Off
note | Frequency - Prior to Construction with continue updates throughout the works
note | Activity - M
note | By - PE
checkpoint | 1.4 - Permits
note | Acceptance / Conformance Criteria - Permit to Dig must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip. Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections. All known services must be clearly marked on site and briefed to the workforce .
note | Standard / Specification - Section 2.2.10 Project Specification
note | Verifying Document - Ground Disturbance Permit DN-ZH-FM043.1
note | Frequency - Prior to Construction Reviewed and Reissued weekly or when site conditions change
note | Activity - H
note | By - PE
section | 2. Material, Personnel & third party approval
checkpoint | 2.1 - Pipes & Fittings
note | Acceptance / Conformance Criteria - Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes/fittings are correct and in good condition and compliant.
note | Verifying Document - Delivery Dockets
note | Frequency - Each Delivery to Site
note | Activity - S
note | By - PE
checkpoint | 2.2 - Bedding/Overlay
note | Acceptance / Conformance Criteria - Confirm material grading and density of pit sand or other approved material
note | Verifying Document - IANZ Lab Test Reports
note | Frequency - 1 Test per 1000m3
note | Activity - H
note | By - PE
checkpoint | 2.3 - Backfill Material Compliance
note | Acceptance / Conformance Criteria - Confirm material grading and density of pit sand or other approved material Use selected native soils in berm
note | Verifying Document - IANZ Lab Test Reports
note | Frequency - 1 Test per 1000m3
note | Activity - H
note | By - PE
checkpoint | 2.4 - Undercut Backfill Material
note | Acceptance / Conformance Criteria - Engineer to Specify Material to meet specifications dependant on material selected
note | Verifying Document - IANZ Lab Test Reports
note | Frequency - 1 Test per 1000m3
note | Activity - HP
note | By - ENG
signoff | AUTHORITY HOLDPOINT
checkpoint | 2.5 - Geotextile/Geogrid
note | Acceptance / Conformance Criteria - NZTA F/07 Strength Class C & Filter Class 1 geotextile is to be used in the undercut. Geotextile or Geogrid that is used in the undercut is to be documented / marked up on drawing
note | Standard / Specification - Project Specification
note | Verifying Document - Certification Photos of Delivery Dockets
note | Frequency - Material Used
note | Activity - C
note | By - PE
checkpoint | 2.6 - Warning Tape
note | Acceptance / Conformance Criteria - Obtain Warning Tape from supplier
note | Verifying Document - Delivery Dockets
note | Frequency - Each Delivery to Site
note | Activity - S
note | By - PE
section | 3. Construction Activity
checkpoint | 3.1 - Trench Excavation
note | Acceptance / Conformance Criteria - Excavate trench to design height, placing spoil in approved area and benching as required Visual Inspection to any hard stones or rocks to be removed Any archaeological finds to be reported Inspections to any formation of soft spots
note | Standard / Specification - Project Specification 4.3
note | Verifying Document - Scala test result
note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
note | Activity - H
note | By - QE
checkpoint | 3.2 - Foundation Compliance
note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm Cohesive Material: Vane Shear Strength 70kPa
note | Standard / Specification - Project Specification 4.3
note | Verifying Document - Scala test result
note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
note | Activity - H
note | By - QE
checkpoint | 3.3 - Undercut Backfill Compliance
note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 95%(Average98%) of MDD
note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
note | Verifying Document - IANZ Lab Test Report
note | Frequency - Based on Undercut Section
note | Activity - H
note | By - QE
checkpoint | 3.4 - Bedding Compaction Testing
note | Acceptance / Conformance Criteria - HS2 Bedding under pavement H2 Bedding outside pavement NDM Back Scatter Minimum Compaction 95%(Average98%) of MDD
note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD AS/NZS 2566.2/2002
note | Verifying Document - IANZ Lab Test Report
note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
note | Activity - H
note | By - QE
checkpoint | 3.5 - Overlay Compaction Testing Overlay zone shall extend from top of Side Zone to 600mm above the top of the pipe. 2 lifts of 300mm should be placed.
note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Minimum Compaction 92% of MDD
note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD AS/NZS 3725:2007
note | Verifying Document - IANZ Lab Test Report
note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
note | Activity - H
note | By - QE
checkpoint | 3.6 - Backfill Inspection
note | Acceptance / Conformance Criteria - Inspection of pipes prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the pipeline.
note | Standard / Specification - Project Specification 4.3
note | Verifying Document - Photographs
note | Frequency - Continuous
note | Activity - S
note | By - PE
checkpoint | 3.7 - Install Warning Tape
note | Acceptance / Conformance Criteria - For open trenching, detector tape shall be placed approximately 200mm below final ground level and metallic ‘detector’ tape coloured blue, stipulating ‘Danger – Water Main Below’ (or similar) shall be laid.
note | Standard / Specification - RITS
note | Verifying Document - Photographs
note | Frequency - Continuous
note | Activity - S
note | By - PE
checkpoint | 3.8 - Survey
note | Acceptance / Conformance Criteria - All Water Mains shall be laid in a straight line or following street layout. The deviation from approved design alignment permitted either in plan or elevation shall be: Open Cut – ± 50mm on straight and 100mm in curves All pipes, fitting and thrust blocks to be as built prior to backfilling
note | Standard / Specification - Vertical tolerance +/- 50mm Horizontal Between Structures +/- 100mm
note | Verifying Document - Survey Data
note | Frequency - Continuous
note | Activity - C
note | By - SV
checkpoint | 3.9 - Backfill Compaction Testing
note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC.
note | Standard / Specification - RITS
note | Verifying Document - IANZ Lab Test Report
note | Frequency - Every 20m along trench 1 test every 5m² at driveways and footpaths
note | Activity - H
note | By - QE
checkpoint | 3.1 - Pressure Testing
note | Acceptance / Conformance Criteria - At least one working day advance notice shall be given to council for pressure testing of pipelines. All pipelines shall be pressure tested and backfilled after anchor blocks, specials and fittings are completed, but with joints and connections visible. The final tests are to be witnessed by Council prior to the pipe being connected to the ‘live’ network. No further connections will be permitted after this stage. Refer to NZS 4404 Appendix C3 for the requirements or if this not available, the pipe manufacturer’s procedure.
note | Standard / Specification - 6.3.10 RITS
note | Verifying Document - Visual Inspection & Report
note | Frequency - Completion of Works
note | Activity - S
note | By - PE
checkpoint | 3.11 - Disinfection & Flushing
note | Acceptance / Conformance Criteria - Appendix D of NZS 4404 – Water Supply Disinfection Specification shall apply Discharge of Testing or Chlorinated Water from pipelines may require a resource consent from the regional council
note | Standard / Specification - 6.3.11 RITS
note | Verifying Document - Visual Inspection & Report
note | Frequency - Completion of Works
note | Activity - S
note | By - PE
checkpoint | 3.12 - Bacteriological Test
note | Acceptance / Conformance Criteria - In commissioning new pipelines, Council shall be given 24 hours’ notice as to when sampling for bacteriological tests is to be carried out. Water in the pipeline shall be sampled between 12 hours and 48 hours after postchlorination flushing and the samples tested for the presence of E.coli, Coliforms and Heterotrophic Plate Count by a Ministry of Health Approved laboratory with IANZ accreditation for this type of test. The number of samples shall be at least one for projects involving less than 100m of pipe, two for projects up to 200m length, etc. “A satisfactory result is s <1 MPN/100ml for E.coli and Total Coliforms and less than 20 CFU/ml for Heterotrophic Plate Counts.” If E.coli is detected the pipeline shall be swabbed, flushed, disinfected, flushed again and then the bacteriological tests repeated. The process shall be repeated until such time a clear test is recorded. Note: There are high risks of test failure due to sample contamination so it is recommended that the testing laboratory is also involved in collecting the sample.
note | Standard / Specification - 6.3.11.2 RITS
note | Verifying Document - Visual Inspection & Report
note | Frequency - Completion of Works
note | Activity - S
note | By - PE
checkpoint | 3.13 - Reinstatement
note | Acceptance / Conformance Criteria - Quality Check on New Works
note | Standard / Specification - Reinstate and Tie into existing surrounds
note | Verifying Document - Photographs
note | Frequency - Continuous
note | Activity - S
note | By - PE
section | 4. Post-construction (Final Inspection & Handover)
checkpoint | 4.01.01 - Survey As-Builts
note | Acceptance / Conformance Criteria - Quality Check on New Works based on the tolerances in RITS
note | Standard / Specification - Project Specification
note | Verifying Document - Survey Data As Built Drawings Photographs
note | Frequency - Post Works Completion
note | Activity - H
note | By - SV