## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Concrete Inspection Record | [5 empty] | Concrete Inspection Record
section | Details
checkpoint-no-status | Details
textbox | Location / Description of Pour:
textbox | Drawings & Revision No. used to check off Pre Pour Inspection:
textbox | Concrete Grade |  |  | MPa
textbox | Concrete Quantity |  |  | m3
number | Pour No.
section | Formwork
checkpoint | Adequately braced and supported
checkpoint | Grout tight
checkpoint | Correct dimensions
checkpoint | Cleaned and oiled
checkpoint | Formed surfaces straight
checkpoint | Major penetrations located
checkpoint | Embedded items located
checkpoint | Correct for specified surface finish
checkpoint | Adequate seating Pre Cast units
checkpoint | Permit to Load Obtained
section | Reinforcement
checkpoint | Reinforcement Content and size
checkpoint | Confirm correct grade markings
checkpoint | Placement, tolerance, clearance
checkpoint | Rigidity and cover
checkpoint | Clean steel
checkpoint | Lap location and lengths
checkpoint | Starters/dowels correctly located
section | Construction Joints
checkpoint | Location
checkpoint | Roughened
checkpoint | Clean
checkpoint | Water bar placed if specified
section | Other
checkpoint | Correct mix ordered
checkpoint | Independent Survey – Check off critical survey points
checkpoint | Engineer’s Rep Notified
checkpoint | Pre-Pour Checked and Accepted – HOLD POINT – Site Engineer & Engineer’s Rep to sign
textbox | Name:
date | Date:
holdpoint | Sign:
section | Wet Concrete Checks
checkpoint | Correct mix delivered
checkpoint | Slump/flow Target
checkpoint | Compliance Cylinders Taken
checkpoint | Site Cured Cylinders Taken
checkpoint | Concrete Vibrated
checkpoint | Mandrels drawn through all ducts to verify no leakage / disconnection
checkpoint | Finished Level: Finished to grout check / angle fillet worked to
checkpoint | Surface to required finish eg U2, U4
checkpoint | Retarder applied at end of the pour
checkpoint | Curing applied (specify type)
checkpoint | Concrete Supply Dockets collected
textbox | Pour Start Time:
textbox | Pour Complete Time:
textbox | Volume Placed:
section | POST CONCRETE INSPECTION
checkpoint | Correct mix delivered
checkpoint | Curing correctly carried out
checkpoint | Concrete Strength for Striking
textbox | Concrete Strength:
checkpoint | Concrete Strength for backfilling
textbox | Concrete Strength:
checkpoint | Preparation of Construction Joints Completed
checkpoint | Blow holes, tie bar holes filled
checkpoint | Inspection of surface/s & any authorised repairs have been completed
checkpoint | As-Built complete
checkpoint | The above works have been inspected and on the basis of this check sheet are considered compliant with the drawings, specifications and instructions.
textbox | Name:
date | Date:
holdpoint | Sign:
checklist | FHIMS-QA-6006 - Insitu Concrete - Process Control Plan PRR | [5 empty] | FHIMS-QA-6006 - Insitu Concrete - Process Control Plan PRR
section | Details
checkpoint | 1 - Permits
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Obtain Permits
label | FREQUENCY: As required
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT: Control Checklist - Fall Prevention (if applicable). Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place
label | RECORDS: Permit attached or permit number noted
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2 - Pre-construction sign offs [1]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Is the Work Instruction for this work complete?
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT:
label | RECORDS: TMP on RecordsLink
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2 - Pre-construction sign offs [2]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Relevant non conformance of previous work signed off
label | FREQUENCY: As required
label | ACCEPTANCE CRITERIA: Document Sign Off
label | HOLD POINT: Relevant parties to inspect and review
label | RECORDS:
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3 - Design
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Ensure that Design is approved and Drawings are of the latest revision
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT:
label | RECORDS: Check Drawing Register
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Material Compliance [1]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Concrete mix design(s) submitted and approved by Design Engineer
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT: Check concrete mix design status
label | RECORDS: Design Engineer Approval
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Material Compliance [2]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: All concrete delivered to site shall be produced in accordance with the approved mix design
label | FREQUENCY: Prior to pouring concrete
label | ACCEPTANCE CRITERIA: Concrete Delivery Dockets
label | HOLD POINT:
label | RECORDS: Concrete Delivery Dockets
label | ONSITE RESPONSIBILITY:
checkpoint | 4 - Material Compliance [3]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Steel reinforcement complys with drawings, specifications and standards
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Document review
label | HOLD POINT: Steel reinforcing conforms to drawings and specification
label | RECORDS: Detail Sheets and Mill Certificates
label | ONSITE RESPONSIBILITY:
checkpoint | 4 - Material Compliance [4]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Any welding or mechanical splicing to be approved in writing by the Design Engineer
label | FREQUENCY: Prior to welding or splicing
label | ACCEPTANCE CRITERIA: Document review
label | HOLD POINT:
label | RECORDS: Mark Up As Built Drawings
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Material Compliance [5]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Any reinforcement modifications (cutting or bending) on site to be approved in writing by the Design Engineer
label | FREQUENCY: Prior to cutting or bending on site
label | ACCEPTANCE CRITERIA: Document review
label | HOLD POINT:
label | RECORDS: Mark Up As Built Drawings
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5 - Foundation Acceptance by Engineer's Rep
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Approval given by engineer's Rep and Signed off Subgrade Approval Checksheet
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Inspection by Engineer
label | HOLD POINT: Inspection and Acceptance of Structure Foundations
label | RECORDS: FHIMS - CS- 4100
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6 - Survey Setout
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Set out design features as per IFC drawings (Cast in items, Ducting, Penetrations)
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Survey
label | HOLD POINT: Consistency with Construction Drawing
label | RECORDS: Survey receipt
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7 - Blinding Concrete
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Once blinding concrete layer has been completed the Engineer's Rep to inspect and give approval for the rest of the works to commence
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Inspection by Engineer
label | HOLD POINT:
label | RECORDS: Sign off this document
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8 - Temporary Works (Formwork) [1]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Formwork to be constructed to design and set to correct line and level as set out by the surveyor
label | FREQUENCY: Daily Visual Inspection
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
checkpoint | 8 - Temporary Works (Formwork) [2]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: The Site Engineer and must sign off the formwork prior to concrete being poured
label | FREQUENCY: Prior to concrete pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9 - Reinforcing [1]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Reinforcing steel shall be handled, placed and fixed as per NZS 3109
label | FREQUENCY: Daily Visual Inspection
label | ACCEPTANCE CRITERIA: Document review
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
checkpoint | 9 - Reinforcing [2]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Check for any cast in items and ensure they are fixed correctly
label | FREQUENCY: Prior to concrete pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
checkpoint | 10 - Waterstop
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Waterstop and Hydrophilic placement checks to ensure correct placement including welds
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Photos & sign off
label | RECORDS: FHIMS-CS- 4029
label | ONSITE RESPONSIBILITY:
checkpoint | 11 - Concrete Pumping Operations
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Ensure the Permit to Concrete Pump Checksheet has been completed before concrete pumping commences
label | FREQUENCY: Prior to commencement
label | ACCEPTANCE CRITERIA: Document review
label | HOLD POINT:
label | RECORDS: FHIMS-CS- 4029
label | ONSITE RESPONSIBILITY:
checkpoint | 12 - Concreting [1]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: The Design Engineer shall be advised at least 24 working hours before the proposed time for concreting that a pre-pour inspection is required
label | FREQUENCY: Prior to concrete pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT:
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12 - Concreting [2]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Concrete dockets checked for correct mix and concrete site testing undertaken. 1 slump test per truck. 1 sample set per 75m3 of each different mix
label | FREQUENCY: Prior to concrete pour
label | ACCEPTANCE CRITERIA: Test Results
label | HOLD POINT: NZS 3104
label | RECORDS: FHIMS-CS- 4090
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12 - Concreting [3]
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Concrete surfaces shall be F4 or better for formed surfaces and U3 or better for unformed surfaces
label | FREQUENCY: Post pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12 - Concreting [4]
label | VERIFICATION ACTIVITY: M
label | METHODS OR REFERENCE: Curing and thermal monitoring
label | FREQUENCY: Post pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
checkpoint | 12 - Concreting [5]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Review concrete compressive tests results
label | FREQUENCY: Post pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
checkpoint | 13 - Remove formwork
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Remove formwork as per the approved work method
label | FREQUENCY: At completion of pour
label | ACCEPTANCE CRITERIA: Visual inspection
label | HOLD POINT: Concrete Inspection Record
label | RECORDS: FHIMS-CS- 4008
label | ONSITE RESPONSIBILITY:
checkpoint | 14 - Lot Number QA File [1]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Ensure all OFIs are closed and included within QA file
label | FREQUENCY: At completion of Lot
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT:
label | RECORDS:
label | ONSITE RESPONSIBILITY:
checkpoint | 14 - Lot Number QA File [2]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: The Concrete Test Result Spreadsheet and Test reports to be included within QA file
label | FREQUENCY: At completion of Lot
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT:
label | RECORDS:
label | ONSITE RESPONSIBILITY:
checkpoint | 14 - Lot Number QA File [3]
label | VERIFICATION ACTIVITY: W
label | METHODS OR REFERENCE: Delivery Dockets to be included in QA file
label | FREQUENCY: At completion of Lot
label | ACCEPTANCE CRITERIA: Document Review
label | HOLD POINT:
label | RECORDS:
label | ONSITE RESPONSIBILITY:
checkpoint | 15 - As-builts
label | VERIFICATION ACTIVITY: H
label | METHODS OR REFERENCE: Red pen mark up drawings to be included in QA file
label | FREQUENCY: At the completion of the Lot of work
label | ACCEPTANCE CRITERIA: Drawings
label | HOLD POINT:
label | RECORDS: Asbuilt Drawing
label | ONSITE RESPONSIBILITY:
holdpoint | AUTHORITY HOLDPOINT