## ITP-xxx
|  |  | Inspection and Test Plan - Installation of Conduits & Pits | [8 empty] | Document # ITP-005
[12 empty] | Revision : 1 | Date : 02/09/24
Client: |  | Department of State Growth |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  |  | Approved by :
Project: |  | Davey To Macquarie Transit Connection |  | Service Relocations - Telstra and NBN |  | Name: | Carter Lawson-Kelleway | Name: |  |  |  | Name:
Contract No: |  | 3741 |  | Specifications: 5. Contract 3741 - Davey to Macquarie Streets - Transit Lane Connection - Attachment 2 - Specification, S009_2006r V2, AS3000, Telstra Specificaitons
|  |  |  | Structure / Component: Telstra/NBN Conduits and Pits |  | Signed : |  | Signed : |  |  |  | Signed :
|  |  |  | Location: Site Wide |  | Date : |  | Date : |  |  |  | Date :
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | QAV | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  | Prior to commencing any activity | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings -all drawings are the latest revision | Drawings and drawing registers | Visual inspection | This ITP signed off | HP* | Fulton Hogan Engineer | N/A |  |  | N/A
1.2 | Implementation of all measures and controls |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: PSP, EMP, TMP/TGS, JSEA, SWMS & WP | PSP, EMP, TMP, JSEA, SWMS, WP | Visual Inspection | This ITP signed off | HP* | Fulton Hogan Engineer | N/A |  |  | N/A
1.3 | Scheduling trenching works with Telstra/NBN contractor |  | Prior to commencing works | Provide Telstra with an accurate date for when the trenches will be available for cable installation and when final ground levels will be established | APPENDIX L | Verify | Service Installation Programme | HP* | Fulton Hogan Engineer | N/A |  |  | N/A
1.4 | Proving Services |  | Prior to commencing works | Underground services shall be proved by clearly marking the location of the service on the ground and physical exposure of relevant services at appropriate locations, in accordance with service authority requirements. | 160.12B | Verify | This ITP signed off | HP | Fulton Hogan Engineer/QAV | N/A |  |  | N/A
2 | Construction Works
2.1 | Survey set-out |  | As required | Prior to setting out trench, advice should be sought from Telstra/NBN for accuracy of cable routes. Cable routes shown on drawing are only approximate. | APPENDIX L | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
2.2 | Excavation |  | Each Lot | •The edges of all trenches located within a road pavement shall be sawcut •Trench to be excavated to the nominal trench depth of 1.8m with a minimum width of 1.0m. •If trench depth is greater than 1.5m; bench, batter or shore •5m EW shall be provided for all conduit bends | APPENDIX L | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
2.3 | Material Assessment |  | Each Lot | Prior to commencing excavation in any area and during excavation work, the Superintendent and the Contractor shall inspect each type of material encountered and subject to verification by appropriate laboratory testing, agree on the category of the material in accordance with Clause 204.04. | 204.06 | Verify | This ITP signed | HP | Fulton Hogan Engineer/Superindentant | N/A |  |  | N/A
2.4 | Bedding |  | Each Lot | Bedding material shall be placed and compacted for the full width of the trench to a depth of not less than 80 mm on an earth foundation or 200 mm on a rock foundation. | 733.06(B) | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
2.5 | Installation of Conduits and Cables |  | Each Lot | •Conduits and cables to be installed by Telstra/NBN contractor. •Once the bedding material has been laid and the conduits put in place, works shall not proceed prior to inspection by superintendent or representative. •Conduit bends to be concrete encased as per Telstra Specifications | 160.12A, 733.06(B) | Verify | This ITP signed WP | HP | Fulton Hogan Engineer | N/A |  |  | N/A
2.6 | Back Fill of Trenches |  | Each Lot | •Conduits to be backfilled as per Table 733.061 •Conduits shall be backfilled with stablised sand to 100mm above top of conduits as per AS3000. | 733.06, APPENDIX L | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
2.7 | Compaction |  | Each Lot | •Bedding, and backfill shall have during compaction a uniform moisture content within the range 85% to 115% of the optimum moisture content as determined in the Standard compaction test. •All pavement material shall have during compaction, uniform moisture content within the range 85% to 115% of the optimum moisture content as determined in the Modified Compaction test. •Backfilling beneath areas to be paved shall be assessed for compaction: -The number of tests per lot shall be three - Compacted to a mean value of density ratio of not less than 95% (passing 37.5mm AS sieve) •Backfilling of pavement materials shall be assessed for compaction: - Compacted to a mean value of density ratio of not less than 98% | 733.06 (D) | Verify | Test Reports | TP | Fulton Hogan Engineer | N/A |  |  | N/A
2.8 | Installation of marker tape |  | Each Lot | Marker tape to be installed by Telstra/NBN contractor | 160.12A | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
2.9 | Cable Pits & Pit Lids |  | Each Lot | • Cable pit excavation to be provided by Fulton Hogan • Cable pit bedding to be installed and approved by Telstra/NBN contractor • Cable pits and lids to be installed by Telstra/NBN contractor • Lift Analysis to be provided to Fulton Hogan by Telstra/NBN contractor 24-48hrs prior to lift. | 160.12A | Verify | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
3 | Completion
3.1 | Cleaning of Site |  | Each Lot | Surplus excavated material shall be removed from road reserve. All affected areas shall be restored to similar conditions that existed prior to work. | 733.09 | Visual inspection | This ITP signed | IP | Fulton Hogan Engineer | N/A |  |  | N/A
3.2 | Recording/As Built |  | Each Lot | Record any changes to cable routes on red line mark-ups. The final alignment of installed Telstra and NBN conduits shall be updated on the service plan | 160.12A | Verify | This ITP signed As Built Drawing | *HP | Fulton Hogan Engineer | N/A |  |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent
Note on K16: Rodrigo Anchico: Write "N/A" to disable the cell.