## CONQA - QA Folder Structure
QA Folder Structure | [5 empty] | Checklists
Site QA
Rough-In
Ground Floor
Wall Closure
|  |  |  | G01 |  | Wall Closure Checklist
|  |  |  | G02 |  | Wall Closure Checklist
|  |  |  | G03 |  | Wall Closure Checklist
|  |  |  | G04 |  | Wall Closure Checklist
|  |  |  | G05 |  | Wall Closure Checklist
|  |  |  | G06 |  | Wall Closure Checklist
|  |  |  | G07 |  | Wall Closure Checklist
|  |  |  | G08 |  | Wall Closure Checklist
|  |  |  | G09 |  | Wall Closure Checklist
Ceiling Closure
|  |  |  | G01 |  | Ceiling Closure Checklist
|  |  |  | G02 |  | Ceiling Closure Checklist
|  |  |  | G03 |  | Ceiling Closure Checklist
|  |  |  | G04 |  | Ceiling Closure Checklist
|  |  |  | G05 |  | Ceiling Closure Checklist
i |  |  |  | G06 |  | Ceiling Closure Checklist
|  |  |  | G07 |  | Ceiling Closure Checklist
|  |  |  | G08 |  | Ceiling Closure Checklist
|  |  |  | G09 |  | Ceiling Closure Checklist
Common Area
|  |  |  | Lobby Area |  | Common Area Rough in Checklist - General
|  |  |  | Ducting | Ability to Add | Duct Installation Checklist
Level 1
Wall Closure
|  |  |  | 101 |  | Wall Closure Checklist
|  |  |  | 102 |  | Wall Closure Checklist
|  |  |  | 103 |  | Wall Closure Checklist
|  |  |  | 104 |  | Wall Closure Checklist
|  |  |  | 105 |  | Wall Closure Checklist
|  |  |  | 106 |  | Wall Closure Checklist
|  |  |  | 107 |  | Wall Closure Checklist
|  |  |  | 108 |  | Wall Closure Checklist
Ceiling Closure
|  |  |  | 101 |  | Ceiling Closure Checklist
|  |  |  | 102 |  | Ceiling Closure Checklist
|  |  |  | 103 |  | Ceiling Closure Checklist
|  |  |  | 104 |  | Ceiling Closure Checklist
|  |  |  | 105 |  | Ceiling Closure Checklist
|  |  |  | 106 |  | Ceiling Closure Checklist
|  |  |  | 107 |  | Ceiling Closure Checklist
|  |  |  | 108 |  | Ceiling Closure Checklist
Common Area
|  |  |  | Lobby Area |  | Common Area Rough in Checklist - General
|  |  |  | Ducting | Ability to Add | Duct Installation Checklist
Level 2
Wall Closure
|  |  |  | 201 |  | Wall Closure Checklist
|  |  |  | 202 |  | Wall Closure Checklist
|  |  |  | 203 |  | Wall Closure Checklist
|  |  |  | 204 |  | Wall Closure Checklist
|  |  |  | 205 |  | Wall Closure Checklist
|  |  |  | 206 |  | Wall Closure Checklist
|  |  |  | 207 |  | Wall Closure Checklist
|  |  |  | 208 |  | Wall Closure Checklist
Ceiling Closure
|  |  |  | 201 |  | Ceiling Closure Checklist
|  |  |  | 202 |  | Ceiling Closure Checklist
|  |  |  | 203 |  | Ceiling Closure Checklist
|  |  |  | 204 |  | Ceiling Closure Checklist
|  |  |  | 205 |  | Ceiling Closure Checklist
|  |  |  | 206 |  | Ceiling Closure Checklist
|  |  |  | 207 |  | Ceiling Closure Checklist
|  |  |  | 208 |  | Ceiling Closure Checklist
Common Area
|  |  |  | Lobby Area |  | Common Area Rough in Checklist - General
|  |  |  | Ducting | Ability to Add | Duct Installation Checklist
Level 3
Wall Closure
|  |  |  | 301 |  | Wall Closure Checklist
|  |  |  | 302 |  | Wall Closure Checklist
|  |  |  | 303 |  | Wall Closure Checklist
|  |  |  | 304 |  | Wall Closure Checklist
|  |  |  | 305 |  | Wall Closure Checklist
|  |  |  | 306 |  | Wall Closure Checklist
|  |  |  | 307 |  | Wall Closure Checklist
|  |  |  | 308 |  | Wall Closure Checklist
Ceiling Closure
|  |  |  | 301 |  | Ceiling Closure Checklist
|  |  |  | 302 |  | Ceiling Closure Checklist
|  |  |  | 303 |  | Ceiling Closure Checklist
|  |  |  | 304 |  | Ceiling Closure Checklist
|  |  |  | 305 |  | Ceiling Closure Checklist
|  |  |  | 306 |  | Ceiling Closure Checklist
|  |  |  | 307 |  | Ceiling Closure Checklist
|  |  |  | 308 |  | Ceiling Closure Checklist
Common Area
|  |  |  | Lobby Area |  | Common Area Rough in Checklist - General
|  |  |  | Ducting | Ability to Add | Duct Installation Checklist
Level 4
Wall Closure
|  |  |  | 401 |  | Wall Closure Checklist
i |  |  |  | 402 |  | Wall Closure Checklist
|  |  |  | 403 |  | Wall Closure Checklist
|  |  |  | 404 |  | Wall Closure Checklist
Ceiling Closure
|  |  |  | 401 |  | Ceiling Closure Checklist
|  |  |  | 402 |  | Ceiling Closure Checklist
|  |  |  | 403 |  | Ceiling Closure Checklist
|  |  |  | 404 |  | Ceiling Closure Checklist
Common Area
|  |  |  | Lobby Area |  | Common Area Rough in Checklist - General
|  |  |  | Ducting | Ability to Add | Duct Installation Checklist
Fit-Off
Ground Floor
|  |  | G01 |  |  | Fit-Off Checklist
|  |  | G02 |  |  | Fit-Off Checklist
|  |  | G03 |  |  | Fit-Off Checklist
|  |  | G04 |  |  | Fit-Off Checklist
|  |  | G05 |  |  | Fit-Off Checklist
|  |  | G06 |  |  | Fit-Off Checklist
|  |  | G07 |  |  | Fit-Off Checklist
|  |  | G08 |  |  | Fit-Off Checklist
|  |  | G09 |  |  | Fit-Off Checklist
|  |  | Common Area |  |  | Common Area Fit-Off Checklist
Level 1
|  |  | 101 |  |  | Fit-Off Checklist
|  |  | 102 |  |  | Fit-Off Checklist
|  |  | 103 |  |  | Fit-Off Checklist
|  |  | 104 |  |  | Fit-Off Checklist
|  |  | 105 |  |  | Fit-Off Checklist
|  |  | 106 |  |  | Fit-Off Checklist
|  |  | 107 |  |  | Fit-Off Checklist
|  |  | 108 |  |  | Fit-Off Checklist
|  |  | Common Area |  |  | Common Area Fit-Off Checklist
Level 2
|  |  | 201 |  |  | Fit-Off Checklist
|  |  | 202 |  |  | Fit-Off Checklist
|  |  | 203 |  |  | Fit-Off Checklist
|  |  | 204 |  |  | Fit-Off Checklist
|  |  | 205 |  |  | Fit-Off Checklist
|  |  | 206 |  |  | Fit-Off Checklist
|  |  | 207 |  |  | Fit-Off Checklist
|  |  | 208 |  |  | Fit-Off Checklist
|  |  | Common Area |  |  | Common Area Fit-Off Checklist
Level 3
|  |  | 301 |  |  | Fit-Off Checklist
|  |  | 302 |  |  | Fit-Off Checklist
|  |  | 303 |  |  | Fit-Off Checklist
|  |  | 304 |  |  | Fit-Off Checklist
|  |  | 305 |  |  | Fit-Off Checklist
|  |  | 306 |  |  | Fit-Off Checklist
|  |  | 307 |  |  | Fit-Off Checklist
|  |  | 308 |  |  | Fit-Off Checklist
|  |  | Common Area |  |  | Common Area Fit-Off Checklist
Level 4
|  |  | 401 |  |  | Fit-Off Checklist
|  |  | 402 |  |  | Fit-Off Checklist
|  |  | 403 |  |  | Fit-Off Checklist
|  |  | 404 |  |  | Fit-Off Checklist
|  |  | Common Area |  |  | Common Area Fit-Off Checklist
Commissioning
Ground Floor
Air Conditioning
|  |  |  | G01 |  | A/C Commissioning Checklist
|  |  |  | G02 |  | A/C Commissioning Checklist
|  |  |  | G03 |  | A/C Commissioning Checklist
|  |  |  | G04 |  | A/C Commissioning Checklist
|  |  |  | G05 |  | A/C Commissioning Checklist
|  |  |  | G06 |  | A/C Commissioning Checklist
|  |  |  | G07 |  | A/C Commissioning Checklist
|  |  |  | G08 |  | A/C Commissioning Checklist
|  |  |  | G09 |  | A/C Commissioning Checklist
Ventilation
|  |  |  | G01 |  | Ventilation Checklist
|  |  |  | G02 |  | Ventilation Checklist
|  |  |  | G03 |  | Ventilation Checklist
|  |  |  | G04 |  | Ventilation Checklist
|  |  |  | G05 |  | Ventilation Checklist
|  |  |  | G06 |  | Ventilation Checklist
|  |  |  | G07 |  | Ventilation Checklist
|  |  |  | G08 |  | Ventilation Checklist
|  |  |  | G09 |  | Ventilation Checklist
Level 1
Air Conditioning
|  |  |  | 101 |  | A/C Commissioning Checklist
|  |  |  | 102 |  | A/C Commissioning Checklist
|  |  |  | 103 |  | A/C Commissioning Checklist
|  |  |  | 104 |  | A/C Commissioning Checklist
|  |  |  | 105 |  | A/C Commissioning Checklist
|  |  |  | 106 |  | A/C Commissioning Checklist
|  |  |  | 107 |  | A/C Commissioning Checklist
|  |  |  | 108 |  | A/C Commissioning Checklist
Ventilation
|  |  |  | 101 |  | Ventilation Checklist
|  |  |  | 102 |  | Ventilation Checklist
|  |  |  | 103 |  | Ventilation Checklist
|  |  |  | 104 |  | Ventilation Checklist
|  |  |  | 105 |  | Ventilation Checklist
|  |  |  | 106 |  | Ventilation Checklist
|  |  |  | 107 |  | Ventilation Checklist
|  |  |  | 108 |  | Ventilation Checklist
Level 2
Air Conditioning
|  |  |  | 201 |  | A/C Commissioning Checklist
|  |  |  | 202 |  | A/C Commissioning Checklist
|  |  |  | 203 |  | A/C Commissioning Checklist
|  |  |  | 204 |  | A/C Commissioning Checklist
|  |  |  | 205 |  | A/C Commissioning Checklist
|  |  |  | 206 |  | A/C Commissioning Checklist
|  |  |  | 207 |  | A/C Commissioning Checklist
|  |  |  | 208 |  | A/C Commissioning Checklist
Ventilation
|  |  |  | 201 |  | Ventilation Checklist
|  |  |  | 202 |  | Ventilation Checklist
|  |  |  | 203 |  | Ventilation Checklist
|  |  |  | 204 |  | Ventilation Checklist
|  |  |  | 205 |  | Ventilation Checklist
|  |  |  | 206 |  | Ventilation Checklist
|  |  |  | 207 |  | Ventilation Checklist
|  |  |  | 208 |  | Ventilation Checklist
Level 3
Air Conditioning
|  |  |  | 301 |  | A/C Commissioning Checklist
|  |  |  | 302 |  | A/C Commissioning Checklist
|  |  |  | 303 |  | A/C Commissioning Checklist
|  |  |  | 304 |  | A/C Commissioning Checklist
|  |  |  | 305 |  | A/C Commissioning Checklist
|  |  |  | 306 |  | A/C Commissioning Checklist
|  |  |  | 307 |  | A/C Commissioning Checklist
|  |  |  | 308 |  | A/C Commissioning Checklist
Ventilation
|  |  |  | 301 |  | Ventilation Checklist
|  |  |  | 302 |  | Ventilation Checklist
|  |  |  | 303 |  | Ventilation Checklist
|  |  |  | 304 |  | Ventilation Checklist
|  |  |  | 305 |  | Ventilation Checklist
|  |  |  | 306 |  | Ventilation Checklist
|  |  |  | 307 |  | Ventilation Checklist
|  |  |  | 308 |  | Ventilation Checklist
Level 4
Air Conditioning
|  |  |  | 401 |  | A/C Commissioning Checklist
|  |  |  | 402 |  | A/C Commissioning Checklist
|  |  |  | 403 |  | A/C Commissioning Checklist
|  |  |  | 404 |  | A/C Commissioning Checklist
Ventilation
|  |  |  | 401 |  | Ventilation Checklist
|  |  |  | 402 |  | Ventilation Checklist
|  |  |  | 403 |  | Ventilation Checklist
|  |  |  | 404 |  | Ventilation Checklist
Penetrations
Basement 1
|  |  | Fire Damper |  |  | Ability to Add
Level 1
Core Hole
|  |  |  | 101-A |  | Core Hole Checklist
|  |  |  | 101-R |  | Core Hole Checklist
|  |  |  | 102-A |  | Core Hole Checklist
|  |  |  | 102-R |  | Core Hole Checklist
|  |  |  | 103-A |  | Core Hole Checklist
|  |  |  | 103-R |  | Core Hole Checklist
|  |  |  | 104-A |  | Core Hole Checklist
|  |  |  | 104-R |  | Core Hole Checklist
|  |  |  | 105-A |  | Core Hole Checklist
|  |  |  | 105-R |  | Core Hole Checklist
|  |  |  | 106-A |  | Core Hole Checklist
|  |  |  | 106-R |  | Core Hole Checklist
|  |  |  | 107-A |  | Core Hole Checklist
|  |  |  | 107-R |  | Core Hole Checklist
|  |  |  | 108-A |  | Core Hole Checklist
|  |  |  | 108-R |  | Core Hole Checklist
Fire Damper
|  |  |  | FD L1.1 |  | Fire Damper Checklist -WSW6
|  |  |  | FD L1.2 |  | Fire Damper Checklist -WSW6
Level 2
Core Hole
|  |  |  | 201-A |  | Core Hole Checklist
|  |  |  | 201-R |  | Core Hole Checklist
|  |  |  | 202-A |  | Core Hole Checklist
|  |  |  | 202-R |  | Core Hole Checklist
|  |  |  | 203-A |  | Core Hole Checklist
|  |  |  | 203-R |  | Core Hole Checklist
|  |  |  | 204-A |  | Core Hole Checklist
|  |  |  | 204-R |  | Core Hole Checklist
|  |  |  | 205-A |  | Core Hole Checklist
|  |  |  | 205-R |  | Core Hole Checklist
|  |  |  | 206-A |  | Core Hole Checklist
|  |  |  | 206-R |  | Core Hole Checklist
|  |  |  | 207-A |  | Core Hole Checklist
|  |  |  | 207-R |  | Core Hole Checklist
|  |  |  | 208-A |  | Core Hole Checklist
|  |  |  | 208-R |  | Core Hole Checklist
Fire Damper
|  |  |  | FD L2.1 |  | Fire Damper Checklist -WSW6
|  |  |  | FD L2.2 |  | Fire Damper Checklist -WSW6
Level 2
Core Hole
|  |  |  | 301-A |  | Core Hole Checklist
|  |  |  | 301-R |  | Core Hole Checklist
|  |  |  | 302-A |  | Core Hole Checklist
|  |  |  | 302-R |  | Core Hole Checklist
|  |  |  | 303-A |  | Core Hole Checklist
|  |  |  | 303-R |  | Core Hole Checklist
|  |  |  | 304-A |  | Core Hole Checklist
|  |  |  | 304-R |  | Core Hole Checklist
|  |  |  | 305-A |  | Core Hole Checklist
|  |  |  | 305-R |  | Core Hole Checklist
|  |  |  | 306-A |  | Core Hole Checklist
|  |  |  | 306-R |  | Core Hole Checklist
|  |  |  | 307-A |  | Core Hole Checklist
|  |  |  | 307-R |  | Core Hole Checklist
|  |  |  | 308-A |  | Core Hole Checklist
|  |  |  | 308-R |  | Core Hole Checklist
Fire Damper
|  |  |  | FD L3.1 |  | Fire Damper Checklist -WSW6
|  |  |  | FD L3.2 |  | Fire Damper Checklist -WSW6
Level 2
Fire Damper
|  |  |  | FD L3.1 |  | Fire Damper Checklist -WSW6
|  |  |  | FD L3.2 |  | Fire Damper Checklist -WSW6
OHS
| Prestart |  |  |  |  | Prestart OH&S Documents
| Tool box |  |  |  |  | Toolbox meeting
| Incident Report |  |  |  |  | Incident Report - Checklist
Variations
Variation

## CONQA - Checklists
type | name | values | prefix | postfix
checklist | Wall Closure Checklist
section | Air Conditioning
checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
text | Wall Closure Date
checkpoint | FCU installed in right locaironan as per mechanical layout and the model number is in accordance with latest AC schdule | Pass Fail, N/A
checkpoint | FCU installed as hight as possible with 5% slop tward the drain point | Pass Fail, N/A
checkpoint | Thermostat control cabling has been installed | Pass Fail, N/A
checkpoint | Thermostat location is correct as per RCP | Pass Fail, N/A
checkpoint | Drains have been run to Tundish | Pass Fail, N/A
checkpoint | Drains tested and witnessed by Broad Air | Pass Fail, N/A
checkpoint | Pipe projecting the wall cavities in balconies have been sealed | Pass Fail, N/A
checkpoint | All wiring including interconnection wiring and power from isolator to the condensers are roughed without defect | Pass Fail, N/A
checkpoint | Refrigeration insulation is not damaged | Pass Fail, N/A
checkpoint | Where refrigeration lines insulated and supported pipe clamps have been installed to avoid damage to insulation | Pass Fail, N/A
checkpoint | Refrigeration pipes are run to condenser without being kinked or damaged | Pass Fail, N/A
checkpoint | All refrigeration pipes, including bends where pass through stud wall are above the ceiling height (+2750mm Above Metre Mark) | Pass Fail, N/A
checkpoint | Vent boxes are sealed | Pass Fail, N/A
section | Sign Off
checkpoint | Sign-Off Completed as per below (Pass once complete)
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Ceiling Closure Checklist
section | Air-Conditioning
checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
text | Ceiling Closure Date
checkpoint | Units all hung with isolation mounts and with 5% fall to drain point | Pass Fail, N/A
checkpoint | Other services installed are not impeding access to fan coil | Pass Fail, N/A
checkpoint | Wiring connections have been terminated to indoor unit electrical box | Pass Fail, N/A
checkpoint | Condensate drainage is in correct location and height | Pass Fail, N/A
checkpoint | Filter Track for return air have been installed at the back of unit | Pass Fail, N/A
checkpoint | Zone damper instaled as per mechanical drawigns designated locations | Pass Fail, N/A
checkpoint | All flexible ducts connections to air terminlas and spigots have been air tight by using duct tape | Pass Fail, N/A
checkpoint | All flexible ducts connections to air terminlas and spigots have been secured by using fixing ties/cables ties | Pass Fail, N/A
checkpoint | Filters for return air have been installed at the back of unit | Pass Fail, N/A
section | Ventilation
checkpoint | Inspection Date - Comment below
text | Date of Inspection
checkpoint | All Flex has been run to correct location | Pass Fail, N/A
checkpoint | All flex are hung independent of other services and supported by intact load spreaders | Pass Fail, N/A
checkpoint | All flexible ducts have been mechanically secured to spigots and air terminals by using fixing ties | Pass Fail, N/A
checkpoint | Filters for return air have been installed at the back of unit | Pass Fail, N/A
checkpoint | PVC sleeves has been installed in wet area walls | Pass Fail, N/A
checkpoint | Vent boxes are installed in correct location as per RCP and SEALED | Pass Fail, N/A
| PVC ducts have been hung and supported indicidually by using hanging straps | Pass Fail, N/A
section | Access Panels
checkpoint | Inspection Date - Comment below
text | Date of Inspection
checkpoint | Access Panel location has been marked on floor as per RCP | Pass Fail, N/A
checkpoint | Access panel location allows sufficient access equipment | Pass Fail, N/A
checkpoint | All other other services do not impede access | Pass Fail, N/A
section | Sign Off
checkpoint | Sign-Off Completed as per below (Pass once complete)
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Common Area Rough in Checklist - General
checkpoint | Inspection Date - Comment below
text | Date of Inspection
checkpoint | Other services installed are not impeding access to fan coil | Pass Fail, N/A
checkpoint | All Ductwork passing block walls are flushed and sealed | Pass Fail, N/A
checkpoint | Transfer duct installed at Accessible toilet wall and penetration flushed and sealed | Pass Fail, N/A
checkpoint | Where passing the block wall flexible ducts has been equipped with Sleeve and penetration sealed | Pass Fail, N/A
checkpoint | Refrigerant pipes passing through fire rarted walls are sealed at wall penetratiobn byu using approved material | Pass Fail, N/A
checkpoint | Sign-Off Completed as per below (Pass once complete)
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Common Area Fit-Off Checklist
checkpoint | Lobby supply grilles fitted | Pass Fail, N/A
checkpoint | Lobby Smoke relief Air grille has been installed | Pass Fail, N/A
checkpoint | All fire dampers provided with an access panel as per mechanical drawing | Pass Fail, N/A
checkpoint | Garbage Room Grlille has been fitted | Pass Fail, N/A
checkpoint | All refrigeration pipes has been labelled as with approved label type | Pass Fail, N/A
checkpoint | Sign-Off Completed as per below (Pass once complete)
text | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Duct Installation Checklist
text | Riser ID
checkpoint | Are drawings on site the latest issue | Pass Fail, N/A
checkpoint | Are plant and equipment location correct | Pass Fail, N/A
checkpoint | Duct size and location correct | Pass Fail, N/A
checkpoint | Material and gauge correct | Pass Fail, N/A
checkpoint | Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method | Pass Fail, N/A
checkpoint | Is correct jointing method being used | Pass Fail, N/A
checkpoint | Are joints completed and cleated installed on flanges | Pass Fail, N/A
checkpoint | Is correct joint sealant being used | Pass Fail, N/A
checkpoint | Is ductwork installation complete | Pass Fail, N/A
type | name | values | prefix | postfix
checklist | Fit-Off Checklist
section | Internal
checkpoint | AC grille to living room installed with no defect | Pass Fail, N/A
checkpoint | AC grille to bedroom installed with no defect | Pass Fail, N/A
checkpoint | Return Air grille installed as per RCP drawings | Pass Fail, N/A
checkpoint | Range hood duct connected and taped to ensure air tight | Pass Fail, N/A
checkpoint | AC Controller installed as per RCP drawings | Pass Fail, N/A
checkpoint | Condensation drain is connected to Tundish point 10 mm air gap is provided at the connection point | Pass Fail, N/A
checkpoint | Ensuit Exhasut fans installed and pluged in as per mechanical drawings | Pass Fail, N/A
checkpoint | Laundry Exhasut fans installed and pluged in as per mechanical drawings | Pass Fail, N/A
checkpoint | Toielt Exhasut fans installed and pluged in as per mechanical drawings | Pass Fail, N/A
section | External
checkpoint | Access panels placed as per drawings | Pass Fail, N/A
checkpoint | Condenser unit installed, refrigeration pipes are connected , all gaps to insulation is sealed and pipes are not kinked | Pass Fail, N/A
checkpoint | External louvres installed all gaps sealed between plenum box and wall/ louvre flange to wall , photo evidence provided for below | Pass Fail, N/A
button | Box sealed internally and the gap between the box and wall is sealed | Pass Fail, N/A
button | Louvre flanges sealed to the external box | Pass Fail, N/A
checkpoint | Sign-Off Completed as per below (Pass once complete)
text | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | A/C Commissioning Checklist
checkpoint | Refrigeration lines have been pressurised and have maintained pressure for more than 24hrs | Pass Fail, N/A
checkpoint | Refrigerant lines have been vacuumed to 500 microns and maintained the vacuum | Pass Fail, N/A
checkpoint | Indoor unit drains have been terminated to the tundish point | Pass Fail, N/A
checkpoint | Outdoor unit drains have been terminated to the tundish point | Pass Fail, N/A
checkpoint | Indoor unit flare connection has been properly insulated with specified insulation | Pass Fail, N/A
checkpoint | Indoor unit drain connection point has been securely fastened and sealed | Pass Fail, N/A
checkpoint | A/C system has been operated for a minimum of 5hrs and no leaks are visible in the drain lines | Pass Fail, N/A
checkpoint | A/C System Flows checked as per mechanical drawings | Pass Fail, N/A
button | Adequate flow has been achieved in bedroom 1 | Pass Fail, N/A
button | Adequate flow has been achieved in bedroom 2 | Pass Fail, N/A
button | Adequate flow has been achieved in bedroom 3/study | Pass Fail, N/A
button | Adequate flow has been achieved in living room | Pass Fail, N/A
checkpoint | Sign-Off Completed as per below (Pass once complete)
text | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Ventilation Checklist
checkpoint | Commissioned as per below (Pass once complete)
button | Fan has been tested and is operational | Pass Fail, N/A
button | Adequate flow has been achieved in bedroom 1 | Pass Fail, N/A
button | Adequate flow has been achieved in Ensuite | Pass Fail, N/A
button | Adequate flow has been achieved in Laundry | Pass Fail, N/A
checkpoint | Range Hood has been tested & is operational | Pass Fail, N/A
button | Adequate flow has been achieved Range Hood | Pass Fail, N/A
checkpoint | Sign-Off Completed as per below (Pass once complete)
text | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Core Hole Checklist
checkpoint | Penetration details have been captured
text | Penetration ID #1:
text | Penetration ID #2:
button | Number of Penetrations | 1, 2, 3, 4, 5
checkpoint | Core hole max 120mm with Firepex sealant filled to a depth of 60mm from either side of wall | Pass Fail, N/A
checkpoint | Cables to be tucked between insulation for a minimum of 300mm each side of the penetration | Pass Fail, N/A
checkpoint | The penetration is labelled and photographic evidence is provided | Pass Fail, N/A
checkpoint | Maximum services passing the penetration is not exceeding the following | Pass Fail, N/A
bool | Two insulated copper pipes with up-to 20mm insulated thickness, with cable up-to 12mm | Pass Fail, N/A
bool | Maximum 1 set of flexible or rigid drain is passing the penetration | Pass Fail, N/A
bool | 20mm. Insulation is FR Amaflex or similar | Pass Fail, N/A
text | Notes/Additional Comments
checkpoint | Sign-Off Completed as per below (Pass once complete)
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
type | name | values | prefix | postfix
checklist | Fire Damper Checklist -WSW6
checklist
checkpoint | Penetration details have been captured
text | Penetration ID
text | Manufacturer
text | Inspection Date
text | Apartment
text | Penetration Location
checkpoint | Centralise the casing and firestop the gap between the casing and wall with Kilargo intumscent sealant. Backing rod used as required to control sealant fill depth. Maximum annular gap between casing and wall 25mm
checkpoint | Approved fire rated mastic has been applied to entire perimeter of fire damper cell on both sides. No evidence of cracking.
checkpoint | Casing perimeter is sealed with Approved intumescent sealant. No evidence of cracking.
checkpoint | O.7mm or greater Z275 Gal steel casing positioned centrally in penetration aperture
checkpoint | Duct Riser is connected to the casing usingSteel Screws or Steel Pop Rivet
checkpoint | 0.7mm (min) Z275 galvanised steel angles to all four sides, angle dimensions shall be continous and at least 2x the dimension of the gap between damper casing and penetrating element
checkpoint | Ensure product and certification labels are in a prominent position for easy identification during subsequent maintenance inspections.
checkpoint | Access is provided to conveniently access fire damper for visual a inspections.
checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
checkpoint | Pictures attached
text | Notes/Additional Comments:
checkpoint | Signature (Contract/Subcontractor Assessor)
text | Date
checkpoint | Siganture (Builder Representative)
text | Name
|  | values | prefix | postfix
type | name | values | prefix | postfix
checklist | Fire Box Checklist
checkpoint | Fire Box Nominally placed in the penetration opening
label | Any issues with fit photo/comment below
checkpoint | Fire Box Fitted Correctly - As per below
button | Fyreflex Mastic is applied around the FyreBox to at least 20mm deep to fill up the gaps | Yes, No, N/A
button | Mounting flanges are fitted around the Fyrebox and are hard up against the wall | Yes, No, N/A
button | Steel Rivet or Screw used to secure the last corner of the flange together | Yes, No, N/A
button | M6 masonry anchors used at 400mm centered to fix the flanges to the wall through preformed holes | Yes, No, N/A
checkpoint | Black foam cut and placed in the Fyrebox to fill up any gaps within the services
checkpoint | FyreWrap installed 450mm from the wall on both sides of the box
button | Steel strapping used to fix the Fyrewrap at three locations | Yes, No, N/A
button | 25mmx25mm nominal fillet of FyreFlex sealant used to seal around the wrap and the wall | Yes, No, N/A
checkpoint | Pictures of Installation attached below
text | Notes/Additional Comments
checkpoint | Sign-Off Completed as per below (Pass once complete)
text | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)

## Fire damper Schedule
LABEL | LOCATION | SIZE (mm) | REFERENCE | Wall Type | SYSTEM TYPE
TBA | Basement 1 | 450x250
TBA | Basement 1 | 250x200
FD-L1.1 | Level 1 | 200x200 | Refuse Rm | Hebel+Gyprock | WSW6
FD-L1.2 | Level 1 | 200x200 | Lobby | Hebel+Gyprock | WSW6
FD-L2.1 | Level 2 | 200x200 | Refuse Rm | Hebel+Gyprock | WSW6
FD-L2.2 | Level 2 | 200x200 | Lobby | Hebel+Gyprock | WSW6
FD-L3.1 | Level 3 | 200x200 | Refuse Rm | Hebel+Gyprock | WSW6
FD-L3.2 | Level 3 | 200x200 | Lobby | Hebel+Gyprock | WSW6
FD-L4.1 | Level 4 | 200x200 | Refuse Rm | Hebel+Gyprock | WSW6
FD-L4.2 | Level 4 | 200x200 | Lobby | Hebel+Gyprock | WSW6