## Table 1
[10 empty] | Inspection and Test Plan - Control and Supervision of the Works | [18 empty] | Doc ID: FH-ZU2-QU-ITP044 REV: 0
Client: Melbourne Airport | [13 empty] | Contract No: CP14038-01 | [8 empty] | Prepared By: Giuliano Follacchio
Project: Taxiway Zulu | [19 empty] | Reviewed By: Jason Lee | [8 empty] | Date: 29/8/24
Construction Process: AGL Luminaires | [19 empty] | Approved By: Giuliano Follacchio | [8 empty] | Date: 29/8/24
Specifications: ZULU-BECA-001-SPC-00003
Structure / Component: AGL
Lot No: Lot Details: Lot size/Quantity: Date:
Item No. |  | Task / Activity Description |  |  |  |  | Inspection/Test | [14 empty] | HP / WP AP / IP / TP /SCP |  | Responsibility Project Engineer Superintendent Surveyor Foreman |  |  |  | Checked by:
[7 empty] | Frequency |  |  | Acceptance Criteria | [5 empty] | Reference Documents |  | Inspection / Test Method |  | Record of conformity | [7 empty] | Subcontractor |  |  | Beca | FH | Date
1 |  | Preliminary Works
1.1 |  | Check for correct documentation |  |  |  |  | Prior to commencing any activity |  |  | Ensure that all employees and subcontractors are using the latest and complete set of drawings | [5 empty] | IFC Drawings |  | Verify |  | Drawings |  | IP |  | Project Engineer
1.2 |  | Implementation of all measures and controls |  |  |  |  | Prior to commencing any activities |  |  | All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP. | [5 empty] | PSP, EMP, TMP, JSEA, SWMS, WP |  | Verify |  | Site and office Inspection |  | HP* |  | Project Engineer / Site Supervisor
1.3 |  | Material/equipment approvals |  |  |  |  | Prior to start |  |  | All materials shall be proven to meet contractual requirements prior to acceptance. - MAGS shall be from ATG Airfield guidance signs range - Taxiway centre lights shall be - from the ADB Safegate range only - Runway guard lights shall be from ADB Safegate only. - Intermediate hold position lights shall be from the ADB Safegate range only - Stop Bar Lights shall be from the ADB Safegate - IWDI shall be from ALS Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering. | [5 empty] | ZULU- BECA-001- SPC- 00003 cl 2.3 |  | Verify |  | Aconex reference(s) |  | HP* |  | Project Engineer
1.4 |  | Setting out for airfield luminaires |  |  |  |  | Each Lot |  |  | HOLD POINT The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator. | [5 empty] | ZULU- BECA-001- SPC- 00003 cl 5.4 |  | Verify |  | Aconex reference |  | HP |  | Project Engineer / Beca
2 |  | Installation of AGL Luminaires
2.1 |  | Elevated Light Installation |  |  |  |  | Each Lot |  |  | Components of elevated lights shall: - Be less than 360mm above the pavement level including the frangible coupling. - Be suitable for installation on a threaded connection when installed. | [5 empty] | ZULU-BECA-001- SPC- 00003 Cl 4.4.4.1 |  | Verify |  | This ITP signed |  | IP |  | Project Engineer
2.2 |  | Inset Light Installation |  |  |  |  | Each Lot |  |  | Components of inset lights shall: - Be less than 13mm height above the surrounding surface. - Have a slope of surface of the unit to be less than 20 degrees (not including any recesses). | [5 empty] | ZULU- BECA-001- SPC- 00003 cl 4.4.4.3 |  | Verify |  | This ITP signed ADBSG Installation of Inset Light Fittings checklist |  | IP |  | Project Engineer
2.3 |  | Series Isolation Transformer (SIT) |  |  |  |  | Each Lot |  |  | SITs shall be installed in specified deep base cans or pits | [5 empty] | ZULU- BECA-001- SPC- 00003 Cl 4.3 |  | Verify |  | This ITP signed ADBSG Installation of Series Isolating Transformer (SIT) |  | IP |  | Project Engineer
2.4 |  | Luminaire Circuit |  |  |  |  | Each lot |  |  | Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule. | [5 empty] | ZULU- BECA-024- DWG- 09001-16 |  | Verify |  | This ITP signed As-Built Documentation |  | IP |  | Project Engineer
3 |  | Post Construction
3.1 |  | As-Built |  |  |  |  | Each lot |  |  | Submission of surveyed luminaire position to superintendent prior to practical completion | [5 empty] | WP-001-09 |  | Verify |  | SCP |  | SCP |  | Project Engineer
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
[10 empty] | Inspection and Test Plan - Control and Supervision of the Works | [18 empty] | Doc ID: FH-ZU2-QU-ITP044 REV: 0
Client: Melbourne Airport | [13 empty] | Contract No: CP14038-01 | [8 empty] | Prepared By: Giuliano Follacchio
Project: Taxiway Zulu | [19 empty] | Reviewed By: Jason Lee | [8 empty] | Date: 29/8/24
Construction Process: AGL Luminaires | [19 empty] | Approved By: Giuliano Follacchio | [8 empty] | Date: 29/8/24
Specifications: ZULU-BECA-001-SPC-00003
Structure / Component: AGL
HP |  | Hold Point |  |  |  | Work shall not proceed past the HP until released by the Superintendent | [10 empty] | IP |  | Inspection point |  |  | Formal Inspection to be done and recorded
HP* |  | Fulton Hogan Hold Point |  |  |  | Work shall not proceed past the HP* until released by Fulton Hogan | [10 empty] | TP |  | Test Point |  |  | Product compliance test to be undertaken and recorded/reported
WP |  | Witness Point |  |  |  | An inspection which must be witnessed by the Superintendent | [10 empty] | SCP |  | Survey conformance point |  |  | A qualified surveyor to check product/section/structure and report
AP |  | Approval Point |  |  |  | Written or verbal approval given by the Superintendent
Notes
[9 empty] | INSPECTION AND TEST PLAN Installation of Series Isolating Transformer (SIT) and Cable Jointing | [15 empty] | Page |  | 1 of 2
[25 empty] | Issue Date |  | 2024-03-30
[25 empty] | Revision |  | 1
REPORT DETAILS |  |  |  |  | Date Completed | [11 empty] | Drawing References |  |  |  | ZULU-BECA-024-DWG
[5 empty] | Project |  |  |  | Taxiway Zulu 2.0 | [7 empty] | Sheet Completed by
Location on Site
WORK DETAILS | [16 empty] | Legend |  |  |  | ✓ yes ✗ no NA not applicable
TERMINATION OF ELECTRICAL CABLES | [13 empty] | INSTALLATION OF SERIES ISOLATING TRANSFORMER AND ACCESSORIES | [6 empty] | PRIMARY / SECONDARY LABELLING | [5 empty] | NOTES
Pit / Deep Base Can No. |  |  | Light No |  | Circuit No. |  |  | Plugs terminated to Primary Cable for SIT (2x) | Record Installed SIT Type (Watts) |  |  | SIT Plugged in and Heatshrink | 6mm Earth Cable installed to SIT | Secondary Cable for SIT Terminated (If applicable) |  |  | Primary Cables Labelled with Circuit Number |  |  |  | Secondary Cable Labelled with Light Number | Tidy Cables (Cable- tie Slack Cables) |  |  | New Pit Cleaned (If applicable)
[9 empty] | INSPECTION AND TEST PLAN Installation of Series Isolating Transformer (SIT) and Cable Jointing | [15 empty] | Page |  | 2 of 2
[25 empty] | Issue Date |  | 2024-03-30
[25 empty] | Revision |  | 1
WORK DETAILS | [16 empty] | Legend |  |  |  | ✓ yes ✗ no NA not applicable
TERMINATION OF PRIMARY AND SECONDARY CABLES | [13 empty] | INSTALLATION OF SERIES ISOLATING TRANSFORMER AND ACCESSORIES | [6 empty] | PRIMARY / SECONDARY LABELLING | [5 empty] | NOTES
Pit / Deep Base Can No. |  |  | Light No |  | Circuit No. |  |  | Plugs terminated to Primary Cable for SIT (2x) | Record Installed SIT Type (Watts) |  |  | SIT Plugged in and Heatshrink | 6mm Earth Cable installed to SIT | Secondary Cable for SIT Terminated (If applicable) |  |  | Primary Cables Labelled with Circuit Number |  |  |  | Secondary Cable Labelled with Light Number | Tidy Cables (Cable- tie Slack Cables) |  |  | New Pit Cleaned (If applicable)
[8 empty] | INSPECTION AND TEST PLAN Installation of Inset Light Fittings | [17 empty] | Page |  |  |  | 1 of 2
[26 empty] | Issue Date |  |  |  | 2024-03-30
[26 empty] | Revision |  |  |  | 1
REPORT DETAILS |  |  |  | Date Completed | [10 empty] | Drawing References |  |  |  |  | ZULU-BECA-024-DWG
|  |  |  | Project |  |  |  | Taxiway Zulu 2.0 | [6 empty] | Sheet Completed by
Location on Site
WORK DETAILS | [14 empty] | Legend |  |  |  |  | ✓ yes ✗ no NA not applicable
LIGHT FITTING INSTALLATION | [29 empty] | Notes
Light no |  |  |  | Light Labelled |  |  |  | Correct Orientation |  |  | Light Fitting Torqued to manufacturer's specfication |  |  |  | Light Fitting Details (Eg. Type GG W Bi- Direct etc.) |  |  |  |  | Sec Cable Plugged into Light Fitting |  |  | Can Cleaned out |  |  | Light Programmed / Verified on Circuit Monitor
[8 empty] | INSPECTION AND TEST PLAN Installation of Inset Light Fittings | [17 empty] | Page |  |  |  | 2 of 2
[26 empty] | Issue Date |  |  |  | 2024-03-30
[26 empty] | Revision |  |  |  | 1
WORK DETAILS CONTINUED | [14 empty] | Legend |  |  |  |  | ✓ yes ✗ no NA not applicable
LIGHT FITTING INSTALLATION | [29 empty] | Notes
Light no |  |  |  | Light Labelled |  |  |  | Correct Orientation |  |  | Light Fitting Torqued to manufacturer's specfication |  |  |  | Light Fitting Details (Eg. Type GG W Bi-Direct etc.) |  |  |  |  | Sec Cable Plugged into Light Fitting |  |  | Can Cleaned out |  |  | Light Programmed / Verified on Circuit Monitor