## QA Folder Structure
QA Folder Structure |  |  |  | Checklists | NOTES
Aurora
Site Estab/Prelims/Temps
In Grounds | B2 |  |  | Ingrounds - Drainage
Ingrounds - Pumpwells/Tanks/Pits
Ingrounds - Cast in
| B1 (Lower) |  |  | Ingrounds - Drainage
Ingrounds - Pumpwells/Tanks/Pits
Ingrounds - Cast in
Ingrounds - Sewer BT Authority Connection
Ingrounds - Stormwater LPD
Ingrounds - Authority connection to meter room
Hydraulic Services
Penetrations (incl Cast In)
|  | B2 |  | Peno - Slab
Peno - Wall
|  | B1 |  | Peno - Slab
Peno - Wall
|  | Ground |  | Peno - Slab
Peno - Wall
Peno - Cast In
|  | Level 1 - Level 8 |  | Peno - Slab | Please expand out so there is a folder for each Level 1, Level 2, Level 3 etc)
Peno - Wall
Drains, Stacks & Vents
|  | B2 |  | Stack Riser: Sewer, Stormwater, Vent & Greasy Vent
Stack Riser: Greasy Waste & Pumplines
Drains - Underslung: Sewer, Stormwater & Vent
Drains: Underslung: Greasy Waste
Drains: Underslung: Pumpline
|  | B1 |  | Stack Riser: Sewer, Stormwater, Vent & Greasy Vent
Stack Riser: Greasy Waste & Pumplines
Drains - Underslung: Sewer, Stormwater & Vent
Drains: Underslung: Greasy Waste
Drains: Underslung: Pumpline
|  | Ground - Level 8 |  | Stack Riser: Sewer, Stormwater, Vent & Greasy Vent | Please expand out so there is a folder for each (Ground, Level 1, Level 2, Level 3 etc)
Drains - Underslung: Sewer, Stormwater & Vent
Rough In
|  | B2 |  | Main Run Rough In (Cold Water)
Rough In - CW Design Components
Main Run Rough In (Non Potable/Rainwater)
Rough In - RW Design Components
|  | B1 |  | Main Run Rough In (Cold Water)
Main Run Rough In (Non Potable/Rainwater)
Main Run Rough In (Hot Water)
Rough In - Mains Water Meter Assembly
Ground
|  |  | Main Run | Main Run Rough In (Cold Water)
Main Run Rough In (Non Potable/Rainwater)
Main Run Rough In (Hot Water)
|  |  | Retail 01 | Rough In - Meter Install (Fitout)
|  |  | Office 01 | Rough In - Meter Install (Fitout)
|  |  | EOT - Acc WshRm L00.15 | Water Services (High & Low Level Rough In)
|  |  | EOT - WshRm L00.16 | Water Services (High & Low Level Rough In)
|  |  | EOT - WshRm L00.17 | Water Services (High & Low Level Rough In)
|  |  | EOT - WshRm L00.18 | Water Services (High & Low Level Rough In)
|  |  | EOT - WshRm L00.19 | Water Services (High & Low Level Rough In)
|  |  | EOT - WshRm L00.20 | Water Services (High & Low Level Rough In)
|  |  | EOT - WshRm L00.21 | Water Services (High & Low Level Rough In)
|  |  | EOT - Unisex WC L00.22 | Water Services (High & Low Level Rough In)
|  |  | EOT - Unisex WC L00.23 | Water Services (High & Low Level Rough In)
|  |  | EOT - Acc WC L00.24 | Water Services (High & Low Level Rough In)
|  |  | EOT - Island basin station | Water Services (High & Low Level Rough In)
|  |  | EOT - WC | Water Services (High & Low Level Rough In)
|  |  | EOT - Ambulant WC | Water Services (High & Low Level Rough In)
Level 1
|  |  | Main Run | Main Run Rough In (Cold Water)
Main Run Rough In (Non Potable/Rainwater)
Main Run Rough In (Hot Water)
Rough In - Meter Install (Fitout)
|  |  | Tea point | Water Services (High & Low Level Rough In)
|  |  | WC 1 - L01.07 | Water Services (High & Low Level Rough In)
|  |  | Acc WC - L01.08 | Water Services (High & Low Level Rough In)
|  |  | WC 1 - L01.09 | Water Services (High & Low Level Rough In)
|  | Level 2 - Level 7 |  |  | Please expand out so there is a folder for each (Level 2, Level 3 etc)
|  |  | Main Run | Main Run Rough In (Cold Water)
Main Run Rough In (Hot Water)
Rough In - Meter Install (Fitout)
|  |  | Tea point | Water Services (High & Low Level Rough In)
|  |  | Unisex WC 1 | Water Services (High & Low Level Rough In)
|  |  | Acc WC | Water Services (High & Low Level Rough In)
|  |  | Unisex WC 2 | Water Services (High & Low Level Rough In)
Level 8
|  |  | Main Run | Main Run Rough In (Cold Water)
Main Run Rough In (Hot Water)
Rough In - Meter Install (Fitout)
|  |  | BBQ Area | Water Services (High & Low Level Rough In)
|  |  | Acc WC | Water Services (High & Low Level Rough In)
Risers
|  | B2 - Level 8 |  | Risers (CW, HWF & HWR, Rainwater) | Please expand out so there is a folder for each (B2, B1, Ground, Level 1, Level 2, Level 3 etc)
Fit Off/ Install
Ground
|  |  | EOT - Acc WshRm L00.15 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WshRm L00.16 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WshRm L00.17 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WshRm L00.18 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WshRm L00.19 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WshRm L00.20 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WshRm L00.21 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - Unisex WC L00.22 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - Unisex WC L00.23 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - Acc WC L00.24 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - Island basin station | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | EOT - WC | Fit Off/ Fixture Install Toilets & Cisterns
|  |  | EOT - Ambulant WC | Fit Off/ Fixture Install Toilets & Cisterns
|  | Level 1 - Level 7 |  |  | Please expand out so there is a folder for each Level 1, Level 2, Level 3 etc)
|  |  | Tea point | Fit Off/ Fixture Install - All Items
|  |  | Unisex WC 1 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | Acc WC | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
|  |  | Unisex WC 2 | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
Level 8
|  |  | BBQ Area | Fit Off/ Fixture Install - All Items
|  |  | Acc WC | Fit Off/ Fixture Install Toilets & Cisterns
Fit Off/ Fixture Install - All Items
Testing
B2
|  |  | Risers | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Main Rough In | Testing - Potable Water - 1500kpa water test (not an air test)
|  | B1 | Risers | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Main Rough In | Testing - Potable Water - 1500kpa water test (not an air test)
Ground
|  |  | Risers | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Main Rough In | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | EOTArea | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test)
Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test)
Level 1
|  |  | Risers | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Main Rough In | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Tea point & WC area | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test)
Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test)
Level 2 - Level 7
|  |  | Risers | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Main Rough In | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Tea point & WC area | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test)
Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test)
Level 8
|  |  | Risers | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | Main Rough In | Testing - Potable Water - 1500kpa water test (not an air test)
|  |  | WC area | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test)
Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test)
Plant & Equipment
Meters
Commissioning/Handover
Ground
|  |  | EOT - Acc WshRm L00.15 | Comm - TMV
|  |  | EOT - WshRm L00.16 | Comm - Tempering Valve
|  |  | EOT - WshRm L00.17 | Comm - Tempering Valve
|  |  | EOT - WshRm L00.18 | Comm - Tempering Valve
|  |  | EOT - WshRm L00.19 | Comm - Tempering Valve
|  |  | EOT - WshRm L00.20 | Comm - Tempering Valve
|  |  | EOT - WshRm L00.21 | Comm - Tempering Valve
|  |  | EOT - Unisex WC L00.22 | Comm - Tempering Valve
|  |  | EOT - Unisex WC L00.23 | Comm - Tempering Valve
|  |  | EOT - Acc WC L00.24 | Comm - TMV
|  |  | EOT - Island basin station | Comm - Tempering Valve
Level 1 - Level 7
|  |  | Tea point | Comm - Tempering Valve
|  |  | Unisex WC 1 | Comm - Tempering Valve
|  |  | Acc WC | Comm - TMV
|  |  | Unisex WC 2 | Comm - Tempering Valve
Level 8
|  |  | Acc WC | Comm - TMV

## Checklists
type | name | values | prefix | postfix | usage count | user addable
checklist-flat | Ingrounds - Drainage
label | ITP/Checklist for Ingrounds - Drainage
text | Description of work zone (e. location/drawing grid reference)
checkpoint | Installation complies with AS/NZS-3500 (2021), current IFC drawings & specifications
checkpoint | Inspection openings and/or clean outs have been installed
checkpoint | All drains are clear of debris and have been securely capped
checkpoint | Invert levels for drains and inspection openings have been checked against current IFC drawings
checkpoint | All drains have been tested
checkpoint | All drains have been backfilled and compaction completed
checklist-flat | Ingrounds - Pumpwells/Tanks/Pits
label | ITP/Checklist for Ingrounds - Installation of pumpwells/tanks/pits
text | Description of work zone (e. location/drawing grid reference)
checkpoint | Installation complies with AS/NZS-3500 (2021), current IFC drawings & specifications
checkpoint | Installation methods & materials are in accordance with manufacturer requirements
checkpoint | Invert levels for inlets, outlets and cover levels have been checked against current IFC drawings
checkpoint | Connection of drainage to pumpwell/tank/pit has been sealed/caulked/grouted both inside and outside
checkpoint | Cast in conduits to pump control panels are correctly sized and in accordance with current IFC drawings
checklist-flat | Ingrounds - Cast in
label | ITP/Checklist for Ingrounds - cast in elements
text | Description of work zone (e. location/drawing grid reference)
checkpoint | Installation complies with current IFC shop drawings
checkpoint | All pipe elements free of damage prior to install
checkpoint | Where practical, pipes water tested prior to the pour
checkpoint | Pipe grades and size have been checked
checkpoint | Invert levels and finished levels have been checked
checkpoint | PVC has been lagged (add photos)
checkpoint | HDPE fusion welds are witness marked
checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | Details of cast in element
text | Location and description of what has been cast in
checklist-flat | Ingrounds - Sewer BT Authority Connection
label | ITP/Checklist for Ingrounds - Sewer BT Authority Connection
checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation meets water authority requirements
checkpoint | All pipe elements free of damage prior to install
checkpoint | Boundary trap is installed and supported correctly
checkpoint | Reflux valve is installed and supported correctly
checkpoint | Access riser to surface level is installed
checklist-flat | Ingrounds - Stormwater LPD
label | ITP/Checklist for Ingrounds - Stormwater LPD
checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation meets Council requirements
checkpoint | All pipe elements free of damage prior to install
checkpoint | Civil pit/s installed and supported correctly
checkpoint | If applicable, reflux valve is installed and supported correctly
checkpoint | Access riser to surface level is installed
checklist-flat | Ingrounds - Authority connection to meter room
label | ITP/Checklist for Ingrounds - Authority connection to meter room
checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation meets water authority requirements
checkpoint | All pipe elements free of damage prior to install
checkpoint | Pipework is connected to water meter assemblies
checkpoint | Pipes have been wrapped in plastic (or denso wrap)
checkpoint | Pipe bedding is correct
checkpoint | Pipes are labelled
checkpoint | Any open ends have been sealed
checkpoint | All mechanical joints are correct and have been checked
checkpoint | Access riser from sluice valves to surface level installed
checklist-flat | Peno - Slab
label | ITP/Checklist for Slab penetrations
checkpoint | Installation complies with current IFC shop drawing
checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint | Collars are firmly secured into formwork
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | Peno - Wall
label | ITP/Checklist for Penetrations through the core/precast etc
checkpoint | Installation complies with current IFC shop drawings
text | Document invert level wall peno has been installed at |  |  | mm
checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | Peno - Cast In
label | ITP/Checklist for elements cast into the slab
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint | Where practical, pipes water tested prior to the pour
checkpoint | Pipe grades and size have been checked
checkpoint | Invert levels and finished levels have been checked
checkpoint | PVC has been lagged (add photos)
checkpoint | HDPE fusion welds are witness marked
checkpoint | RWO body installed level
checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | Drains - Underslung: Sewer, Stormwater & Vent
label | ITP/Checklist for underslung/suspended drains (sewer, stormwater and vents)
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/grade meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | Drains: Underslung: Greasy Waste
label | ITP/Checklist for underslung/suspended drains for greasy waste
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | Drains: Underslung: Pumpline
label | ITP/Checklist for underslung/suspended pumplines
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct with secure fixings to reduce pipe movement
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Pumpline has been water tested (include photos)
checklist-flat | Stack Riser: Sewer, Stormwater, Vent & Greasy Vent
label | ITP/Checklist for stack risers servicing sewer, stormwater & vents
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Clips, fixings & anchor points are correct and secure (includes independent clipping (no piggy backed clips)
checkpoint | Peno has been caulked (top and underside of slab)
checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint | Pipes & junctions are clear of debris
checkpoint | Inspection opening caps have been tightened and duct tape applied
checkpoint | For sewer: Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | Stack Riser: Greasy Waste & Pumplines
label | ITP/Checklist for stack risers for greasy waste and pumplines
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Clips, fixings & anchor points are correct and secure (includes independent clipping (no piggy backed clips)
checkpoint | Peno has been caulked (top and underside of slab)
checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint | Pipes & junctions are clear of debris
checkpoint | Expansion correctly clipped
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Greasy waste/pumpline has been water tested (include photos)
checklist-flat | Main Run Rough In (Cold Water)
label | ITP/Checklist for the main CW run from riser to tenancy/bathrooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Connected to meter manifold and pipe labelled with destination
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied
checkpoint | Rough in is ready for a hydrostatic water test
checklist-flat | Main Run Rough In (Hot Water)
label | ITP/Checklist for the main HWF & HWR run from riser to tenancy/bathrooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips, fixings & furrel blocks are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Hot water meter has been installed
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Rough in is ready for a hydrostatic water test
checklist-flat | Main Run Rough In (Non Potable/Rainwater)
label | ITP/Checklist for the main RW run from riser to tenancy/bathrooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied
checkpoint | Rough in is ready for a hydrostatic water test
checklist-flat | Rough In - CW Design Components
label | ITP/Checklist for specific design requirements for CW
checkpoint | CW tank bypass has been roughed in
checkpoint | CW backup to RW system has been roughed in
checkpoint | Check meter installed
checkpoint | RPZD/ back flow prevention device installed
checkpoint | Isolation valves installed
checkpoint | Pressure reducing valves installed
checkpoint | Future provision for connection to BMS
checkpoint | Installation complies with current IFC Schematic & shop drawings
checklist-flat | Rough In - RW Design Components
label | ITP/Checklist for specific design requirements for CW
checkpoint | CW backup to RW system has been roughed in
checkpoint | Check meter installed
checkpoint | Isolation valves installed
checkpoint | Future provision for connection to BMS
checkpoint | Installation complies with current IFC Schematic & shop drawings
checklist-flat | Rough In - Mains Water Meter Assembly
label | ITP/Checklist for specific design requirements for CW water meter assembly
checkpoint | Installation complies with current IFC Schematic & shop drawings
checkpoint | Installation meets water authority requirements with specific clearances, distances and heights achieved
checkpoint | Barrel unions have been used to allow for future maintenance ease
checklist-flat | Rough In - Meter Install (Fitout)
label | ITP/Checklist for install of meter for future fitout
checkpoint | Installation complies with current IFC Schematic & shop drawings
checkpoint | Meter installation meets water authority requirements
checkpoint | Isolation valve has been installed
checkpoint | PRV has been installed
checklist-flat | Risers (CW, HWF & HWR, Rainwater)
label | ITP/Checklist for install of all risers
checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Branch junctions & off-set levels are correct
checkpoint | Pipe joints & witness marks are correct
checkpoint | Checked for damage prior to install
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint | All risers are ready for testing
checklist-flat | Water Services (High & Low Level Rough In)
label | ITP/Checklist for rough in of high level and low level water services to specific areas (tea point/bathrooms/EOT etc)
checkpoint | Pressure Pipework (for high & low level rough-in) checked off as below
Label | Install Phase
Checkpoint | If pex is being insulated with armaflex, a barrier of duct tape has been applied to all pex crimp fittings
Checkpoint | All joints have been crimped correctly and to manufacturers spec
Checkpoint | Spacing of clips and fixings for WaterPex as per AS3500.1.2021
Checkpoint | Any pex through metal studs is entirely protected from sharp edges (achieve through additional oversized sleeving or suitable grommets)
Checkpoint | Check has been undertaken to ensure no cross connections
Checkpoint | All pex fittings are crimped and ready for 1500 kPa bump test
Label | Rough In Fitting Install
Checkpoint | Installation and location of tempering valve or T.M.V is correct (must be within access panel area)
Checkpoint | Location of shower mixer is as per latest IFC
Checkpoint | Location of lugged elbow is as per latest IFC
Checkpoint | Location of WC water point is as per latest IFC
Checkpoint | Location of vanity water points are as per latest IFC
checklist-flat | Fit Off/ Fixture Install Toilets & Cisterns
label | ITP/Checklist for fit off of toilet and cistern (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Installation is aligned, level and secure
checkpoint | Flush pipe has been measured to suit the pan prior to being cut to size
checkpoint | Button flush plate is in working order and not damaged/scratched
checkpoint | Seat and accessories are secure and correct
checkpoint | DDA suite back rest installed correctly
checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint | Pan trap is clear of debris
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | Fit Off/ Fixture Install - All Items
label | ITP/Checklist for fit off of all fixtures (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | All fixtures were checked for damage. Damaged fixtures do not get installed
checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint | All floor wastes and trap/s are clear of debris
checkpoint | All fixtures are covered and protected and the area is clean
label | Items installed
checkpoint | Vanity installed - aligned, level, secure, damage free (include photo)
checkpoint | Vanity tapware installed - aligned, level, damage free (include photo)
checkpoint | Shower rail/rose installed - secure, damage free (include photo)
checkpoint | Shower mixer installed - secure, damage free (include photo)
checkpoint | Kitchen sink installed - aligned, level, damage free (include photo)
checkpoint | Kitchen mixer installed - aligned, level, damage free (include photo)
checkpoint | Kitchen underbench boiling & chilling unit installed & connected - (include photo)
checklist-flat | Testing - Water Hold - Sewer & Stormwater Underslung
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint | Open ends have been sealed
checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint | Water was drained from the pipe at the end of the test
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint | Open ends have been sealed
checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint | Water was drained from the pipe at the end of the test
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | Testing - Potable Water - 1500kpa water test (not an air test)
label | ITP/Checklist for undertaking a hydrostatic test at 1500kPa
checkpoint | Water test is being conducted on material that is rated to withstand 1500kpa
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to 1500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test)
label | ITP/Checklist for undertaking a hydrostatic test to 500kPa to accommodate pressure sensitive fittings
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to 500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test)
label | ITP/Checklist for undertaking a bump test on Couta WaterPex fittings to meet manufacturer's guidelines
checkpoint | Pressure sensitive valves have been removed from test section (Note: this test will damage pressure sensitive fittings)
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Pressure was slowly increased to 1500kpa and held for 2 minutes
checkpoint | Pressure was decreased to 1000kpa and held for 20secs, then immediately and rapidly the pressure was increased back to 1500kpa for a further 2 minutes.
checkpoint | The previous step has been repeated: Pressure was decreased to 1000kpa and held for 20secs, then immediately and rapidly the pressure was increased back to 1500kpa and held for 30minutes.
text | Pressure reading photos must be taken at start & finish of 30minutes test. Add in comments (test duration etc)
checklist-flat | Comm - TMV
label | ITP/Checklist for commissioning TMV and temp testing each tap/mixer
text | Hot water delivery time from cold to stable hot to be logged |  |  | secs
text | Hot water delivery temperature to be logged |  |  | degrees
checkpoint | Test has been conducted to fully isolate CW supply to demonstrate HW is not delivered through TMV
checkpoint | System has been returned to working conditions
text | Temp and Time reading photos from each fitting must be taken at start & finish of test
checklist-flat | Comm - Tempering Valve
label | ITP/Checklist for commissioning Tempering valve and temp testing each tap/mixer
text | Hot water delivery time from cold to stable hot to be logged |  |  | secs
text | Hot water delivery temperature to be logged |  |  | degrees
checkpoint | System has been returned to working conditions
text | Temp and Time reading photos from each fitting must be taken at start & finish of test