## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Fire Detection Installation ITP |  |  |  |  | Yes | Fire Detection Installation ITP | 58083fd1-8e32-4f0c-831b-74b67bae8cb2
checkpoint-group |  |  | section | Installation Inspection
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
checkpoint-status |  |  | checkpoint | Installed to approved drawing
checkpoint-status |  |  | checkpoint | Check Cabling
checkpoint-status |  |  | checkpoint | Conduits installed
checkpoint-group |  |  | section | Cabling Rough In
checkpoint-status |  |  | checkpoint | Cabling roughed into RCP and interface locations and Cable continuity checks have been conducted prior to ceiling sheeting.
checkpoint-status |  |  | checkpoint | Fire Rating completed prior to ceiling sheeting
checkpoint-status |  |  | checkpoint | Are wires clearly drawn and submitted for AS BUILTS/AS CONSTRUCTED drawings
checkpoint-status |  |  | checkpoint | Riser Cable Tray Installation & cables fed
checkpoint-status |  |  | checkpoint | Fire rated cabling to floor LOOP, WIP, SPEAKER
checkpoint-status |  |  | checkpoint | Cable supported to tray
checkpoint-status |  |  | checkpoint | Cable connections
checkpoint-status |  |  | checkpoint | Fire rating of penetrations in riser
checkpoint-group |  |  | section | Final Fit Off
checkpoint-status |  |  | checkpoint | Thermal and Smoke Detectors
checkpoint-status |  |  | checkpoint | Check Thermal and Smoke Detectors installed in accordance with AS1670, AS1668, BCA
checkpoint-status |  |  | checkpoint | Spacing, no paints / marks & fit for purpose
checkpoint-status |  |  | checkpoint | Check Speakers installed in accordance with AS1670, BCA
checkpoint-status |  |  | checkpoint | Spacing, no paints / marks & fit for purpose
checkpoint-status |  |  | checkpoint | WIP & ECP installed in accordance with AS1670, BCA
checkpoint-status |  |  | checkpoint | Spacing, no paints / marks & fit for purpose
checkpoint-status |  |  | checkpoint | Check Interfaces as noted above are installed in accordance with AS1670, AS1668, BCA
checkpoint-status |  |  | checkpoint | Fit for purpose
checkpoint-status |  |  | checkpoint | Cabling Test to be conducted after fit off to confirm end of line resistance and/or loop continuity
checklist-sectioned |  |  | checklist | Sprinkler System Installation ITP |  |  |  |  | Yes | Sprinkler System Installation ITP | 74aed2a8-3ad1-4a89-ac38-8303435798a3
checkpoint-group |  |  | section | First Fix
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
checkpoint-status |  |  | checkpoint | Installed to approved drawing
checkpoint-status |  |  | checkpoint | Delivery inspection
checkpoint-status |  |  | checkpoint | Pipework to spec and approved sample
checkpoint-status |  |  | checkpoint | Fittings to spec and approved sample, piping & weld quality reviewed
checkpoint-status |  |  | checkpoint | Cut sheets and plans align with pipe delivered to sit
checkpoint-status |  |  | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
checkpoint-status |  |  | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
checkpoint-status |  |  | checkpoint | Valves Set Installed as per approved sample
checkpoint-status |  |  | checkpoint | Joints, connections, supports and position correct - any accessories installed if required
checkpoint-status |  |  | checkpoint | Controls and electrical services
checkpoint-status |  |  | checkpoint | Signage, Labelling, Locks and straps
checkpoint-status |  |  | checkpoint | Seismic Restraint Installed as per the design
checkpoint-status |  |  | checkpoint | Painting of exposed Pipework
checkpoint-group |  |  | section | Second Fix
checkpoint-status |  |  | checkpoint | Check Sprinkler Heads
checkpoint-status |  |  | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
checkpoint-status |  |  | checkpoint | Escutcheon plates added
checkpoint-status |  |  | checkpoint | Sprinkler Support Systems are installed to not impede other services installed
checkpoint-status |  |  | checkpoint | Seismic Restraint Installed as per the design
checkpoint-status |  |  | checkpoint | Fire Rating completed prior to ceiling sheeting
checkpoint-status |  |  | checkpoint | Sprinkler heads have been installed straight prior to ceiling sheeting PFS advise any heads found not straight will not be at our expense to rectify - please take photos
checkpoint-group |  |  | section | Final Fit Off
checkpoint-status |  |  | checkpoint | Check Sprinkler Heads
checkpoint-status |  |  | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
checkpoint-status |  |  | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
checkpoint-status |  |  | checkpoint | Escutcheon plates added
checkpoint-group |  |  | section | Hydraulic Pressure Test
checkpoint-status |  |  | checkpoint | 1.4MPa or 1400 kpa in excess of the maximum static working pressure (whichever is greater) for a period of 2 hours)
text | c1e22bb7-5490-5b66-a720-ae3c7913e014 |  | textbox | Start Time:
text | dd76b00a-115d-5487-82cd-28bb209f5285 |  | textbox | Pressure:
checkpoint-status |  |  | checkpoint | Attach picture of pressure test gauge:
text | 9dd0f077-ee1c-583c-899c-d809e600f34f |  | textbox | Finish Time:
text | 7f2409dc-9f12-5033-bce9-2acf216db520 |  | textbox | Pressure:
checklist-flat |  |  | checklist | Fire Pump Commissioning |  |  |  |  | Yes | Fire Pump Commissioning | 915c6233-3de8-4e25-9a40-d261eee4004e
checkpoint-status |  |  | checkpoint | Floor inspect to confirm all system works are complete
checkpoint-status |  |  | checkpoint | Confirm schematic design reference & pump room design drawings reference
checkpoint-status |  |  | checkpoint | Installation of only approved sample equipment & to approved drawing
checkpoint-status |  |  | checkpoint | Confirm factory acceptance testing documents from supplier
checkpoint-status |  |  | checkpoint | Complete pump room hydrostatic test
checkpoint-status |  |  | checkpoint | Confirm/witness Axis Hydrostatic testing of pipework system
checkpoint-status |  |  | checkpoint | Check pump area for obstructions
checkpoint-status |  |  | checkpoint | Check pump discharge drains
checkpoint-status |  |  | checkpoint | Check signage and ID plates on engine & pump
text | c34de4a1-8157-5780-a5bd-e053f4762e2f |  | textbox | Check and record number of water supply valves are secured
text | eb58c50c-bea2-579a-97f6-344c154bdfc8 |  | textbox | Record and verify pressure gauge readings suction kPa
checkpoint-status |  |  | checkpoint | Check general condition of Pump
checkpoint-status |  |  | checkpoint | Check Pump controller
checkpoint-status |  |  | checkpoint | Check monitor and engine start batteries and record
checkpoint-status |  |  | checkpoint | Check controller safety functions, alarms, set point validation and measurement of fuel consumption
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ 0 flow (record)
label | ac06465d-1b8e-598d-bd3c-3d0ac7ac36e9 |  | note | Check Pump Starting devices and record
text | f8987bb3-22c6-5ac2-a008-bbeabbc1b911 |  | textbox | Starting pressure (kpa)
text | 89ac5496-ba2f-5b56-8515-d22bfd9134aa |  | textbox | Run time
text | 9b62b60f-bee9-5113-b345-288b67d5913f |  | textbox | Hour meter
label | 745145f7-9d69-5576-b7ec-c428e43b19bf |  | note | Check and verify pump operation and record in comments
text | 8e9b3857-77f3-5d78-8307-7e8d55cf1be8 |  | textbox | Suction (kPa)
text | dd7e2b9f-9144-562b-871f-7dc726e9aa39 |  | textbox | Discharge (kPa)
text | 53222c57-38d3-5a1b-b8bf-25cc06707325 |  | textbox | Charger Voltage (V)
text | 27ad2cc8-d7ec-5c23-83c9-f4402e7553b8 |  | textbox | Oil Pressure (kPa)
text | 58c32663-b35a-57ad-9b24-a03abb3d2e35 |  | textbox | Engine Temp (C)
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ 130% flow (record)
label | 630b3b4e-7bc1-5f35-9c6b-16003a66923c |  | note | Check Pump Starting devices and record
text | 9ac0774c-6b7b-5b70-af38-beaec37da386 |  | textbox | Starting pressure (kpa)
text | 836a9c34-4d41-513e-a16b-31eb8b2a91bd |  | textbox | Run time
text | bf138287-99ec-5df0-ade2-3de5be600f5c |  | textbox | Hour meter
label | 6a23e277-97d7-5e45-9aab-158605c8dcac |  | note | Check and verify pump operation and record in comments
text | 0788b966-fab4-5414-a0b9-10e3b6ccd5f8 |  | textbox | Suction (kPa)
text | b83e498d-6553-50d5-afb3-5a0a216fb07c |  | textbox | Discharge (kPa)
text | b937a69b-344e-55d4-8036-3b4265c1fa31 |  | textbox | Charger Voltage (V)
text | 15b7a799-67f3-51f4-8f61-cfaa39c0a056 |  | textbox | Oil Pressure (kPa)
text | 3cd7a452-2533-569f-b115-e9be48929e48 |  | textbox | Engine Temp (C)
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ reduce flow to duty (record)
label | 10e41592-13e7-5f1e-8f5e-ae8f437632da |  | note | Check Pump Starting devices and record
text | 79b27911-5231-5087-8419-c6a34dd39b9b |  | textbox | Starting pressure (kpa)
text | b8baadaa-7157-5a46-aba8-dcea6a34864c |  | textbox | Run time
text | de360b6a-1776-595c-a4bc-ddfc6300d4f8 |  | textbox | Hour meter
label | 9b66ffd0-d7cc-5c44-bbab-fe0c77f876c3 |  | note | Check and verify pump operation and record in comments
text | 2615ed12-da4b-50e6-b1e5-d4f03e8513c0 |  | textbox | Suction (kPa)
text | b63fb075-37e4-5327-a321-f70f59e8a40d |  | textbox | Discharge (kPa)
text | 834c8776-faa8-5463-9aae-d4c19517a6dd |  | textbox | Charger Voltage (V)
text | 6850525d-ce3e-53cc-8899-15d2fb7aabcb |  | textbox | Oil Pressure (kPa)
text | 1bde550b-476f-5296-acb1-3f9aba5e02de |  | textbox | Engine Temp (C)
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ 0 flow until the pump has run for 30 mins
label | 478a281b-af24-522a-8276-2cbaa2713f52 |  | note | Check Pump Starting devices and record
text | 1e38685b-2c8a-5794-8a79-f3427f133107 |  | textbox | Starting pressure (kpa)
text | 1e4dc600-62bb-5f65-9269-9a362b297c99 |  | textbox | Run time
text | 2ade7502-9cd2-595c-961a-2723f8ec28c3 |  | textbox | Hour meter
label | 693500e3-b3fe-55dc-9f22-caab550e4a78 |  | note | Check and verify pump operation and record in comments
text | e547705d-18c4-595c-91e1-2d7bf2f10918 |  | textbox | Suction (kPa)
text | fc3120bd-ced1-557f-92de-6385f72bddab |  | textbox | Discharge (kPa)
text | d9d84646-57f2-5b3d-8935-d59b722b018b |  | textbox | Charger Voltage (V)
text | 6eba2bd2-9978-5f41-88ff-6aab6b7292b5 |  | textbox | Oil Pressure (kPa)
text | 7e6d3f19-7df8-5c0d-a518-234a3b50f8fe |  | textbox | Engine Temp (C)
label | 8f7d94ef-8a0f-513a-b7dd-4525ff4e5267 |  | note | Basement & Podium
label | dc3ec0d1-1c1c-55e5-9ff2-00e290d452a6 |  | note | Pressure Zone / Level Reference of Test
checklist-sectioned |  |  | checklist | Fire Detection System Commissioning |  |  |  |  | Yes | Fire Detection System Commissioning | b71d410c-b8fc-40ff-9cb7-305c6d43d08d
checkpoint-group |  |  | section | Visual Inspection
checkpoint-status |  |  | checkpoint | Floor inspect to confirm all system works are complete
checkpoint-status |  |  | checkpoint | All faults and isolations cleared for area
checkpoint-status |  |  | checkpoint | Installation of only approved sample equipment
checkpoint-status |  |  | checkpoint | Fit for purpose
checkpoint-status |  |  | checkpoint | Installed to approved drawing
checkpoint-status |  |  | checkpoint | Compliance with AS1670, AS1668, BCA 2015
checkpoint-status |  |  | checkpoint | Joints, Connections and Terminations
checkpoint-status |  |  | checkpoint | Separation of Cables
checkpoint-status |  |  | checkpoint | Fixings and Supports
checkpoint-status |  |  | checkpoint | Position and spacing/obstruction
checkpoint-status |  |  | checkpoint | Signage & Labelling
checkpoint-status |  |  | checkpoint | Block Plans
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Test Thermal and Smoke Detectors in accordance with AS1670, AS1668, BCA
checkpoint-status |  |  | checkpoint | Test Speakers/ Visual in accordance with AS1670, BCA
checkpoint-status |  |  | checkpoint | Test WIP & ECP in accordance with AS1670, BCA
checkpoint-status |  |  | checkpoint | Test Interfaces in accordance with AS1670, AS1668, BCA
checklist-flat |  |  | checklist | Sprinkler System Commissioning |  |  |  |  | Yes | Sprinkler System Commissioning | bb5d7d22-b5d1-494f-b061-d3621930f092
checkpoint-status |  |  | checkpoint | Floor inspect to confirm all system works are complete
checkpoint-status |  |  | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
checkpoint-status |  |  | checkpoint | Escutcheon plates installed
checkpoint-status |  |  | checkpoint | Joints, connections,position & spacing / obstruction correct
checkpoint-status |  |  | checkpoint | Shields/guards provided (where specified)
checkpoint-status |  |  | checkpoint | Fixings and supports in accordance with AS2118
checkpoint-status |  |  | checkpoint | Sprinkler Support Systems are installed to not impede other services installed
checkpoint-status |  |  | checkpoint | Controls and electrical services
checkpoint-status |  |  | checkpoint | Signage & Labelling, Locks & Straps installed, block plans reviewed
checkpoint-status |  |  | checkpoint | Seismic Restraint & paint assessed
checkpoint-status |  |  | checkpoint | Check operation of isolation valve & FIP interface
checkpoint-status |  |  | checkpoint | Inspect and test gauge operation
checkpoint-status |  |  | checkpoint | Check operation of drain for sprinkler system
checkpoint-status |  |  | checkpoint | Check operation of manual test drain confirm FSW activation to FIP
checkpoint-status |  |  | checkpoint | Check operation of solenoid test drain confirm FSW activation to FIP