## Copy of MASTER ITCsQA Checklist
type | name | values | CONQA Notes (Clear once completed and reissused to Apps)
checklist | AE-ITCX-001 - Temp Board Checklist (Rev 0 +Names)
section | Defects
checkpoint | Major Defects (Send back to Aline)
label | Add photos/comments & Send back to Aline
button | Is the switchboard structurally sound | Yes, No
button | Does the main door close | Yes, No
checkpoint | Minor defects (Fix Onsite)
button | Is the main isolating switch identified | Yes, No
button | Are all C.B’s and R.C.D’s identified | Yes, No
button | Is 1.2m clearance signage in place | Yes, No
label | Add Photo below
button | Is ‘Live Parts’ signage in place | Yes, No
label | Add Photo below
section | Electrical
checkpoint | Do pole fillers cover all gaps
checkpoint | Are test points installed in the board
checkpoint | Are all holes in connection (J.Box) filled with screwed stops
checkpoint | Are Perspex covers in place
checkpoint | Do escutcheon plates have all screws fitted
checkpoint | Is insulated lead stand attached and insulation intact
checkpoint | Do the flap-lock and door-lock work
section | Replacement Parts
checkpoint | Replacement parts list - Pass=Required, N/A if not Required
label | Complete this section and order from the office as required. Send report to office Top Right
label | ----Please do not strip other boards for parts.----
checkpoint | Galvanised Style - Pass=Required, N/A if not Required
label | Input quantities required below
text | 10 A DIN mounted GPO
text | 15 A DIN mounted GPO
text | Line taps
text | Hinges
text | Door
text | Door handle and tongue
text | Bottom connection box
text | Bottom connection box cover
text | RCD cover lock 001
text | RCD cover
text | Pole fillers
text | 63 A main switch
text | 100 A main switch
text | 16 A RCBO 2 pole
text | 20 A RCBO 2 pole
text | 32 A 4 pole CB
text | 40 A 4 pole CB
text | Set of legs
text | Set of feet
text | Perspex cover for line tap
text | Lead stand
text | Escutcheon
text | Connectors
text | RCD cover lock 001
checkpoint | New Green Style
label | Input quantities required below
text | Door
text | Hinges
text | Legs
text | Lead stand
text | Escutcheon
text | Rcd cover
text | Rcd cover lock 001
text | Door handle and tongue
text | 32 A 3 phase outlet
text | Connectors
text | 15 A GPO
text | 10 A DGPO
text | 63 A main switch
text | 100 A main switch
text | 40 A 4 pole CB
text | 32 A 4 pole CB
text | 16 A RCBO 1 pole
text | 20 A RCBO 1 pole
section | Sign-Off
checkpoint | Temp Board completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-002 - Monthly RCD Test Sheet (Rev 0 +Names)
section | Details
checkpoint | Details - Pass once entered
text | Test Date
text | Switchboard No.
text | Tag No.
select | Tested by (Appselec) | #NAME?
text | Other (Specify here)
bool | Signature attached below
section | RCD Test 1
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 2
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 3
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 4
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 5
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 6
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 7
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 8
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 9
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 10
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
text | RCD No
text | Nominal Trip Current (mA)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg (ms)
text | 180.Deg (ms)
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
checklist | AE-ITCX-003 - Mandatory Test Results For Construction Wiring (Rev 0 +Names)
section | Electrician Details
checkpoint | Details - Pass once entered
text | Equipment being Energised
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
section | Temporary Board Visual Inspection
checkpoint | All cables secured and protected appropriately
checkpoint | All cables identified with Construction Wiring tape
checkpoint | Switchboard is structurally sound
checkpoint | Appropriate signage in place
checkpoint | All holes filled with stops
section | Temporary lighting visual inspection
checkpoint | All cables secured and protected appropriately
checkpoint | All cables identified with Construction Wiring tape
checkpoint | Appropriate number of emergency lights installed
checkpoint | All lighting plug bases terminated
checkpoint | Light fittings in serviceable condition with wire-guards or plastic diffusers
section | Test Results
checkpoint | Test Results - Pass once complete
text | Insulation Resistance (Mega Ohms)
button | Result | Pass, Fail
label | .. ..
text | Earth Resistance & Continuity (Ohms)
button | Result | Pass, Fail
label | .. ..
text | Polarity
text | Earth loop impedance
button | Result | Pass, Fail
checkpoint | RCD Time trip test completed
checkpoint | Correct circuit connection
checklist | AE-ITCX-004 - Construction Emergency and Exit Lighting to AS 2293 Logbook (Rev 0 +Names)
section | Details
checkpoint | Details - Pass once entered
text | Building/Level
text | Switchboard No.
text | Circuit No
text | Test Date
text | Start Time
text | Finish Time
select | Tested By | #NAME?
text | Other (Specify here)
bool | Signature added below
section | Fitting No.1
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.2
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.3
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.4
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.5
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.6
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.7
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.8
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.9
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
section | Fitting No.10
checkpoint | Fitting Details - Pass once entered
text | Fitting No.
text | Fitting Type
label | Report/Repairs undertaken photograph/comment below
checkpoint | Fitting Condition
checkpoint | Lamp Operation
checkpoint | Operating Time
checklist | AE-ITCX-005 - Construction Wiring 6-Monthly Re-Test Results (Rev 0 +Names)
section | Details
checkpoint | Details - Pass once entered
text | Level
text | DB No.
text | Drawing # & Revision (Or photgraph below)
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
label | .. ..
label | Test Equipment
text | Tester Type
text | Serial No.
text | Callibration Certification Date
section | Test No.1
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.2
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.3
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.4
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.5
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.6
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.7
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.8
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.9
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
section | Test No.10
checkpoint | Test Details - Pass once entered
text | Submain cable No.
text | Cable Size
text | Phase Qty
text | Insulation Resistance - A+N/E
button | Pass/Fail (>1MOhm) | Pass, Fail
label | .. ..
text | Earth Continuity
button | Result | Pass, Fail
label | .. ..
text | Earth Loop Impedance (to furthest point) Result
button | Result | Pass, Fail
checklist-flat | AE-ITCX-006 - Distribution Board Visual Inspection (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Switchboard No.
text | Drawing & Revision #
checkpoint | Appselec typed legend, schematic and labels all in place
checkpoint | Manufacturer's QA check list provided - Attached as applicable
checkpoint | All connections tight with no copper visible out of terminals
checkpoint | Contactors labelled
checkpoint | Wiring neatly loomed (Internally and Externally)
checkpoint | Surge arrestors installed
checkpoint | Cable entries appropriately insulated and fire rated
checkpoint | Bottom entry cables have mechanical protection (if applicable)
checkpoint | Panel, escutcheon, cover plate, door, operable lock and pole fillers in place
checkpoint | Lighting control cabling and emergency cabling labelled
checkpoint | Emergency power sensing installed (if applicable)
checkpoint | Switchboard cupboard cleaned
checkpoint | Distribution Board Visual inspection completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-007 - Conduit Checklist (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
text | Location
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Conduit layout plan prepared
label | Plan addresses minimum distance from other services, as per AS/NZS 3000 Table 3.7 (Minimum Separation of Underground Services
checkpoint | Required cover identified as per AS/NZS 3000 – Table 3.6 (Underground Wiring Systems – Minimum Depth of Cover)
checkpoint | Conduit installation. Check all joints
checkpoint | Accessories installation. Check all joints
checkpoint | Check conduits are securely anchored
checkpoint | Check accessories are securely anchored
checkpoint | Warning tape installed (not required for cast-in concrete conduits) as per AS/NZS 3000 – 3.11.4.5.
checkpoint | Conduits installed as per plan (inspect prior to pour)
label | Photos taken showing all conduits - Attach below
checkpoint | Required cover in place
checkpoint | Conduit locations marked on As built drawing - Attached below as applicable
checkpoint | Conduit works completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by (Builder/QAM)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
text | Position & Purpose of Cable Tray
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Plan & confirm cable tray route
checkpoint | Coordination of other services (Mechanical, Hydraulics Fire)
checkpoint | Correct spacing of brackets
checkpoint | Correct & suitable fixings for brackets
checkpoint | Joins of tray are secure
checkpoint | Tray is securely fixed to brackets
checkpoint | Check all hangers secure?
checkpoint | Check all lock nuts are tight?
checkpoint | Check the tray is level & straight?
checkpoint | Check no sharp edges or protrusions?
checkpoint | Update drawing for as built
checkpoint | Cable Tray works completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by (Builder/QAM)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-009 - Mains Cabling Reticulation Test Sheet (Rev 1 +Names)
section | Details
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
section | Test No.1
checkpoint | Pass Once below details are completed
text | Cable No
text | Cable Origin
text | Cable Destination
text | Upstream Circuit Breaker Size
select | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | Fire Rated | Yes, No
text | Cable Size (mm²)
text | Earth Conductor Size (mm²)
select | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | Other (Specify here)
select | Tie in Method | Nylon, Steel, Cleats
button | Line & Load Side Termination Checked & torque (ITCX-010) | Yes, No
select | Cable Grouping | Trefoil, Flat, Quad
text | Cable Spacing on tray required | Yes - Minimum 1D, Not required
text | Cable Earth Resistance
checkpoint | Insulation Resistance - Pass Once below details are completed
text | Red / White
text | Red / Blue
text | Red / Earth
text | Blue / White
text | Blue / Earth
text | White / Earth
text | White / Neutral
text | Red / Neutral
text | Blue / Neutral
text | Neutral / Earth (MEN Disconnected)
text | Earth Loop Impedance
text | Name
label | Signature added below
checkpoint | Photo
button | Photo of Completed Cable in Chamber | Yes, No
section | Test No.2
checkpoint | Pass Once below details are completed
text | Cable No
text | Cable Origin
text | Cable Destination
text | Upstream Circuit Breaker Size
select | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | Fire Rated | Yes, No
text | Cable Size (mm²)
text | Earth Conductor Size (mm²)
select | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | Other (Specify here)
select | Tie in Method | Nylon, Steel, Cleats
button | Line & Load Side Termination Checked & torque (ITCX-010) | Yes, No
select | Cable Spacing | Trefoil, Flat, Quad
text | Cable Earth Resistance
checkpoint | Insulation Resistance - Pass Once below details are completed
text | Red / White
text | Red / Blue
text | Red / Earth
text | Blue / White
text | Blue / Earth
text | White / Earth
text | White / Neutral
text | Red / Neutral
text | Blue / Neutral
text | Neutral / Earth (MEN Disconnected)
text | Earth Loop Impedance
text | Name
label | Signature added below
checkpoint | Photo
button | Photo of Completed Cable in Chamber | Yes, No
section | Sign-Off
checkpoint | Testing completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by (Builder/QAM)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-010 - Torque Settings for Bolts (Rev 1 +Names)
section | Reference Tables
checkpoint | Torque Setting Tables - Pass once tables are confirmed/read
label | .. ..
label | Lugged Cables
label | M6 - Class 8.8 Zinc plated - 9 Newton Meters
label | M8 - Class 8.8 Zinc plated - 22 Newton Meters
label | M10 - Class 8.8 Zinc plated - 44 Newton Meters
label | M12 - Class 8.8 Zinc plated - 77 Newton Meters
label | M16 - Class 8.8 Zinc plated - 190 Newton Meters
label | .. ..
label | Bus Bars
label | M8 - Class 8.8 Zinc plated - 35 Newton Meters
label | M10 - Class 8.8 Zinc plated - 50 Newton Meters
label | M12 - Class 8.8 Zinc plated - 75 Newton Meters
label | M16 - Class 8.8 Zinc plated - 190 Newton Meters
label | .. ..
label | ALL BOLTS SUPPLIED BY SWITCH BOARD MANUFACTURES, INCLUDING ALINE, ARE GRADE 8.8 BOLTS AND SHOULD NOT BE SUBSTITUTED
label | .. ..
label | Torque Settings for SAGAME IPCs
label | TTD051XFA - 16 to 95 (Conductor Size MM2) - 1.5-10 (Branch Cable MM2) - 9 Newton Meters
label | TTD101XFA - 6 to 54 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 9 Newton Meters
label | TTD151XFA - 25 to 95 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 14 Newton Meters
label | TTD201XFA - 35 to 95 (Conductor Size MM2) - 25 to 95 (Branch Cable MM2) - 18 Newton Meters
label | TTD241XFA - 50 to 150 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 14 Newton Meters
label | TTD251XFA - 50 to 150 (Conductor Size MM2) - 35 to 95 (Branch Cable MM2) - 18 Newton Meters
label | TTD301XFA - 25 to 95 (Conductor Size MM2) - 25 to 95 (Branch Cable MM2) - 14 Newton Meters
label | TTD341F - 50 to 150 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 14 Newton Meters
label | TTD351XFA - 50 to 150 (Conductor Size MM2) - 35 to 95 (Branch Cable MM2) - 18 Newton Meters
label | TTD401XFA - 50 to 185 (Conductor Size MM2) - 50 to 150 (Branch Cable MM2) - 18 Newton Meters
label | TTD431XFA - 70 to 240 (Conductor Size MM2) - 16 to 95 (Branch Cable MM2) - 20 Newton Meters
label | TTD451XFA - 95 to 240 (Conductor Size MM2) - 95 to 240 (Branch Cable MM2) - 25 Newton Meters
label | TTD551FJA - 120 to 380 (Conductor Size MM2) - 95 to 240 (Branch Cable MM2) - 37 Newton Meters
label | INSTALLATION NOTES FOR IPC’S: WHEN USING TWO BOLT CONNECTORS EACH BOLT MUST BE TIGHTENED A1/4 T0 1/2 TURN ALTERNATIVELY UNTIL THE SHEAR HEAD OPERATES
label | .. ..
label | MANUFACTURES CIRCUIT BREAKERS- All tourque seting must follow manufactures recommendations
label
label
section | Test No.1
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.2
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.3
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.4
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.5
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.6
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.7
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.8
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.9
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Test No.10
checkpoint | Pass Once below details are completed
text | Bolt Size
text | Switch/cable Identification
text | Line/Load
text | Red Phase Torqued
text | White Phase Torqued
text | Blue Phase Torqued
text | Neutral Torqued
text | Earth Torqued
text | Bolts Crossed With Black Texta
text | Name
label | Signature added below
section | Sign-Off
checkpoint | Cable Tray works completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by (Builder/QAM)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-011 - Main Switchboard Inspection Sheet (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Switchboard No.
text | Drawing & Revision #
checkpoint | MEN and MSB Meter Panel Checklist (AF019) complete
checkpoint | Main switchboard location and clearances as per AS/NZS 3000
checkpoint | Perform insulation resistance test on main switchboard
checkpoint | Service protection device set and labelled
checkpoint | Consumer mains entry point fire rated
checkpoint | Emergency and exit lighting complete
checkpoint | Access/egress doors installed and labelled
checkpoint | Switchboard room fire rating confirmed
checkpoint | Verification of Switchboard Integrity by Supplier (e.g. Aline Final Inspection & Testing Checklist)
checkpoint | Electrical inspection – Prescribed Works Certificate signed
checkpoint | Power Supply Authority energisation sign off
checkpoint | Main Switchboard works completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-012 - MEN & MSB Meter Panel Checklist (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
text | Switchboard No.
checkpoint | Incoming Service Protection Device
text | A
text | kA
checkpoint | CTs Installed
text | CT Ratio
checkpoint | CT Rated to Suit Supply
checkpoint | CT - Meter Mounted
checkpoint | CT - Metering Loom Installed
checkpoint | Voltage Fuses checked
text | Amps
checkpoint | Isolation Circuit Breaker checked
text | kA
select | Isolation Method | Circuit Breaker, Isolator
checkpoint | Earthing Testing Completed - As per below
text | Main Earth Resistance Test (Substation) - Ohms
text | Earth Resistance
text | Earth Stake
select | MEN Position | Wall Switchboard, Main
button | MEN Size Equal to Neutral | Yes, No
button | MEN Bonded to Switchboard Chassis | Yes, No
checkpoint | Bonding Testing Completed - As per below
text | Cold Water
text | Cable Support Systmes
text | Fire Hydrant
text | Gas Services
checkpoint | Labelling Inspection - DB Labels installed
checkpoint | Labelling Inspection - Cable Labels installed
checkpoint | MEN & MSB works completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
label | .. ..
text | Test Equipment Tester Type
text | Serial No.
text | Calibration Certification Date
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-013 - T-Off Visual Inspection Test (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Switchboard No.
text | Drawing & Revision #
checkpoint | Earthing check
checkpoint | Visual Inspection
checkpoint | All terminations points tight
checkpoint | Labels
checkpoint | Insulation Test
checkpoint | Wiring neatly loomed
checkpoint | Check takeoff box fuse/breaker rating
checkpoint | Energisation procedure
checkpoint | Fire rating of penetrations
checkpoint | Cover plate secure
checkpoint | Switchboard and cupboard cleaned
checkpoint | T-Off Box Visual inspection completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-014 - Meter Panel Visual Inspection Checklist (Rev 0 +Names)
checkpoint | Latest consented drawings checked & referenced
text | Meter Panel Info
text | Drawing & Revision #
checkpoint | Wiring Neatly Loomed
checkpoint | All connection points tight Inc. fuses and panel isolators
checkpoint | All factory fitted connections tight
checkpoint | Panel, cover plate, door, lock and pole filters
checkpoint | Supplier Check List (e.g. Aline) Completed and Attached
checkpoint | Meter panel installed as per Appselec shop drawing
checkpoint | Meter panel and cupboard cleaned
checkpoint | Apartment sub-main relabelled at entry point.
checkpoint | Meter panel face wiped and cleaned
checkpoint | Glands tight
checkpoint | Cables fire sealed where required
checkpoint | Wago Plugs installed, labelling is correct & polarity is correct
checkpoint | Meter Panel Visual inspection completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Installed by (Appselec) | #NAME?
text | Other (Specify here)
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-015 - Mandatory Test Results (Rev 1 +Names) |  | UPDATED 13/09/21 - To be updated in library and projects
checkpoint | Latest consented drawings checked & referenced
text | Meter Panel Info
text | Drawing & Revision #
checkpoint | Details - Pass once entered
select | Type | RCD, RCBO, MCB, MCCB, Fuse, Other (Specify below)
text | Other (Specify here)
select | Type | A, B, C, D, Other (Specify below)
text | Other (Specify here)
select | RCD/RCBO mA | 10mA, 20mA, 100mA, Other (Specify below)
text | Other (Specify here)
select | Rating in (A) | 6A, 10A, 16A, 20A, 25A, 32A, 40A, 50A, 63A, 80A, 100A, 125A, 160A, 200A, 250A, 320A, 400A, 630A, Other (Specify below)
text | Other (Specify here)
select | Cable size (mm2) | 1.5mm, 2.5mm, 4mm, 6mm, 10mm, 16mm, 25mm, 35mm, 50mm, 70mm, 95mm, 120mm, 150mm, 185mm, 240mm, 300mm, 400mm, 630mm
select | Phase Qty | 1 Phase, 3 Phase
checkpoint | Visual Inspection
checkpoint | Earth Continuity
label | Pass/Fail Measurement in OHMS, <0.5 for main earthing conductor, refer to Table 8.2 for final sub circuits
checkpoint | Polarity
checkpoint | Earth loop impedance
label | Pass/ Fail Measured in OHMS to the furthest point Refer to AS3000 table 8.1. N/A for an RCD protected circuit
checkpoint | Correct circuit connections
checkpoint | L1 - N (Measurement) >1MΩ is a Pass
checkpoint | L2 - N (Measurement) >1MΩ is a Pass
checkpoint | L3 - N (Measurement) >1MΩ is a Pass
checkpoint | L1 - E (Measurement) >1MΩ is a Pass
checkpoint | L2 - E (Measurement) >1MΩ is a Pass
checkpoint | L3 - E (Measurement) >1MΩ is a Pass
checkpoint | N - E (Measurement MEN disconnected) >1MΩ is a Pass
checkpoint | L1 - L2 (Measurement) >1MΩ is a Pass
checkpoint | L2 - L3 (Measurement) >1MΩ is a Pass
checkpoint | L1 - L3 (Measurement) >1MΩ is a Pass
checkpoint | RCD Testing
label | Correct function of RCD has been verified by the operation of the integral test device or by the use of special test equipment
checkpoint | Commissioning Completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-017 - RCD Test Sheet (Rev 0 +Names)
section | Details
checkpoint | Details - Pass once entered
text | Test Date
text | Switchboard No.
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
section | RCD Test 1
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 2
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 3
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 4
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 5
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 6
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 7
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 8
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 9
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | RCD Test 10
checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
checklist-flat | AE-ITCX-018 - DB Fit Off Sheet (Rev 0 +Names) |  | UPDATED 13/09/21 - To be updated in library and projects
checkpoint | Latest consented drawings checked & referenced
text | Distribution Board No.
text | Drawing & Revision #
checkpoint | All screw terminations tight
label | With copper not visibly out of terminal
checkpoint | Neutrals correspond with actives
checkpoint | Pole fillers installed
checkpoint | DB door and eschucheon scratch and defect free
checkpoint | Switchboard labelled and cleaned
checkpoint | Cable entry points fire sealed
checkpoint | BMU circuits protected by a 100mA RCD
checkpoint | Correct lighting control equipment installed
checkpoint | Appselec 'installed by' sticker installed
checkpoint | Warning: Interrupting power supply will discharge emergency lighting batteries' installed next to RCBO feeding emergency lighting
checkpoint | Energy Meter been installed with CT metering
checkpoint | Wiring goes through the correct CT,
label | Installed in the correct direction and terminated to the correct phase
checkpoint | Wiring neatly loomed internally and externally of the DB
checkpoint | MANDATORY PHOTO 1 - Accurate DB schedule (Taken and Attached below)
label | Additional photos where required (Example - Lighting control schedule)
checkpoint | DB Fit-Off completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME? | To be updated with employee list
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-020 - MATV Backbone Rough in, Testing & Panel Fit Off (Rev 0 +Names)
section | No.1
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.2
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.3
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.4
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.5
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.6
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.7
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.8
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.9
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | No.10
checkpoint | MATV Backbone Instalaltion completed
text | MATV Backbone Cable Type
text | From MATV Panel
text | To MATV Panel
checkpoint | Tested and Labelled
checkpoint | MATV Panel Installed (Level)
checkpoint | MATV Panel Fit-Off Completed
checkpoint | MATV Panel Labelled
section | Sign-Off
checkpoint | Backbone Works completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
select | Backbone by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by
label | Signature Sign-Offs - Attach signature(s) below
label | .. ..
select | Panel Fit-Off by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by
label | Signature Sign-Offs - Attach signature(s) below
label | .. ..
select | Testing by (Appselec) | #NAME?
text | Other (Specify here)
text | Witnessed by
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-021 - Temp Board Audit Form (Rev 0)
section | Structural
checkpoint | Is insulated lead stand with board and in good condition
checkpoint | Is the insulation on the lead hook in good condition
checkpoint | Is the switchboard structurally sound
checkpoint | Does the main door close properly
checkpoint | Does the main door have the facility to be propped open
checkpoint | Is the chain to prevent the wind catching the door
checkpoint | Is the insulated bar in place
checkpoint | Do the flap-lock and door-lock work
checkpoint | Are all screws holding escutcheon covers in place
section | Signage
checkpoint | Is the main isolating switch identified
checkpoint | Are all C.B’s and R.C.D’s identified
checkpoint | Is 1.2m clearance signage in place
checkpoint | Is ‘Live Parts’ signage in place
checkpoint | Is KEEP CLOSED-RUN LEADS THROUGH BOTTOM sign on the door
checkpoint | Is the ID number of the board clearly visible
section | Electrical
checkpoint | Has all external wiring been removed?(not just cut off)
checkpoint | Do pole fillers cover all gaps
checkpoint | Are test points installed in the board
checkpoint | Is the 15amp GPO’s protected by a 25amp C/B
checkpoint | Are all holes in connection (J.Box) filled in/covered
checklist | AE-ITCX-022 - Emergency & Exit Lighting to AS 2293 Logbook (Rev 0) - TBC W/CONQA
section | Preface
checkpoint | Summary of Information - Pass once confirmed
label | This logbook has been compiled in accordance with the requirements of Australian Standard AS 2293. Persons using/completing this logbook should be familiar with all parts of AS 2293
label | .. ..
label | Summary of Test Procedures as required under AS 2293 Part 2 Section 3. Six (6) monthly inspection and test procedures for Single Point Systems
label | 1. Test procedures should be carried out at intervals not less than 6 months
label | 2. Check to ensure that no interruption has taken place to the power supply of fittings to be tested for at least 16 hours prior to carrying out testing
label | 3. Carry out visual inspection of all fittings prior to conducting testing to ensure that power is connected, tubes are functioning correctly and fittings are free of damage that may otherwise affect the test results
label | 4. Operate the emergency and exit luminaires from their battery supply by simulating failure of the monitored supply. All emergency and exit luminaires shall remain illuminated for a period of not less than 90 minutes or 2 hours for initial test of new fittings
label | 5. Restore all emergency and exit luminaires to normal monitored supply and check battery charge operation is functioning
label | 6. Enter test results into logbook
label | .. ..
label | Summary of Test Procedures as required under AS 2293 Part 2 Section 3. Annual inspection and maintenance procedures for Single Point Systems
label | 1. Carry out all functions listed above as per six (6) monthly
label | 2. Clean all light emitting and reflective surfaces of emergency and exit luminaires as required
label | For further information regarding the testing of emergency and exit lighting, please refer to AS 2293-2
section | Emergency Light Fitting Legend
checkpoint | No.1 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.2 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.3 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.4 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.5 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.6 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.7 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.8 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.9 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
checkpoint | No.10 - Details Completed and Entered below
text | Legend
text | Manufacturer
text | Cat Number
text | Descriptin
text | Lamp
text | Battery
section | Fittings
checkpoint | Fittings Details - Pass once entered
text | Fitting Number
text | Fitting Type
text | Controlled from Switchboard
text | C/B Number
checkpoint | Fitting No.1 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.2 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.3 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.4 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.5 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.6 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.7 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.8 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.9 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checkpoint | Fitting No.10 - Pass once completed
button | Fitting Condition | Pass, Fail
button | Lamp Operation | Pass, Fail
bool | Clean Fitting
label | .. ..
label | Operating Time
text | Time
text | P/F
label | Any repairs photographed/commented on below
label | Attach Signature Sign-off below once completed
checklist | AE-ITCX-024 - Communications/Security Rack Installation QA (Rev 0)
section | QA ITEM 1 - Communications Rack
checkpoint | Is the communications riser ready for communications rack installation
label | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint | Does the communications rack match the approved technical data
checkpoint | Has the communications rack been installed in position as per the Appselec communications riser elevation shop drawings and floor plan layout
text | Drawing & Revision #
checkpoint | Has the communications rack been fixed to the floor using appropriate fixings
checkpoint | Are the doors and side panels installed and free from damage
checkpoint | Does the communications rack comply with all the relevant clearances
label | Are door swings and access to the communications rack unobstructed
checkpoint | Has the communications rack been permanently labelled with a traffolyte label or similar on the door
label | Check that the label matches the communications rack layouts
checkpoint | Has the Appselec label/logo been fixed to the front of the communications rack
section | QA ITEM 2 - Communications Earthing Terminal (CET)
checkpoint | Has a CET been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth cable been terminated to the CET
label | Refer to Communications SLD for earth cabling schematic
checkpoint | Has an earth bar been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth been terminated to the earth bar from the CET
checkpoint | Has the 6 mm2 green/yellow earth been identified and labelled with “Communications Earth” at the originating electrical distribution board
section | QA ITEM 3 - FOBOTS (Fibre Optical Breakout Trays)
checkpoint | Does the FOBOT match the approved technical data
checkpoint | Has the FOBOT been installed in the correct rack RU position as per the communications rack layout
checkpoint | Has the FOBOT been labelled permanently with traffolyte label or similar
checkpoint | Has a service loop been provided in the optical fibre cable
checkpoint | Has the fibre port arrangement on the FOBOT been detailed and labelled
checkpoint | Do the fibre adapters on the FOBOT match the type of fibre being used
label | For example: aqua = multimode, green = singlemode. Adapters, pigtail connector colours must match, fibre cable type must match
checkpoint | Have fibre protective caps been installed on all fibre adapter ports
section | QA ITEM 4 - Cat 6/6A Patch Panels
checkpoint | Does the Cat 6/6A patch panels match the approved technical data
checkpoint | Have the Cat 6/6A patch panels been installed in correct rack RU position as per the communications rack layout
checkpoint | Have the Cat 6/6A patch panel ports been labelled permanently with traffolyte label or similar
checkpoint | Have cable wrap-around labels been attached to each individual Cat 6/6A cable behind the patch panels
checkpoint | Have the Cat 6/6A patch panels been earthed with 2.5 mm2 green/yellow earth cable from the earth bar within the communications rack
label | Shielded patch panels only
section | QA ITEM 5 - Cable Management
checkpoint | Have horizontal cable managers been installed in the correct rack RU position as per the communications rack layout
checkpoint | Have vertical cable managers been installed in the correct rack RU position as per the communications rack layout
section | QA ITEM 6 - Power
checkpoint | Has the correct power been provided for the communications racks
label | Check for captive outlets? Are there 2x or 1x? Are they 10A, 15A or 20A? Check the Appselec power floor layouts against the communications specification
checkpoint | Do the PDU’s match the approved technical data
checkpoint | Have the PDU’s been installed in position as per the communications rack layout
checkpoint | Have the PDU’s been plugged into the captive outlets/rack mounted UPS as detailed on the communications rack layouts
checkpoint | Have the PDU’s been labelled appropriately detailing the power source
label | For example UPS supply (Generator backed) DB-XX
section | QA ITEM 7 - Rackmount UPS
checkpoint | Is the communications rack/riser ready for UPS installation
label | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint | Does the UPS match the approved technical data
checkpoint | Has the UPS been installed in position as per the communications rack layouts
checkpoint | Has the UPS been labelled appropriately detailing the power source
label | For example UPS supply (Generator backed) DB-XX
checkpoint | Has any associated Battery Backup for the UPS been installed as per the communications rack layouts and is it connected
checkpoint | Has the UPS been commissioned? Refer to UPS ITP for commissioning details
section | QA ITEM 8 - Active Equipment
checkpoint | Is the communications rack/riser ready for Active Equipment installation
label | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint | Does the Active Equipment need to be configured prior to installation within the communications rack
checkpoint | Does the Active Equipment match the approved technical data
checkpoint | Has the Active Equipment been installed in the correct rack RU position as per the communications rack layouts
checkpoint | Do you have a network diagram detailing the connection and labelling of all Active Equipment
checkpoint | Has the Active Equipment been labelled appropriately as per the vendor requirements
label | All switches are to be labelled with the correct vendor labelling convention
checkpoint | Have SFPs been provided and installed
label | Check that they are the correct SFP for the optical fibre cable installed. Check they are installed into the correct port. (SFP is a small form-factor pluggable transceiver)
checkpoint | Have stacker cables been provided to stack switches together Are they connected as per the integrator/vendor requirements
label | Are they connected as per the integrator/vendor requirements
checkpoint | Have the switches been connected to the PDUs
label | Check if switches require one supply or two supplies (dual power redundancy). Check if switches require UPS supply/UPS + generator supply
section | QA ITEM 9 - Patching
checkpoint | Do you have the correct length, colour, type (Cat6/6A) and quantity of patch leads
checkpoint | Do you have a patching schedule detailing which switch port patches to which patch panel port
checkpoint | Do you have the appropriate cable management capacity installed to patch cables as per the patching schedule
section | QA ITEM 10 - Photos
checkpoint | Photos must be taken of each communications rack when completed
label | Attach photos below as applicable
bool | Photo 1: Front of rack, door closed
bool | Photo 2: Front of rack, door open
bool | Photo 3: Front of rack, door closed
bool | Photo 4: Rear of rack, doors open
bool | Photo 5: Any other relevant photos
checklist | AE-ITCX-025 AS:3003 - Appendix E Body Protected CL (Rev 0 +Names)
section | Preface
checkpoint | Appendix E: Summary of Information - Pass once confirmed
label | Routine inspection checklist for Body-Protected electrical areas
label | .. ..
label | This checklist shall beused in accordance with Clause 8.2.7
label | Note: The checklist may be in a different format and may be recorded electronically
section | Inspection & labelling
checkpoint | 8.2.1.1: Inspection - All electrical equipment and fittings in good condition
checkpoint | 8.2.1.2: Labelling - Circuit identification visible and intact on each
checkpoint | 8.2.1.2: Labelling - Protected points labelled as to which RCD protects them
checkpoint | 8.2.1.2: Labelling - Circuit identification visible and intact on each LIM
checkpoint | 8.2.1.2: Labelling - Overload monitors labelled with alarm setting
checkpoint | 8.2.1.2: Labelling - Socket-outlets protected by RCD labelled 'RCD PROTECTED'
checkpoint | 8.2.1.2: Labelling - Socket-outlets protected by isolating transformers labelled 'ISOLATING TRANSFORMER PROTECTED'
checkpoint | 8.2.1.2: Labelling - Socket-outlets intended for cleaning purposes labelled 'CLEANING PURPOES ONLY'
checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Still Visible
checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Labelled with current inspection date
checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Labelled with identity of authorised person
checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Labelled with next test date
section | Socket-Outlets
checkpoint | 8.2.1.3.1: Socket-outlets coloured according to type of supply
checkpoint | 8.2.1.3.2: If RCD protected, power-available indicator operational
checkpoint | 8.2.1.3.2: Number of socket-outlets and permanently wired electrical equipment protected by RCD does not exceed 12
checkpoint | 8.2.1.3.2: On/Off luminous indicators operational, if applicable
checkpoint | 8.2.1.3.2: Socket-outlets double-poled if protected by a transformer-isolated supply
checkpoint | 8.2.1.3.2: All socket-outlets below 2.3m protected by LPD
checkpoint | 8.2.1.3.2: Confirm that when a fault is applied to each socket-outlet within patient area or within 2.0m of entrance of the patient area, the RCD trips
checkpoint | 8.2.1.3.2: Confirm that when a fault is applied to each socket-outlet within patient area or within 2.0m of entrance of the patient area causes a response on LIM
section | 8.2.2: Earthing
checkpoint | Confirm that the earth pins of all socket-outlets below 2.3m are earthed to less than 1.0-Ohm
checkpoint | Confirm that the earth pins of all socket-outlets within 2.0m of entrance to patient area are earthed to less than 1.0-Ohm
checkpoint | Confirm that all socket-outlets used by medical electrical equipment accessible above 2.3m are earthed to less than 1.0-Ohm
checkpoint | Confirm that all permanently wired electrical equipment with conductive parts below 2.3m are earthed to less than 1.0-Ohm
section | RCD
checkpoint | 8.2.3.2: RCD Sensitivity for Australia - Confirm that the RCD trips between 4.5-10.5 mA
text | Record the RCD sensitivity (may)
checkpoint | 8.2.3.3: RCD Tripping times for Australia - Confirm this by carrying out at least two such tests
text | Record the worst case (ms)
checkpoint | 8.2.3.5: RCD Supply available indicator lights - If applicable, confirm that they are operational
checkpoint | 8.2.3.6: Audiovisual RCD Trip Indicators - If applicable, confirm that they are operational
section | 8.2.4.1: Prospective Hazard current
checkpoint | Confirm that the hazard current is below 2.00mA
text | Record hazard current (may)
label | For routine testing, the PHC under normal conditions of operation shall be verified by applying the following process to each transformer Line Isolation Overload Monitor (LIOM)
checkpoint | All electrical equipment are disconnected from the supply
checkpoint | The current flowing through a low impedance ammeter connected between one isolated supply conductor and earth is noted
label | The test is repeated for the other isolated supply conductor. The larger of the noted values is the prospective hazard current. It shall be less than 2mA
checkpoint | The prospective hazard current of the supply is recorded in the commissioning checklist
section | 8.2.5: Overload Monitors
checkpoint | Confirm that a load of 110-120% of transformer rated current causes the alarm to activate in 3-5 Seconds
section | 8.2.6: Uninterruptible Power Supplies (UPS)
checkpoint | Confirm that UPS status indicator performance is routinely verified
section | Sign-Off
checkpoint | Checks completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-026 AS:3003- Appendix F Cardiac Protected CL (Rev 0 +Names)
section | Preface
checkpoint | Appendix F: Summary of Information - Pass once confirmed
label | Routine inspection checklist for Cardiac-Protected electrical areas
label | .. ..
label | This checklist shall beused in accordance with Clause 8.3.7
label | Note: The checklist may be in a different format and may be recorded electronically
section | Inspection & labelling
checkpoint | 8.3.1.1: Inspection - All electrical equipment and fittings in good condition
checkpoint | 8.3.1.2: Labelling - Circuit identification visible and intact on each
checkpoint | 8.3.1.2: Labelling - Relevant electrical points labelled to identify associated RCDs
checkpoint | 8.3.1.2: Labelling - Circuit identification visible and intact on each LIM
checkpoint | 8.3.1.2: Labelling - Relevant electrical points labelled to identify associated LIMs
checkpoint | 8.3.1.2: Labelling - Overload monitors labelled with alarm setting
checkpoint | 8.3.1.2: Labelling - Socket-outlets protected by RCD labelled 'RCD PROTECTED'
checkpoint | 8.3.1.2: Labelling - Socket-outlets protected by isolating transformers labelled 'ISOLATING TRANSFORMER PROTECTED'
checkpoint | 8.3.1.2: Labelling - Socket-outlets intended for cleaning purposes labelled 'CLEANING PURPOES ONLY'
checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Visible
checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Labelled with current inspection date
checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Labelled with identity of authorised person
checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Labelled with next test date
section | 8.3.1.3: Socket-Outlets
checkpoint | Socket-outlets coloured according to type of supply
checkpoint | If RCD protected, power-available indicator operational
checkpoint | Number of socket-outlets and permanently wired electrical equipment protected by RCD does not exceed 12
checkpoint | On indicator light operational, if present
checkpoint | Socket-outlets double-poled if protected by a transformer-isolated supply
checkpoint | All socket-outlets used for medical electrical equipment or installed below 2.3m protected by LPD
checkpoint | Confirm that when a fault is applied to each socket-outlet within patient area or within 5.0m of entrance of the patient area, the RCD trips
checkpoint | Confirm that when a fault is applied to each socket-outlet within patient area or within 5.0m of entrance of the patient area causes a response on LIM
checkpoint | Confirm that RCDs do not protect socket-outlets in another patient location
section | 8.3.2: Earthing
checkpoint | Confirm that the earth pins of all socket-outlets below 2.3m are earthed to less than 1.0-Ohm with respect to EP junction or node or other electrical equipment
checkpoint | Confirm that the earth pins of all socket-outlets within 5.0m of entrance to patient area are earthed to less than 1.0-Ohm with respect to EP junction or node or other electrical equipment
checkpoint | Confirm that all permanently wired electrical equipment with conductive parts below 2.3m are earthed to less than 1.0-Ohm with respect to EP junction or node or other electrical equipment
section | RCD
checkpoint | 8.3.3.2: RCD Sensitivity for Australia - Confirm that the RCD trips between 4.5-10.5 mA
checkpoint | 8.3.3.3: RCD Tripping times for Australia - Confirm this by carrying out at least two such tests
text | Record the longest tripping time (ms)
checkpoint | 8.3.3.5: RCD Supply available indicators - Confirm that they are operational
checkpoint | 8.3.3.6: Audiovisual RCD Trip Indicators - If applicable, confirm that they are operational
section | 8.3.4.1: Prospective Hazard current
checkpoint | Ensure PHC is less than 2.00mA when no electrical equipment is plugged in
label | For routine testing, the PHC under normal conditions of operation shall be verified by applying the following process to each transformer Line Isolation Overload Monitor (LIOM)
checkpoint | All electrical equipment are disconnected from the supply
checkpoint | The current flowing through a low impedance ammeter connected between one isolated supply conductor and earth is noted
label | The test is repeated for the other isolated supply conductor. The larger of the noted values is the prospective hazard current. It shall be less than 2mA
checkpoint | The prospective hazard current of the supply is recorded in the commissioning checklist
section | 8.3.4.2: LIM Prospective Hazard Current Alarm
checkpoint | Confirm that the LIM alarms between 4.5-10.5mA
text | Record alarm current (mA)
section | 8.3.5: Overload Monitors
checkpoint | Confirm that a load of 110-120% of transformer rated current causes the alarm to activate in 3-5 Seconds
section | 8.3.6: Uninterruptible Power Supplies (UPS)
checkpoint | Confirm that UPS status indicator performance is routinely verified
section | Sign-Off
checkpoint | Checks completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Checked by (Appselec) | #NAME?
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-027 AS:3003-Table B1 Patient Area CL (Rev 0)
section | Preface
checkpoint | Appendix B: Summary of Information - Pass once confirmed
label | Commissioning Inspection Checklist
label | .. ..
label | B1: General
label | This Appendix sets out a checklist for electrical area installations in accordance with this standard
label | All body-protected and cardiac-protected electrical areas shall be in accordance with this Standard by the use of a commissioning checklist
label | The commissioning results may be recorded electronically, on paper, or other similar medium. The commissioning checklist shall be retained by the person conducting the tests and a copy provided to the responsible organisation/entity. NOTE:This checklist can also be used for special patient areas as specified in Section 5
label
label | .. ..
label | B2: Commissioning Inspection Checklist for Patient Areas
label | A checklist shall be developed to record the results for each patient area commissioned, in accordance with each of the required clauses of this Standard
label | The checklist shall be in English, and shall clearly record the result for each item. NOTE: Checked boxes with a 'Pass' or 'Fail' or 'N/A' would satisfy this requirement
label | .. ..
label | B3: Commissioning Checklist
label | The information in Table B1 shall be included in the commissioning checklist and have a result recorded against each item
section | 2.1: General Requirements for Body-Protected and Cardiac-Protected Electrical Areas
checkpoint | 2.1 - All locations that form part of the current works and which it is intended that low-voltage medical electrical equipment will be used in contact with patients and can be operated while connected to the electrical supply mains (except in emergencies) are checked to confirm that they are signposted as bidy-protected or cardiac-protected electrical areas
label | Where there is doubt about the intended use of a particular location, formal clarification should be sought from the responsible organisation
label | If an area is not required to be wired as a patient area a letter stating that mains operated medical electrical equipment will not be used within that area should be provided by the responsible organisation
checkpoint | 2.1 - Cardiac-protected and body-protected electrical areas not in the same room
section | Classification of Patient Areas
checkpoint | 2.2.3 - Only those specified areas are wired as cardiac-protected
checkpoint | If others nominated, then confirm documentation outlining specific requirements is provided by responsible organisation
checkpoint | 2.2.4 - Patient areas not wired as cardiac-protected electrical areas are wires as body-protected electrical areas
checkpoint | All patient ensuites, bathrooms, shower rooms and toilets wired a body-protected electrical areas
section | Low-Voltage A.C. Supplies
checkpoint | 2.4.1.1 - Confirm that electrical final sub-circuits are unique to respective rooms in body-protected electrical areas
checkpoint | Ensuite in adjoining room may share final sub-circuit
checkpoint | Confirm that cleaning outlets are on a separate electrical sub-circuit to other socket-outlets in the room
checkpoint | 2.4.1.2 - Confirm that electrical final sub-circuits are unique to respective rooms in cardiac-protected electrical areas
checkpoint | 2.4.1.3 - Final sub-circuit for socket-outlets identified 'CLEANING PURPOSES ONLY' supplies no other socket-outlets
checkpoint | 2.4.2 - Confirm conformance with AS/NZS:3000 for protection against mechanical damage
checkpoint | 2.4.3.2.1 - Confirm by inspection and testing that al socket-outlets specified are protected by LPD (except those exempted)
checkpoint | 2.4.3.2.2(a) - Socket-outlets that are accessible in patient areas without using a key or tool
checkpoint | 2.4.3.2.2(b) - Excludes multi-phase outlets conforming with AS/NZS:3123
label | Socket-outlets conforming with AS/NZS:3112 that are located within 2.0m of the entrance to a body-protected electrical area and are accessible without the use of a key or tool in any room, corridor, etc., opening directly off a patient area
checkpoint | Socket-outlets conforming with AS/NZS:3112 that are located within 5.0m of the entrance to a cardiac-protected patient area and are accessible without the use of a kay or tool in any room, corridor, etc., opening directly off a patient area
checkpoint | 2.4.3.2.2(c) - Socket-outlet(s) installed outside the patient area but used to supply medical electrical equipment used within the patient area
checkpoint | 2.4.3.2.3 - LPD protection not required for permanently installed pendant-type sockets that will not accept common 10 or 15A plugs conforming to AS/NZS:3112
checkpoint | LPD protection required for socket-outlets that are mounted on, and form part of, a permanently installed medical system provided that such socket-outlets are clearly intended to power specified component parts of the medical electrical system
checkpoint | LPD protection not required for socket-outlets specifically intended for clocks
checkpoint | 2.4.3.2.2(a) - LPD protection not required for socket-outlets that are mounted on the ceiling or above 2.3m on the wall, and are clearly intended for permanently mounted plug-in equipment other than medical electrical equipment
checkpoint | 2.4.3.3 - LPD protection provided for permanently wired medical electrical equipment with Type B applied parts, consisting
bool | Electrodes or transducers that contact patients
bool | Parts that enter patients
bool | Parts that contact liquid in patients
button | Other permanently wired electrical equipment is protected as required by AS/NZS:3000 | Pass, Fail, N/A
checkpoint | 2.4.4.1 - Where the switchboard from which the UPS is to be supplied contains an essential supply of sufficient capacity the UPS is connected to that essential supply
checkpoint | 2.4.4.2 - Where the output circuit of the UPS is earth-free in every mode of operation, the UPS is treated as an isolation transformer and provided with a LIM
checkpoint | Where one output terminal of the UPS is connected to the neutral input terminal earthed within the UPS, the output is protected by RCD or isolated supply
checkpoint | 2.4.4.3 - A suitably located UPS status indicator is provided where socket-outlets or permanently wired equipment are connected to a UPS and there is continuous patient observation
checkpoint | Confirm that the alarm/indicator operates as intended
section | Low-voltage D.C. Supplies
checkpoint | 2.5 - Reticulated low-voltage D.C. - Confirm that they are earth-free and measure current
text | Current
section | Access to Controls & Indicators
checkpoint | 2.6 - Confirm that Controls & Indicators are readily accessible
checkpoint | Confirm that Controls & Indicators, depending on the location of socket-outlets or permanently connected equipment requiring LPD protection, located in accordance with Table 2.1
checkpoint | Confirm that Controls & Indicators, Not mounted under benches, within cupboards or cabinets, or behind bulky equipment in such manner as to inhibit easy access to the controls and indicators
checkpoint | Confirm that Controls & Indicators, if mounted ne the entrance of a room, separated by at least 500mm from any wall-mounted light switch
checkpoint | The above checked requirements do not apply to RCDs protecting socket-outlets that are identified 'CLEANING PURPOSES ONLY' in accordance with Clause 2.7.3 or RCDs mounted in ensuite vanities
section | Socket-Outlets
checkpoint | 2.7.2 - Socket-outlets that are not readily accessible and are not protected by a dedicated LPD are provided with a separate readily accessible isolating double-pole switch
checkpoint | 2.7.3.1 - In body-protected electrical areas, confirm socket-outlet identified 'CLEANING PURPOSES ONLY' within 15.0m of any point in the patient area
checkpoint | In cardiac-protected electrical areas, confirm socket-outlet identified 'CLEANING PURPOSES ONLY' within the patient area
checkpoint | 2.7.3.2 - Socket-outlets that are identified 'CLEANING PURPOSES ONLY' are protected by LPDs that do not protect any other type of socket-outlet
checkpoint | 2.7.4 - Correct labelling is used
checkpoint | 2.7.4.1 - Socket-outlets protected by LPD are labelled 'From RCDX' or 'From LIMX', depending on whether the LPD is an RCD or isolated supply
checkpoint | 2.7.4.2 - Confirm 'ON' indication of socket-outlet switch
checkpoint | 2.7.4.3 - Confirm socket-outlets connected to a normal (mains) supply are colour-coded white
checkpoint | Confirm socket-outlets connected to an essential supply are colour-coded red
checkpoint | Confirm socket-outlets connected to an uninterruptible supply are colour-coded dark blue
checkpoint | Confirm socket-outlets identified 'CLEANING PURPOSES ONLY' are colour-coded beige
checkpoint | 2.7.4.4 - Confirm indicator colour and operation
checkpoint | 2.7.5 - Confirm each socket-outlet is individually switched
checkpoint | Confirm if socket-outlet supplied from isolated supply then it is double poled
section | Residual Current Devices (RCDs)
checkpoint | 2.8.1 - Confirm Type1 RCDs in use
checkpoint | Confirm RCD sensitivity using tests in this Standard (and record results)
text | RCD result
checkpoint | Confirm RCD maximum tripping time using tests in this Standard (and record results)
text | RCD result
checkpoint | Check cClauses 8.2.3.2 and 8.2.3.3 for body-protected areas or Clauses 8.3.4.2 and 8.3.4.3 for cardiac-protected areas
checkpoint | 2.8.2 - Confirm by inspection and testing that there are no RCDs protecting other RCDs
checkpoint | 2.8.1 - Confirm by testing that all RCDs are double poled
checkpoint | 2.8.3 - Confirm that RCDs that are used as LPDs do not protect the supply to the below
bool | More than 12 electrical points, i.e. socket-outlets, items of permanently-wired equipment or combinations thereof
bool | Socket-outlets in different rooms
bool | Socket-outlets in a a patient area and socket-outlets in an area that is not a patient area except, if applicable, for socket-outlets mounted in the ceiling space of a patient area in accordance with Clause 2.4.3.2(iii)
checkpoint | 2.8.4 - Confirm indicator colour and operation of power available indicator of RCDs used as LPDs
checkpoint | 2.8.5 - Confirm by inspection that each RCD is labelled to identify distribution board and circuit breaker, and with unique identifier, e.g. RCD X
checkpoint | 2.8.7 - Confirm that separate test facility is provided for RCD used as LPD when connected to permanently wired equipment
section | Low Voltage Isolated Supplies
checkpoint | 2.9.1 - Confirm isolation transformer LIM and overload monitor are correctly labelled that they conform with AS/NZS:4510
label | 2.9.2 - Confirm by examining the location, housing and ventilation of the isolation transformer
checkpoint | In cardiac-protected electrical areas, confirm that isolation transformer only supplies one patient location
label | 2.9.3 - See to Clause 2.9.3
checkpoint | 2.9.4 - Confirm overload monitor by inspection and testing using tests in this Standard (and record results)
text | RCD result
checkpoint | 2.9.5 - Confirm LIM prospective hazard current display and current alarm using tests in this Standard (and record results)
text | RCD result
checkpoint | Confirm by inspection that labelling is consistent and identifies circuit and LIM
label | See to Clause 2.9.3
checkpoint | 2.9.6 - Confirm prospective hazard current of each transformer-isolated supply does not exceed 2mA
checkpoint | For commissioning, the PHC under normal conditions of operation shall be confirmed by applying the following process to each transformer Line Isolation Overload Monitor (LIOM)
bool | All electrical equipment are disconnected from the supply
bool | The current flowing through a low impedance ammeter connected between one isolated supply conductor and earth is noted. The test is repeated for the other isolated supply conductor. The larger of the noted values is the prospective hazard current. It shall be less than 2mA
bool | The prospective hazard current of the supply is recorded in the commissioning checklist
checkpoint | 2.9.7 - In body-protected electrical areas, confirm that the number of socket-outlets protected by isolated supply does not exceed 12
checkpoint | In cardiac-protected electrical areas, confirm that the number of socket-outlets protected by isolated supply does not exceed 12
checkpoint | 2.9.8 - Confirm that a test facility is provided if permanently wired equipment is protected by an individual isolated supply
section | Isolation Switches
checkpoint | 2.10 - Confirm that a separate individual readily accessible switch(s) has been provided for the below
bool | For conductors that supply an inaccessible socket-outlet that is protected by an LPD
bool | To permanently wired electronical equipment that is connected to an LPD that also protects socket-outlets
checkpoint | Confirm correct labelling of the switch
section | Identification
checkpoint | 2.12.1 - Confirm labelling is of the correct format and size and placed in correct location
checkpoint | 2.12.2 - Confirm patient area signage installed in correct location and appropriate labels attached and signed
section | Testing & Verification of Electrical Work
checkpoint | 2.13 - To confirm that requirements of this Standard have been met, after completion, but before being placed in service, the installation shall be as per below
bool | Inspected as far as is practicable
bool | Tested and confirmed in accordance with Appendix B of this Standard and AS/NZS:3000
section | Additional Documentation
checkpoint | 2.14 - Confirm commissioning checklist in accordance with Appendix B
checkpoint | 3.2 - Additional requirements for body-protected electrical areas - Earthing
label | Confirm conformance with AS/NZS:3000
checkpoint | 4.2 - Additional requirements for cardiac-protected electrical areas - Earth-Free ELV
label | Confirm that no more than 10mA can flow to earth
checkpoint | 4.3 - Disposition of electrical points controlled by LPDs
label | Confirm by tripping all RCDs in a particular patient location, to confirm that socket-outlets in any other patient location(s) are not protected
section | Earthing & Equipotential Bonding
checkpoint | 4.4.1 - Confirm earthing ha sbeen carried out in accordance with the requirements of this Clause and the requirements of AS/NZS:3000
checkpoint | The minimum size of any protective earthing system conductor shall be not less than that required by AS?NZS:3000
checkpoint | The minimum size of any EP bonding system conductor associated with the fixed wiring installed on site shall be 4mm2
checkpoint | 4.4.2.3 - Confirm by inspection that only one EP junction is in use
checkpoint | 4.4.2.4.1 - Confirm by inspection and testing that the resistance of the earthing conductor between each socket-outlet and EP junction or node is <=0.1 Ohm For the below
bool | Socket-outlets within cardiac-protected electrical area
bool | Socket-outlets within specified distance of entrance to cardiac-protected electrical area
bool | Socket-outlets in another room/ceilings for medical electrical equipment with conductive parts accessible within cardiac-protected electrical area
checkpoint | Confirm protective earthing conductors are insulated and segregated from other conductive items
checkpoint | Confirm the below by inspecting and testing
bool | Each node is individually connected to the EP junction by insulated conductors with a maximum resistance of 0.01 Ohms
bool | Each node is accessible and its location identified by labelling
bool | Each node is fully insulated or isolated from contact with structural metal
bool | Each node is numbered and identified to identify the location of the EP junction
bool | 4.4.1 - Confirm earthing has been carried out in accordance with the requirements of this Clause and the requirements of AS/NZS:3000
bool | The EP junction is identified to identify the number of nodes connected
checkpoint | 4.4.2.4.1 - Confirm inspection and testing that the following socket-outlets conforming to Clause4.4.2.4.1 are connected to an EP junction or node
checkpoint | All socket-outlets that are accessible anywhere in the cardiac-protected electrical area without using a key or a tool, including those that are mounted on permanently installed electrical equipment and are available for general use
checkpoint | All socket-outlets that conform with AS/NZS:3112 or AS/NZS:60884.1, or both, and are located within 5.0m of the entrance to the cardiac-protected electrical area and accessible without the use of a key or tool in any room, corridor, etc,., opening directly off the cardiac-protected electrical area
checkpoint | Confirm that these outlets are only connected by one EP earthing system
checkpoint | Socket-outlets that are installed outside cardiac-protected electrical area but are used to supply medical electrical equipment
checkpoint | 4.4.2.4.1 - Confirm earthing in accordance with AS/NZS:3000
bool | Permanently installed cord extension sockets that are part of a medical electrical equipment system and will not accept common 10A plugs
bool | Earth pin of socket-outlets for clocks
checkpoint | 4.4.2.4.2 - Confirm that the protective earthing conductors used to connect socket-outlets to the EP junction or node is insulated and segregated from contacting other conductive items except at the EP junction
checkpoint | Check the resistance between the earth pin of the socket-outlet and the EP junction or node is <+0.1 Ohms using a four-wire milliohm measuring device
checkpoint | 4.4.2.5 - Confirm by inspection and measurement that the following (if within patient environment) are directly earthed to the EP junction or node with a resistance of <+0.1 Ohms:
bool | The protective earthing terminal of permanently installed Class1 electrical equipment that is accessible within patient environment
bool | Metal enclosure containing socket-outlets
checkpoint | 4.4.2.6 - Confirm by inspection and measurement that the following (if within patient environment) and measure <1 Mega Ohm with respect to the EP junction or node are directly earthed to the EP junction or node with a resistance of <=0.1 Ohms
checkpoint | Medical gas outlets and water taps contact reticulated metal services such as medical gas, water or drainpipes, the reticulated metal services etc
checkpoint | Accessible fittings such as hinged window frames or lift-out air-conditioning registers, etc
checkpoint | 4.4.2.7 - Confirm inspection (except for EP junctions) that all joints are as per below
bool | Fully insulated or isolated from contact with structural metal
bool | Effected so that conductors forming part of the equipotential earthing systems are not joined in tunnel connectors in which a single screw bears directly on the conductors
checkpoint | 4.4.2.8 - Confirm where EP junction is readily accessible within the cardiac area it is identified
bool | EP Test Point
bool | 0.1 Ohm Ep Earthing System
bool | EP Junction
checkpoint | 4.4.2.9 - Confirm where the EP junction is not readily accessible in the cardiac-protected electrical area, a test facility is provided as per below
bool | Isolated from structural steel
bool | Identified 'EP Test Point'
bool | Identified '0.1 Ohms EP Earthing System'
bool | Indicates the location of the EP junction
checkpoint | 4.4.2.10 - Confirm that the EP test terminal between EP junction or node has resistance of <+0.01 Ohms
checkpoint | Confirm that the EP test terminal is not used for any other purpose
checkpoint | Confirm that the EP test terminal has separate individual return earths
checkpoint | 4.4.3 - Confirm return to earth distribution board supplying the cardiac-protected electrical area
checkpoint | Confirm each return earth is labelled correctly at the EP junction and the distribution board
checkpoint | Confirm each EP junction has separate individual return earths
section | Alterations & Repairs to Electrical Installations in Patient Areas
checkpoint | 6.2.1 - Confirm that every alteration of the electrical installation in an existing patient area conforms with all relevant provisions of the Standard
checkpoint | 6.2.3 - Confirm inspection within the last 12 months before carrying out any alterations
checkpoint | Confirm in-service sticker is current
checkpoint | 6.2.4 - Check % increase in socket-outlets. If 10% or more increase, then verify all socket-outlets in patient area conform with colour requirements
checkpoint | 6.2.5.1 - Confirm EP wiring system as per below
bool | EP junction accessible
bool | EP test point labelled
checkpoint | Confirm the rating of the new fixed electrical equipment
checkpoint | 6.2.5.2 - Conformance is checked by confirming or actioning Items (a) to (c) of Clause 6.2.5.1
checkpoint | 6.2.5.3 - For the reclassification of a cardiac-protected electrical area to a body-protected electrical area, verify the below
bool | Conformance with Sections 2 & 3, except that, the requirement of Clause 2.4.1.3 for a claner's outlet to have a dedicated circuit need not apply
bool | All EP studs or EP receptacles removed
bool | Re-certification as a body-protected electrical area in accordance with Clause 2.13
bool | Identification in accordance with Clause 2.12
section | Repairs
checkpoint | 6.3.1 - If the patient ares is not sign posted as a cardiac-protected electrical area or a body-protected electrical area, the repairs may only be completed when the patient area meets the requirements of this Standard
checkpoint | 6.3.2 - Confirm that the repair is only an equivalent fitting replacement and not the replacement for the fixed electrical equipment
section | 7.1, 7.2. 7.3 - Identification of Patient Areas
checkpoint | Confirm that sign is correct size, affixed in correct location, correctly completed, dated and sighted and the tester clearly identified
checkpoint | Where alterations have occurred, confirm addition of label stating this and indicating the date, name and organisation responsible
checklist-flat | AE-ITCX-028 - Lead-Ins Checklist (Rev 0 +Names) |  | NEW CL 13/09/21 - To be added to each project
checkpoint | Latest consented drawings checked & referenced
text | Meter Panel Info
text | Drawing & Revision #
checkpoint | Roughin Leadin cables
checkpoint | Submains installed to the documented location in the field/riser
label | Grouped together 3 or less and labelled correctly
checkpoint | MATV cables installed to the documented location in the field/riser and labelled correctly
checkpoint | Confirm comms leadins
bool | Fibre
bool | Cat6
bool | Cat6A
bool | NBN Conduit
checkpoint | NBN - Select N/A if not NBN
label | Confirm each of the below, add comments and photos as applicable below
button | NBN Conduit installed to the documented location in the field/riser and labelled correctly | Yes, No, N/A
button | Draw string installed with the correct “stopper” tied off and labelled correctly | Yes, No, N/A
button | NBN box/enclosure installed or spatial NBN allocation is compliant | Yes, No, N/A
checkpoint | Fibre, Cat 6 & Cat 6A
label | Confirm each of the below, add comments and photos as applicable below
button | Minimum 50mm seperation from other services | Yes, No, N/A
button | Velcro used to support cable | Yes, No, N/A
button | No more than 24 cables per bundle | Yes, No, N/A
button | Labelled correctly | Yes, No, N/A
checkpoint | Intercom cable installed to the documented location in the field/riser and labelled correctly
checkpoint | DB installed prior to plaster, in the correct location and height
checkpoint | Leadin cables & conduits fire rated/smoke sealed through all walls
checkpoint | Lead-Ins completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Checked by (Appselec) | #NAME? | To be updated with employee list
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-029 - Rough-In Checklist (Rev 0 +Names) |  | NEW CL 13/09/21 - To be added to each project
section | Power
checkpoint | Power circuits installed to the documented location in the field/riser/DB and labelled correctly
checkpoint | Outlets within joinery/feature ceilings and walls have been co-ordinated
checkpoint | Steel framework earthed
checkpoint | MATV splitter earth installed
checkpoint | MANDATORY PHOTO - Accurate aswired drawings upon completion of fit off including variations & site changes
label | Additional Photos attached below as applicable
section | Lighting
checkpoint | All cabling installed to the documented location in the field/riser/DB location and labelled correctly,
label | Including 2 way/int switching, smoke detector interlink & LED ELV cabling
checkpoint | Plugbases/Quick connects fit off
checkpoint | External lighting (including PE cell) cabling installed to the documented location
checkpoint | Lighting control cabling installed to the documented location and correct cable type used
checkpoint | All cabling installed within the correct documented zones
checkpoint | Confirm that the documented lighting control topology has been installed
select | Lighting control topology | Star, Ring, Daisy
checkpoint | Confirm that the documented lighting control topology has been installed
checkpoint | Timber noggins installed for large pendant lights
checkpoint | MANDATORY PHOTO - Accurate aswired drawings upon completion of fit off including variations, site changes, driver and puk locations
label | Additional Photos attached below as applicable
section | MATV
checkpoint | MATV cabling been installed to the documented location and labels reference shop drawing
checkpoint | Splitters fit off
checkpoint | MANDATORY PHOTO - Accurate aswired drawings upon completion of fit off including variations, site changes
label | Additional Photos attached below as applicable
section | Comms
checkpoint | Comms cabling installed to the documented location
label | Including correct cable type installed and labels reference shop drawing
checkpoint | MANDATORY PHOTO - Accurate aswired drawings upon completion of fit off including variations, site changes
label | Additional Photos attached below as applicable
section | Security
checkpoint | Access control cabling installed to the documented location in the field/riser and labelled correctly
checkpoint | CCTV cabling installed to the documented location in the field/riser and labelled correctly
checkpoint | MANDATORY PHOTO - Accurate aswired drawings upon completion of fit off including variations, site changes
label | Additional Photos attached below as applicable
section | UPS
checkpoint | UPS circuits installed to the correct locations, and labelled correctly at the DB
checkpoint | MANDATORY PHOTO - Accurate aswired drawings upon completion of fit off
label | Additional Photos attached below as applicable
section | Sign-Off
checkpoint | Lead-Ins completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME? | To be updated with employee list
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-030 - Cut-Out Sheet (Rev 0 +Names) |  | UPDATED 13/09/21 - To be updated in library and projects
checkpoint | Walls cutout
checkpoint | Ceilings cutout
checkpoint | Cut outs with obstructions have been resolved (for example furring channel, main bar)
checkpoint | All cables located and pulled out of penetration
checkpoint | Fire boxes installed correctly on all fire rated walls
checkpoint | Fire boxes documented on fire register
checkpoint | MANDATORY PHOTO - Attach/photo below of marked up fire register
label | Additional photos of Obstructions attached below as applicable
checkpoint | Cut-Out completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here) |  | To be updated with employee list
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-31 - Fit-Off General Checklist (Rev 0 +Names) |  | NEW CL 13/09/21 - To be added to each project
section | Power
checkpoint | Power outlets fit off including GPOs, isolators & hard wired equipment
checkpoint | Outlets within Joinery, feature ceilings and walls fit off
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of fit off including variations & site changes
label | Additional Photos attached below as applicable
section | Lighting
checkpoint | Light switches, LCPs, dimmers, drivers and PUKs fit off
checkpoint | Light fittings within ceiling fit off
checkpoint | Light fittings within joinery and walls fit off
checkpoint | Light fittings within finished floors fit off
checkpoint | Smoke detectors fit off
checkpoint | External lighting fit off
checkpoint | Motion detectors fit off
checkpoint | Emergencies installed in documented location
checkpoint | Exit directional signage facing the correct way
checkpoint | Exits un-obstructed from view
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of fit off including variations, site changes, driver and puk locations
label | Additional Photos attached below as applicable
section | MATV
checkpoint | MATV outlets fit off
checkpoint | Splitters fit off
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of fit off including variations & site changes
label | Additional Photos attached below as applicable
section | Comms
checkpoint | Comms outlets fit off
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of fit off including variations & site changes
label | Additional Photos attached below as applicable
section | Security Final Review (Excluding Testing)
checkpoint | Access control fit off to the documented location
checkpoint | Cameras installed and fit off to the documented location
checkpoint | Cameras have a clear line of site and un-obstructed from other services
checkpoint | Intercoms installed and fit off to the documented location
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of fit off including variations & site changes
label | Additional Photos attached below as applicable
section | UPS
checkpoint | Correct UPS outlets fit off completed
label | Photos attached below as applicable
section | Sign-Off
checkpoint | Fit-Off completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME? | To be updated with employee list
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-32 - Electrical Commissioning Checklist (Rev 0 +Names) |  | NEW CL 13/09/21 - To be added to each project
section | Documentation to proceed with commissioning
checkpoint | AE-FORM-006 - Builders Works Completion Notice' been completed
label | Photo/Upload of AE-FORM-006
checkpoint | AE-FORM-011 - Notice of Intent to Energise Electrical Installation' been completed
label | Photo/Upload of AE-FORM-011
checkpoint | AE-FORM-009 - Start card been filled out by all workers within the commissioning crew
label | Photo/Upload of AE-FORM-009
checkpoint | Rough In/ Fit Off QA been reviewed and utilised for commissioning QA
section | Switchboard
checkpoint | All screw terminations tight, with copper not visibly out of terminal
checkpoint | Neutrals correspond with actives
checkpoint | Pole fillers installed
checkpoint | DB door and eschucheon scratch and defect free
checkpoint | Switchboard labelled and cleaned
checkpoint | Cable entry points fire sealed
checkpoint | All circuits RCD protected if answer is no confirm in note section the circuit number and reason for no protection
checkpoint | BMU circuits protected by a 100mA RCD
checkpoint | Correct lighting control schematic and schedule installed
checkpoint | Correct lighting control equipment installed
checkpoint | Appselec 'installed by' sticker installed
checkpoint | Warning: Interupting power supply will discharge emergency lighting batteries' installed next to RCBO feeding emergency lighting
checkpoint | Energy Meter been installed with CT metering
checkpoint | Wiring goes through the correct CT, installed in the correct direction and terminated to the correct phase
checkpoint | Wiring neatly loomed internally and externally of the DB
checkpoint | Lighting control and timers set to the documented schedule and labelled
checkpoint | Contactors functioning correctly
checkpoint | Surge arrestors installed and switched on upon completion of commissioning
checkpoint | Cables mechanicaly protected external of DB where applicable
checkpoint | Manual test of ATS/load shedding contactor completed to confirm power drops out to the correct circuits
checkpoint | Fire rating complete to all risers
checkpoint | Air sealing complete under floors
checkpoint | MANDATORY PHOTOS - ONLY PASS ONCE ALL PHOTOS HAVE BEEN ATTACHED BELOW
label | Photos attached below as applicable
bool | Mandatory Photo 1 - Accurate DB schedule matching installation
bool | Mandatory Photo 2- DB Name (N/A for apartment DB)
bool | Mandatory Photo 3 - DB Installation and surrounds
bool | Mandatory Photo 4 - DB with eschucheon
bool | Mandatory Photo 5- DB without eschucheon showing wiring
section | General - Final review
checkpoint | Outlets, switches and other equipment installed straight, level, in the correct location and mounting height
checkpoint | Outlets, switches and other equipment either fit off or made safe
checkpoint | Master switch operates documented items
checkpoint | Electric appliances switching correctly
checkpoint | AC/FCU control functions correctly
checkpoint | Electric cooktop has a visible isolation switch in accordance with AS3000
checkpoint | Exhaust fans function correctly Where a fan is switched from multiple locations, double pole mechs are installed to prevent the “back feeding” of lights in the other spaces
checkpoint | All outlets labelled correcly
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of commissioning including variations, site changes, driver and puk locations
label | Additional Photos attached below as applicable
section | Variations/Purchaser Changes
checkpoint | Is there variations within zone (If you are unsure confirm with your Site Manager)
checkpoint | All variations captured on an As-Built
section | Lighting control - General
checkpoint | Lighting control function as per the documented functional description
checkpoint | Dimmers function correctly Applicable lights dim smoothly without strobing
checkpoint | Lights correctly switching, including 2-ways and intermediates
checkpoint | Neons correctly switching (plantroom switches etc.)
checkpoint | Dali fittings flash tested and confirmed they are in the correct dali zones
checkpoint | Black out test completed for PE cell and fittings functioning correctly
checkpoint | Motion detectors tested independantly of one another
checkpoint | Motion detectors un-obstructed from functioning correctly
checkpoint | Motion detectors switch correct fittings/zones
checkpoint | Motion detectors set to nominated time once commissiong complete
section | Emergency lighting
checkpoint | Dali emergencies flash tested
checkpoint | 120min battery discharge test completed and documented
checkpoint | Exit and emergencies numbered on the asbuilt
checkpoint | Exit and emergencies labelled on the fitting and numbers match the asbuilt drawing
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of commissioning including variations, site changes, driver and puk locations
label | Additional Photos attached below as applicable
section | UPS System
checkpoint | UPS backing up the correct circuits
checkpoint | UPS transfer switch is functioning correctly when power supply is interupted
checkpoint | Circuits backed up by the UPS continue to have power when power is interupted
checkpoint | Load test completed and results recorded
checkpoint | Labelling of outlets complete
checkpoint | MANDATORY PHOTO - Accurate asbuilt drawings upon completion of commissioning including variations, site changes
label | Additional Photos attached below as applicable
section | Documentation
checkpoint | All circuits locked/tagged out been entered into the "AE-FORM-010 - Isolation Tag Register"
checkpoint | MANDATORY PHOTO - Isolation tag register
label | Additional Photos attached below as applicable
section | Sign-Off
checkpoint | Electrical Commissioning completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME? | To be updated with employee list
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist-flat | AE-ITCX-033 - Busduct Installation (Rev 0 +Names) |  | UPDATED 13/09/21 - To be updated in library and projects
checkpoint | Busduct Details - Pass once entered/confirmed
text | Drawing & Revision # (or Attach photo below)
text | Run details
text | Package #
text | Approx weight (kg) - Excluding Packaging
checkpoint | Piece 1 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 2 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 3 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 4 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 5 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 6 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 7 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 8 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 9 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Piece 10 - Item onsite - Pass=Yes / Fail=No
text | Vass Shop Draing Piece #
text | Piece weight
select | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | Final location
checkpoint | Sign-Off - Busduct Installation completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here) |  | To be updated with employee list
label | Signature Sign-Offs - Attach signature(s) below
checklist | AE-ITCX-34 - Communications/Security Rack Installation QA (Rev 0 +Names) |  | NEW CL 13/09/21 - To be added to each project
section | Communications Rack
checkpoint | Is the communications riser ready for communications rack installation
label | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
label | MANDATORY PHOTO - Photo attached below
checkpoint | Does the communications rack match the approved technical data
checkpoint | Has the communications rack been installed in position as per the Appselec communications riser elevation shop drawings and floor plan layout
text | Drawing & Revision # (or Attach photo below)
checkpoint | Has the communications rack been fixed to the floor using appropriate fixings
checkpoint | Are the doors and side panels installed and free from damage
checkpoint | Does the communications rack comply with all the relevant clearances
label | Are door swings and access to the communications rack unobstructed
checkpoint | Has the communications rack been permanently labelled with a traffolyte label or similar on the door
label | Check that the label matches the communications rack layouts
checkpoint | Has the Appselec label/logo been fixed to the front of the communications rack
label | MANDATORY PHOTO - Photo attached below
section | Communications Earthing Terminal (CET)
checkpoint | Has a CET been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth cable been terminated to the CET
label | Refer to Communications SLD for earth cabling schematic
label | MANDATORY PHOTO - Photo attached below
checkpoint | Has an earth bar been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth been terminated to the earth bar from the CET
checkpoint | Has the 6 mm2 green/yellow earth been identified and labelled with “Communications Earth” at the originating electrical distribution board
section | FOBOTS (Fibre Optical Breakout Trays)
checkpoint | Does the FOBOT match the approved technical data
checkpoint | Has the FOBOT been installed in the correct rack RU position as per the communications rack layout
checkpoint | Has the FOBOT been labelled permanently with traffolyte label or similar
checkpoint | Has a service loop been provided in the optical fibre cable
checkpoint | Has the fibre port arrangement on the FOBOT been detailed and labelled
label | MANDATORY PHOTO - Photo attached below
checkpoint | Do the fibre adapters on the FOBOT match the type of fibre being used
label | e.g. aqua = multimode, green = singlemode
label | Adapters, pigtail connector colours must match, fibre cable type must match
checkpoint | Have fibre protective caps been installed on all fibre adapter ports
section | Cat 6/6A Patch Panels
checkpoint | Does the Cat 6/6A patch panels match the approved technical data
checkpoint | Have the Cat 6/6A patch panels been installed in correct rack RU position as per the communications rack layout
checkpoint | Have the Cat 6/6A patch panel ports been labelled permanently with traffolyte label or similar
label | MANDATORY PHOTO - Photo attached below
checkpoint | Have cable wrap-around labels been attached to each individual Cat 6/6A cable behind the patch panels
label | MANDATORY PHOTO - Photo attached below
checkpoint | Have the Cat 6/6A patch panels been earthed with 2.5 mm2 green/yellow earth cable from the earth bar within the communications rack? (Shielded patch panels only)
section | Cable Management
checkpoint | Have horizontal cable managers been installed in the correct rack RU position as per the communications rack layout
checkpoint | Have vertical cable managers been installed in the correct rack RU position as per the communications rack layout
section | Power
checkpoint | Has the correct power been provided for the communications racks
label | Check for captive outlets? Are there 2x or 1x? Are they 10A, 15A or 20A? Check the Appselec power floor layouts against the communications specification
checkpoint | Do the PDU’s match the approved technical data
checkpoint | Have the PDU’s been installed in position as per the communications rack layout
checkpoint | Have the PDU’s been plugged into the captive outlets/rack mounted UPS as detailed on the communications rack layouts
checkpoint | Have the PDU’s been labelled appropriately detailing the power source
label | For example UPS supply (Generator backed) DB-XX
section | Rackmount UPS
checkpoint | Is the communications rack/riser ready for UPS installation
label | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint | Does the UPS match the approved technical data
checkpoint | Has the UPS been installed in position as per the communications rack layouts
checkpoint | Has the UPS been labelled appropriately detailing the power source
label | For example UPS supply (Generator backed) DB-XX
label | MANDATORY PHOTO - Photo attached below
checkpoint | Has any associated Battery Backup for the UPS been installed as per the communications rack layouts and is it connected
checkpoint | Has the UPS been commissioned? Refer to UPS ITP for commissioning details
section | Active Equipment
checkpoint | Is the communications rack/riser ready for Active Equipment installation
label | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint | Does the Active Equipment need to be configured prior to installation within the communications rack
checkpoint | Does the Active Equipment match the approved technical data
checkpoint | Has the Active Equipment been installed in the correct rack RU position as per the communications rack layouts
label | MANDATORY PHOTO - Photo attached below
checkpoint | Do you have a network diagram detailing the connection and labelling of all Active Equipment
checkpoint | Has the Active Equipment been labelled appropriately as per the vendor requirements
label | All switches are to be labelled with the correct vendor labelling convention
checkpoint | Have SFPs been provided and installed
label | Check that they are the correct SFP for the optical fibre cable installed
label | Check they are installed into the correct port
label | (SFP is a small form-factor pluggable transceiver)
checkpoint | Have stacker cables been provided to stack switches together
label | Are they connected as per the integrator/vendor requirements
checkpoint | Have the switches been connected to the PDUs
label | Check if switches require one supply or two supplies (dual power redundancy)
label | Check if switches require UPS supply/UPS + generator supply
section | Patching
checkpoint | Do you have the correct length, colour, type (Cat6/6A) and quantity of patch leads
checkpoint | Do you have a patching schedule detailing which switch port patches to which patch panel port
checkpoint | Do you have the appropriate cable management capacity installed to patch cables as per the patching schedule
section | Mandatory Photos
checkpoint | MANDATORY Photo 1: Front of rack, door closed - Photo attached below
checkpoint | MANDATORY Photo 2: Front of rack, door open - Photo attached below
checkpoint | MANDATORY Photo 3: Front of rack, door closed - Photo attached below
checkpoint | MANDATORY Photo 4: Rear of rack, doors open - Photo attached below
label | Additional Photos attached below as applicable
section | Sign-Off
checkpoint | Communications/Security Rack Installation completed to specification/drawings - Area left clean & tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | Any Corrective Actions to be Photographed & Commented below
select | Name of A-Grade Electrician | #NAME? | To be updated with employee list
text | Other (Specify here)
label | Signature Sign-Offs - Attach signature(s) below
checklist | AF-502 - Electrical Services commissioning Sheet - Details & 10x Circuit Checklist (Rev 0 +Names)
section | Electrician Details
checkpoint | Details - Pass once entered
text | Test Date
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
section | Circuit Details
checkpoint | Details - Pass once entered
text | Designation of service
text | Location of Service
text | Test Equipment Model
text | Test Equipment Serial No.
text | Method of Fault Protection
text | Prospective Fault Current
text | ZE
label | .. ..
label | Specify Board Type below,Pass to applicable, N/A to irrelevant ones
checkpoint | Main Switchboard
label | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance
checkpoint | House Dist. Board
label | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance, RCD Test (Where installed)
checkpoint | Apartment Dist. Board
label | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance RCD test
checkpoint | Mains Reticulation
label | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance
checkpoint | Other (Specify below)
text | Other (Specify here)
label | To be determined by competent/qualified technician
section | CB 1
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 2
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 3
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 4
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 5
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 6
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 7
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 8
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 9
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
section | CB 10
checkpoint | CB Details
text | CB #
text | Circuit description
checkpoint | Visual Inspection
checkpoint | Earth Continuity (Pg. Resistance)
checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint | Polarity
checkpoint | Correct Circuit Connection
checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint | RCD Test (Pg. Proactive)
checklist | AF-502 - Electrical Services commissioning Sheet - Details & 10x Circuit Resistance & Fault-Loop Impedance (Rev 0 +Names)
section | Electrician Details
checkpoint | Details - Pass once entered
text | Test Date
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
section | Circuit Details
checkpoint | Details - Pass once entered
text | Designation of service
text | Location of Service
text | ZE
section | No. 1
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 2
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 3
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 4
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 5
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 6
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 7
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 8
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 9
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 10
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
text | Rating in (A)
checkpoint | Data Capture
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
checklist | AF-502 - Electrical Services commissioning Sheet - DETAILS & 10x Circuits- Insulation Resistance (Rev 0 +Names)
section | Electrician Details
checkpoint | Details - Pass once entered
text | Test Date
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
section | Circuit Details
checkpoint | Details - Pass once entered
text | Designation of service
text | Location of Service
label | L1= Red Phase, L2= White Phase, L3= Blue Phase
label | Where a single phase circuit is being tested, enter the result in the column that corresponds to the supplying phase, enter N?A for the other phases
section | No. 1
checkpoint | Details - Pass once entered
text | L1 - N
text | L2 - N
text | L3 - N
text | L1 - E
text | L2 - E
text | L3 - E
text | N - E (MEN Disconnected)
checkpoint | L1-L2 (N/A if 1 Ph)
text | Calculation
checkpoint | L2-L3 (N/A if 1 Ph)
text | Calculation
checkpoint | L1-L3 (N/A if 1 Ph)
text | Calculation
section | No. 2
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 3
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 4
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 5
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 6
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 7
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 8
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 9
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
section | No. 10
checkpoint | Overcurrent Device - Pass once entered
text | Short Circuit Capacity (i.e. 6kA, 10kA)
text | Type B, C, D, TM Electronic
checkpoint | Data Capture
text | Rating in (A)
text | (A) Active CSA mm2
text | (B) Earth CSA mm2
text | (C) = A+B
checkpoint | Measure
text | (D) Rphe (Ohms)
checkpoint | Data Capture
text | RE = (D/C) * A
text | Calculated Loop impedance = D + ZE
checkpoint | Measure
text | (F) Tested ZS
checkpoint | Data Capture
text | Difference (F) - Calc'd ZS
checklist | DETAILS & 10x - AF-502 - Electrical Services commissioning Sheet - Protective Device Details and RCD Results (Rev 0 +Names)
section | Electrician Details
checkpoint | Details - Pass once entered
text | Test Date
select | Name of A-Grade Electrician | #NAME?
text | Other (Specify here)
bool | Signature added below
section | Circuit Details
checkpoint | Details - Pass once entered
text | Designation of service
text | Location of Service
section | No. 1
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 2
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 3
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 4
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 5
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 6
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 7
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 8
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 9
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken
section | No. 10
checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint | Protective Device type selected and details entered
select | Device type | RCD, RCBO, CB, FUSE
select | RCD Type - Where applicable | A, AC, B, F
text | Nominal Trip Current (may)
checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 0.Deg (P/F)
text | 180.Deg (P/F)
checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 0.Deg
text | 180.Deg
checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | Action taken

## Employee List V.150921
| Appselec Employee Names | CONQA Notes - Date added
Example | James Braddock - AGrade: 1234 - Employee#: 1234
| ADAM KENT - AGrade: A56009 - Employee#: 1622 | 15/9/21
| ADAM STRONG - AGrade: A38815 - Employee#: 2002 | 15/9/21
| ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 | 15/9/21
| ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 | 15/9/21
| ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 | 15/9/21
| ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 | 15/9/21
| ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 | 15/9/21
| ALI HASAN - Agrade: A48087 - Employee#: 1654 | 15/9/21
| ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 | 15/9/21
| ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957 | 15/9/21
| ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 | 15/9/21
| ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 | 15/9/21
| BEN DARBY - Agrade: A53332 - Employee#: 1702 | 15/9/21
| BEN FINDLAY - Agrade: A41429 - Employee#: 2006 | 15/9/21
| BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 | 15/9/21
| BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 | 15/9/21
| BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865 | 15/9/21
| BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 | 15/9/21
| BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 | 15/9/21
| BRENTON HILL - Agrade: A47213 - Employee#: 1729 | 15/9/21
| BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 | 15/9/21
| BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 | 15/9/21
| BROCK LLOYD - Agrade: A44808 - Employee#: 1680 | 15/9/21
| CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644 | 15/9/21
| DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 | 15/9/21
| DANIEL MILLER - Agrade: A42685 - Employee#: 1909 | 15/9/21
| DANIEL SETTE - Agrade: A50502 - Employee#: 1812 | 15/9/21
| DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 | 15/9/21
| DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 | 15/9/21
| DAVID OLSEN - Agrade: A42915 - Employee#: 1685 | 15/9/21
| DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 | 15/9/21
| DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 | 15/9/21
| ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 | 15/9/21
| EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 | 15/9/21
| FERGUS COATES - Agrade: A59054 - Employee#: 1774 | 15/9/21
| FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 | 15/9/21
| HUY DO - Agrade: A40954 - Employee#: 873 | 15/9/21
| IMMANUEL KAWITI - Agrade: - Employee#: 2023 | 15/9/21
| JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 | 15/9/21
| JAMES MARASCO - Agrade: A55184 - Employee#: 1758 | 15/9/21
| JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 | 15/9/21
| JAMES SPOKES - Agrade: A48756 - Employee#: 1770 | 15/9/21
| JASON CRAMER - Agrade: A57832 - Employee#: 1673 | 15/9/21
| JASON GARETTO - Agrade: A46469 - Employee#: 1896 | 15/9/21
| JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 | 15/9/21
| JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 | 15/9/21
| JASON PERL - Agrade: A36692 - Employee#: 1868 | 15/9/21
| JASON SALE - Agrade: A28662 - Employee#: 1615 | 15/9/21
| JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 | 15/9/21
| JESS ZAHRA - Agrade: A52969 - Employee#: 1403 | 15/9/21
| JOEL BASSETT - Agrade: A39498 - Employee#: 1958 | 15/9/21
| JOEL COGHLAN - Agrade: A43339 - Employee#: 1220 | 15/9/21
| JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 | 15/9/21
| JOHN GREEN - Agrade: A55589 - Employee#: 1734 | 15/9/21
| JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 | 15/9/21
| JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 | 15/9/21
| KALE BLACKLER - Agrade: A39293 - Employee#: 1751 | 15/9/21
| KAYNE WALKER - Agrade: A38805 - Employee#: 1718 | 15/9/21
| KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 | 15/9/21
| KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 | 15/9/21
| LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 | 15/9/21
| MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 | 15/9/21
| MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 | 15/9/21
| MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 | 15/9/21
| MATTHEW COX - Agrade: A42092 - Employee#: 1704 | 15/9/21
| MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 | 15/9/21
| MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 | 15/9/21
| MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 | 15/9/21
| NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 | 15/9/21
| PAT DOUBLE - Agrade: A46604 - Employee#: 1118 | 15/9/21
| PAUL HARMAN - Agrade: A26306 - Employee#: 1728 | 15/9/21
| PAUL RABAHI - Agrade: A52747 - Employee#: 1939 | 15/9/21
| PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 | 15/9/21
| PETER LEWIS - Agrade: A53556 - Employee#: 1749 | 15/9/21
| PHILIP BROWN - Agrade: A55466 - Employee#: 1940 | 15/9/21
| PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 | 15/9/21
| ROB POLLARD - Agrade: A56906 - Employee#: 1754 | 15/9/21
| ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 | 15/9/21
| RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 | 15/9/21
| SCOTT RYAN - Agrade: A59062 - Employee#: 2017 | 15/9/21
| SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 | 15/9/21
| SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 | 15/9/21
| SIMON COLLARD - Agrade: A32749 - Employee#: 883 | 15/9/21
| STEVEN THOM - Agrade: A48941 - Employee#: 1199 | 15/9/21
| STUART MALVENAN - Agrade: A61071 - Employee#: 1829 | 15/9/21
| TOM HAMILTON - Agrade: A48254 - Employee#: 1434 | 15/9/21
| VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 | 15/9/21
| WILLIAM FISHER - Agrade: A20679 - Employee#: 859 | 15/9/21
Other (Specify below)
#NAME?

## Distribution Boards & Sub Circ
Distribution Boards and Sub Circuits
| Building A - IPU | Sub DB JEN-2 LLG | AE-ITCX-015 - Mandatory Test Results (Rev 1 +Names)
AE-ITCX-018 - DB Fit Off Sheet (Rev 0 +Names)
AE-ITCX-006 - Distribution Board Visual Inspection (Rev 0 +Names)
AE-ITCX-029 - Rough-In Checklist (Rev 0 +Names)
AE-ITCX-030 - Cut-Out Sheet (Rev 0 +Names)
AE-ITCX-31 - Fit-Off General Checklist (Rev 0 +Names)
AE-ITCX-32 - Electrical Commissioning Checklist (Rev 0 +Names)
AE-ITCX-025 AS:3003 - Appendix E Body Protected CL (Rev 0 +Names)
AE-ITCX-026 AS:3003- Appendix F Cardiac Protected CL (Rev 0 +Names)
AE-ITCX-027 AS:3003-Table B1 Patient Area CL (Rev 0)
|  | DB-1A-L00-DRC3.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-DRC3.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRC3.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRC3.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-DRC3.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-DRC3.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-DRC3.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-DRC3.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-DRC0.4 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-DRC4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-DRC4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-DRC4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-DRC4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-EM4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-EM4.3 - Deleted | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRC4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRC4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-DRC4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-DRC4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-DRG4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-ES4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-ES4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-ES4.3 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-DRC4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-ES4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-ES4.3 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-DRC4.3 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-DRG4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LB1-DRC0.4 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LB1-DRG0.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRC4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRG4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRG4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L00-CR4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L00-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L00-EM4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L01-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L01-EM4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L02-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L02-NE4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L03-ES4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L03-ES4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L04-ES4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L05-CR4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L05-NE4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L05-NE4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LB1-CR0.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-CR0.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LB1-NE0.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-ES4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-NE4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-NE4.2 | As per - Sub DB JEN-2 LLG
|  | DB-GEN-AUX-2 | As per - Sub DB JEN-2 LLG
|  | DB-GEN-AUX-4 | As per - Sub DB JEN-2 LLG
|  | MDB-2A-LB1-DRC | As per - Sub DB JEN-2 LLG
|  | MDB-2A-LB1-DRCR | As per - Sub DB JEN-2 LLG
|  | MDB-2A-LB1-DRG | As per - Sub DB JEN-2 LLG
|  | MDB-2A-L05-PV4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-CR0.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L02-CR2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-CR4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-NE0.6 | As per - Sub DB JEN-2 LLG
|  | TDB-2B-L00-NE4.1 | As per - Sub DB JEN-2 LLG
|  | TDB-2B-L01-NE4.1 | As per - Sub DB JEN-2 LLG
|  | TDB-2B-L04-NE4.1 | As per - Sub DB JEN-2 LLG
|  | TX2.A1 | As per - Sub DB JEN-2 LLG
|  | TX2.A2 | As per - Sub DB JEN-2 LLG
|  | TX2.B1 | As per - Sub DB JEN-2 LLG
|  | TX2.B2 | As per - Sub DB JEN-2 LLG
As per - Sub DB JEN-2 LLG
| Building B - IPU | Sub DB JEN-1 LLG | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-DRC1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-DRC1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-DRG1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-DRG1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-EM1.1 | As per - Sub DB JEN-2 LLG
|  | Sub DB PET L00 | As per - Sub DB JEN-2 LLG
|  | Sub DB SPECT-1 L00 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-EM1.2 | As per - Sub DB JEN-2 LLG
|  | Sub DB CT-1 L00 | As per - Sub DB JEN-2 LLG
|  | Sub DB MRI-1 L00 | As per - Sub DB JEN-2 LLG
|  | Sub DB MRI-3 L00 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-DRC1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-DRC1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-DRG1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-DRG1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-EM1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-EM2.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRC1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRC1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRCR1.1 | As per - Sub DB JEN-2 LLG
|  | Sub DB Fluroscopy-1 L02 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRCR1.2 | As per - Sub DB JEN-2 LLG
|  | Sub DB CLAB-2 L02 | As per - Sub DB JEN-2 LLG
|  | Sub DB CLAB-4 L02 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-DRCR1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L02-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-DRC1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-DRG1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-EM1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-DRC1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-DRC0.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-DRG1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-DRC1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-DRCR1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-DRG1.1 - (FUTURE) | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-ES1.1 - (FUTURE) | As per - Sub DB JEN-2 LLG
|  | DB-1A-L05-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L06-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L06-DRCR1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L06-DRG1.2 - (FUTURE) | As per - Sub DB JEN-2 LLG
|  | DB-1A-L06-DRG1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L06-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L06-EM1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L07-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L07-DRCR1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L07-DRG1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L07-DRG1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L07-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L07-EM1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L08-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L08-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L08-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L09-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L09-DRG1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L09-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L09-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L10-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L10-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L10-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-DRC0.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-DRG0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRC1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRC1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRCR1.1 | As per - Sub DB JEN-2 LLG
|  | Sub DB Pandemic Mode-1 LLG | As per - Sub DB JEN-2 LLG
|  | Sub DB Pandemic Mode-2 LLG | As per - Sub DB JEN-2 LLG
|  | Sub DB Pandemic Mode-3 LLG | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRCR1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRCR1.3 | As per - Sub DB JEN-2 LLG
|  | Sub DB CT Satellite LLG | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRG0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-EM2.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L00-EM1.1 | As per - Sub DB JEN-2 LLG
|  | Sub DB SPECT-2 L00 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L00-EM1.2 | As per - Sub DB JEN-2 LLG
|  | Sub DB CT-2 L00 | As per - Sub DB JEN-2 LLG
|  | Sub DB MRI-2 L00 | As per - Sub DB JEN-2 LLG
|  | Sub DB Fluroscopy-1 L00 | As per - Sub DB JEN-2 LLG
|  | Sub DB Fluroscopy-2 L00 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L01-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L02-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-NE1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-NE1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L03-NE2.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L04-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-NE1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L05-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L05-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L06-ES1.2 - (FUTURE) | As per - Sub DB JEN-2 LLG
|  | DB-1B-L06-EM1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L07-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L07-EM1.3 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L08-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L08-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L09-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L09-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L10-ES1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-L10-ES1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L11-NE1.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L11-NE1.2 | As per - Sub DB JEN-2 LLG
|  | DB-1B-LLG-CR0.2 | As per - Sub DB JEN-2 LLG
|  | DB-1B-LB1-CR0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1B-LB1-CR0.2 | As per - Sub DB JEN-2 LLG
|  | DB-1B-LB1-CR0.4 | As per - Sub DB JEN-2 LLG
|  | DB-1B-LB1-EM0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-NE0.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-NE0.4 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-NE0.11 (FUTURE) | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-DRC2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-DRG4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L00-EM4.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-DRC2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-DRG2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-EM1.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L01-EM2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRC2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRC2.3 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRCR2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRCR2.2 | As per - Sub DB JEN-2 LLG
|  | Sub DB CLAB-1 L02 | As per - Sub DB JEN-2 LLG
|  | Sub DB CLAB-1 L02 | As per - Sub DB JEN-2 LLG
|  | Sub DB HYBRID L02 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L02-DRCR2.3 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-DRC2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L03-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-DRC2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LB1-DRC0.3 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-DRG2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L04-ES2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-DRC2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-DRCR2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-DRG2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L05-ES2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L06-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L06-DRCR2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L07-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L07-DRCR2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L08-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L09-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-L10-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LB1-DRC0.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LB1-DRG0.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRC0.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRC2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRCR2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRCR2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2A-LLG-DRCR2.3 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L00-EM4.3 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L00-EM2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L01-EM2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L01-NE2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L02-NE2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L03-EM4.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L03-ES2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L04-ES2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L04-ES2.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-L05-ES2.1 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LB1-CR0.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LB1-CR0.4 | As per - Sub DB JEN-2 LLG
|  | DB-GEN-AUX-1 | As per - Sub DB JEN-2 LLG
|  | DB-GEN-AUX-3 | As per - Sub DB JEN-2 LLG
|  | TDB-1A-L00-NE2.2 | As per - Sub DB JEN-2 LLG
|  | MDB-1A-LB1-DRCR0.2 | As per - Sub DB JEN-2 LLG
|  | MDB-1A-LB1-DRC | As per - Sub DB JEN-2 LLG
|  | MDB-1A-LB1-DRCR | As per - Sub DB JEN-2 LLG
|  | MDB-1A-LB1-DRG | As per - Sub DB JEN-2 LLG
|  | MDB-1A-LB1-DRCR0.1 | As per - Sub DB JEN-2 LLG
|  | MDB-2A-LB1-DRCR0.2 | As per - Sub DB JEN-2 LLG
|  | MDB-2A-LB1-DRCR0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L01-EM2.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.11 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.12 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.15 | As per - Sub DB JEN-2 LLG
|  | TDB-1A-L00-NE1.3 | As per - Sub DB JEN-2 LLG
|  | TX1.A1 | As per - Sub DB JEN-2 LLG
|  | TX1.A2 | As per - Sub DB JEN-2 LLG
|  | TX1.A3 | As per - Sub DB JEN-2 LLG
|  | TX1.B1 | As per - Sub DB JEN-2 LLG
|  | TX1.B2 | As per - Sub DB JEN-2 LLG
|  | STS-1A-LB1-DRCR0.1 | As per - Sub DB JEN-2 LLG
|  | STS-1A-LB1-DRCR0.2 | As per - Sub DB JEN-2 LLG
|  | STS-2A-LB1-DRCR0.1 | As per - Sub DB JEN-2 LLG
|  | STS-2A-LB1-DRCR0.2 | As per - Sub DB JEN-2 LLG
|  | STS-1A-LB1-DRG (1) | As per - Sub DB JEN-2 LLG
|  | STS-1A-LB1-DRG (2) | As per - Sub DB JEN-2 LLG
|  | DRUPS LOAD BANK ATS | As per - Sub DB JEN-2 LLG
|  | STS-2A-LB1-DRG (2) | As per - Sub DB JEN-2 LLG
|  | STS-2A-LB1-DRG (1) | As per - Sub DB JEN-2 LLG
| Building C - Carpark | C-DB-1A-L00-NE0.1 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L00-NE0.2 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L00-NE0.3 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L01-NE7.1 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L02-NE7.1 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L03-NE7.1 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L04-NE7.1 | As per - Sub DB JEN-2 LLG
|  | C-TDB-1A-L00-NE0.1 | As per - Sub DB JEN-2 LLG
|  | C-TDB-1A-L00-NE0.2 | As per - Sub DB JEN-2 LLG
|  | C-TDB-1A-L00-NE0.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L04-NE7.11 (FUTURE) | As per - Sub DB JEN-2 LLG
|  | DB-1A-LB1-NE0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE7.10 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE7.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.4 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.5 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.6 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.11 | As per - Sub DB JEN-2 LLG
|  | C-MDB-1A-L00-NE7 | As per - Sub DB JEN-2 LLG
|  | C-DB-1A-L00-DRC7.1 | As per - Sub DB JEN-2 LLG
|  | C-DB-2A-L00-DRC7.1 | As per - Sub DB JEN-2 LLG
|  | C-MDB-1A-LB1-PV0.1 | As per - Sub DB JEN-2 LLG
|  | C-MDB-1A-LB1-PV0.2 | As per - Sub DB JEN-2 LLG
|  | C-MDB-1B-LB1-PV0.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-NE7.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-NE7.2 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-NE7.3 | As per - Sub DB JEN-2 LLG
|  | DB-1A-L00-NE7.4 | As per - Sub DB JEN-2 LLG
| Building D - Tiernan Commercial |  | As per - Sub DB JEN-2 LLG
|  | D-DB-1A-LLG-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-DB-1A-L05-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-L00-NE6.4 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-L00-NE6.5 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-L01-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-L02-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-L03-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-L04-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-LLG-NE6.1 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-LLG-NE6.2 | As per - Sub DB JEN-2 LLG
|  | D-TDB-1A-LLG-NE6.3 | As per - Sub DB JEN-2 LLG
|  | D-MDB-1A-LLG-NE6 | As per - Sub DB JEN-2 LLG
| Building E - Victoria University |  | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-DRC0.1 | As per - Sub DB JEN-2 LLG
|  | DB-1A-LLG-NE0.8 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-NE0.2 | As per - Sub DB JEN-2 LLG
|  | DB-2B-LLG-NE0.4 | As per - Sub DB JEN-2 LLG
|  | E-DB-1A-L05-DRC5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-1A-LLG-DRC0.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2A-L05-DRC5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2A-LLG-DRC0.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2A-L05-DRG5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L00-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L00-NE5.2 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L01-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L02-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L03-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L04-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L05-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-TDB-2B-L00-NE5.1 | As per - Sub DB JEN-2 LLG
|  | E-TDB-2B-L00-NE5.2 | As per - Sub DB JEN-2 LLG
|  | E-TDB-2B-L00-NE5.3 | As per - Sub DB JEN-2 LLG
|  | E-MDB-2B-LLG-NE5 | As per - Sub DB JEN-2 LLG
|  | E-DB-2B-L05-PV5.1 | As per - Sub DB JEN-2 LLG

## Main Switch Boards
MSB Installation
Main Switch Boards
| MSB-1A-LB1-DR | AE-ITCX-012 - MEN & MSB Meter Panel Checklist (Rev 0 +Names)
AE-ITCX-011 - Main Switchboard Inspection Sheet (Rev 0 +Names)
| MSB-1A-LB1-ES | As per MSB-1A-LB1-DR
| MSB-1A-LB1-EM | As per MSB-1A-LB1-DR
| MSB-1A-LB1-ME | As per MSB-1A-LB1-DR
| MSB-1A-LB1-NE | As per MSB-1A-LB1-DR
| MSB-1B-LB1-LS | As per MSB-1A-LB1-DR
| MSB-1B-LB1-ES | As per MSB-1A-LB1-DR
| MSB-1B-LB1-EM | As per MSB-1A-LB1-DR
| MSB-1B-LB1-ME | As per MSB-1A-LB1-DR
| MSB-1B-LB1-CR | As per MSB-1A-LB1-DR
| MSB-2A-LB1-DR | As per MSB-1A-LB1-DR
| MSB-2A-LB1-ME | As per MSB-1A-LB1-DR
| MSB-2A-LB1-ES | As per MSB-1A-LB1-DR
| MSB-2A-LB1-EM | As per MSB-1A-LB1-DR
| MSB-2B-LB1-LS | As per MSB-1A-LB1-DR
| MSB-2B-LB1-NE | As per MSB-1A-LB1-DR
| MSB-2B-LB1-EM | As per MSB-1A-LB1-DR
| MSB-2B-LB1-CR | As per MSB-1A-LB1-DR
| MSB-2B-LB1-ES | As per MSB-1A-LB1-DR

## Cable Tray
Tray Installation QA
Cable Tray
| Zone A | IPU | Basement 2 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Basement 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Lower Ground | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Ground floor | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 2 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 3 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 4 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 5 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 6 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 7 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 8 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 9 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 10 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 11 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 12 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
| Zone B | Sub - Acute | Basement 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Lower Ground | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Ground floor | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 2 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 3 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 4 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 5 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
| Zone C | Carpark Levels. | Lower Ground | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Lower Ground Mezz | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  | Building C - Carpark Building | Ground Floor | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 2 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 3 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 4 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 5 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  | Building D - Tiernan Commercial | Ground Floor | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 2 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 3 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 4 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 5 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  | Building E - Victoria University | Ground Floor | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 1 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 2 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 3 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 4 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)
|  |  | Level 5 | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names)

## Take of Boxes
TOB QA
| TOB | Building A
TOB-2A-L00-EM4.1
AE-ITCX-013 - T-Off Visual Inspection Test (Rev 0 +Names)
AE-ITCX-010 - Torque Settings for Bolts (Rev 0 +Names)
TOB-1A-L01-DRC3.1/2
|  |  | TOB-1A-L03-DRC3.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L03-DRC3.3 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L01-DRC4.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L03-DRC4.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L03-DRC4.3 | As per - TOB-2A-L00-EM4.1
Building B
|  |  | TOB-1A-L00-DRC1.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L00-DRC1.3/4 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L00-DRC1.5 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L02-DRC1.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L04-DRC1.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L04-DRC1.3/4 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L06-DRC1.1 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L09-DRC1.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L00-EM1.1 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1A-L04-EM1.1 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-1B-L09-EM1.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L00-DRC2.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L00-DRC2.3 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L00-DRC4.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L02-DRC2.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L04-DRC2.1/2 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L04-DRC2.3/4 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L06-DRC2.1 | As per - TOB-2A-L00-EM4.1
|  |  | TOB-2A-L09-DRC2.1/2 | As per - TOB-2A-L00-EM4.1
Building C
|  |  | C-TOB-1A-L01-NE7.1 | As per - TOB-2A-L00-EM4.1
|  |  | C-TOB-1A-L03-NE7.1 | As per - TOB-2A-L00-EM4.1
Building D
|  |  | D-TOB-1A-LLG-NE6.1 | As per - TOB-2A-L00-EM4.1
|  |  | D-TOB-1A-LLG-NE6.2 | As per - TOB-2A-L00-EM4.1
Building E
|  |  | E-TOB-1A-LLG-DRC0.1 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2A-LLG-DRC0.1 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2B-L00-NE5.1 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2B-L00-NE5.2 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2B-L01-NE5.1 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2B-L01-NE5.2 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2B-L03-NE5.1 | As per - TOB-2A-L00-EM4.1
|  |  | E-TOB-2B-L03-NE5.2 | As per - TOB-2A-L00-EM4.1

## Meter Panels
Meter Panel Installation
Meter Panels
| C-TDB-1A-L00-NE0.1 | AE-ITCX-014 - Meter Panel Visual Inspection Checklist (Rev 0 +Names)
AE-ITCX-015 - Mandatory Test Results (Rev 1 +Names)
AE-ITCX-010 - Torque Settings for Bolts (Rev 0 +Names)
C-TDB-1A-L00-NE0.2
C-TDB-1A-L00-NE0.3
D-TDB-1A-LLG-NE6.1
D-TDB-1A-LLG-NE6.2
D-TDB-1A-LLG-NE6.3
D-TDB-1A-L00-NE6.4
D-TDB-1A-L00-NE6.5
D-TDB-1A-L01-NE6.1
D-TDB-1A-L02-NE6.1
D-TDB-1A-L03-NE6.1
D-TDB-1A-L04-NE6.1
E-TDB-2B-L00-NE5.1
E-TDB-2B-L00-NE5.2
E-TDB-2B-L00-NE5.3
TDB-2B-L00-NE4.1
TDB-2B-L01-NE4.1
TDB-2B-L04-NE4.1
D-MDB-1A-LLG-NE6
E-MDB-2B-LLG-NE5
NFH-HV-MSB 1
NFH-HV-MSB 2

## Mains Cables
Main Cable Install
| Mains Cables | PH1A
|  |  | 1A-DR-0.01 | AE-ITCX-009 - Mains Cabling Reticulation Test Sheet (Rev 1 +Names)
AE-ITCX-010 - Torque Settings for Bolts (Rev 1 +Names)
|  |  | 1A-DR-0.02 | As per - 1A-DR.01
|  |  | 1A-DR-0.03 | As per - 1A-DR.01
|  |  | 1A-DR-0.04 | As per - 1A-DR.01
|  |  | 1A-DR-0.05 | As per - 1A-DR.01
|  |  | 1A-DRC-0.30 | As per - 1A-DR.01
|  |  | 1A-DRC-0.31 | As per - 1A-DR.01
|  |  | 1A-DRC-0.32 | As per - 1A-DR.01
|  |  | 1A-DRC-0.36 | As per - 1A-DR.01
|  |  | 1A-DRC-0.36.1 | As per - 1A-DR.01
|  |  | 1A-DRC-5.36.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.01 | As per - 1A-DR.01
|  |  | 1A-DRC-1.01.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.01.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.02 | As per - 1A-DR.01
|  |  | 1A-DRC-1.02.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.02.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.02.3 | As per - 1A-DR.01
|  |  | 1A-DRC-1.03 | As per - 1A-DR.01
|  |  | 1A-DRC-1.03.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.03.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.03.3 | As per - 1A-DR.01
|  |  | 1A-DRC-1.09 | As per - 1A-DR.01
|  |  | 1A-DRC-1.09.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.09.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.09.3 | As per - 1A-DR.01
|  |  | 1A-DRC-1.09.3 | As per - 1A-DR.01
|  |  | 1A-DRC-1.14 | As per - 1A-DR.01
|  |  | 1A-DRC-1.14.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.14.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.14.3 | As per - 1A-DR.01
|  |  | 1A-DRC-1.15 | As per - 1A-DR.01
|  |  | 1A-DRC-1.15.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.15.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.15.3 | As per - 1A-DR.01
|  |  | 1A-DRC-0.20 | As per - 1A-DR.01
|  |  | 1A-DRC-1.25 | As per - 1A-DR.01
|  |  | 1A-DRC-1.25.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.25.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.27 | As per - 1A-DR.01
|  |  | 1A-DRC-1.27.1 | As per - 1A-DR.01
|  |  | 1A-DRC-1.27.2 | As per - 1A-DR.01
|  |  | 1A-DRC-1.27.3 | As per - 1A-DR.01
|  |  | 1A-DRC-3.04 | As per - 1A-DR.01
|  |  | 1A-DRC-3.04.1 | As per - 1A-DR.01
|  |  | 1A-DRC-3.04.2 | As per - 1A-DR.01
|  |  | 1A-DRC-3.04.3 | As per - 1A-DR.01
|  |  | 1A-DRC-3.12 | As per - 1A-DR.01
|  |  | 1A-DRC-3.12.1 | As per - 1A-DR.01
|  |  | 1A-DRC-3.12.2 | As per - 1A-DR.01
|  |  | 1A-DRC-3.12.3 | As per - 1A-DR.01
|  |  | 1A-DRC-3.17 | As per - 1A-DR.01
|  |  | 1A-DRC-3.17.1 | As per - 1A-DR.01
|  |  | 1A-DRC-3.17.2 | As per - 1A-DR.01
|  |  | 1A-DRC-3.22 | As per - 1A-DR.01
|  |  | 1A-DRC-7.38 | As per - 1A-DR.01
|  |  | 1A-DRCR-0.01 | As per - 1A-DR.01
|  |  | 1A-DRCR-STS-0.01 | As per - 1A-DR.01
|  |  | 1A-DRCR-0.05 | As per - 1A-DR.01
|  |  | 1A-DRCR-STS-0.05 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.01.1 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.01.2 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.01.3 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.02 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.03 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.04 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.05.1 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.05.2 | As per - 1A-DR.01
|  |  | 1A-DRCR-1.05.3 | As per - 1A-DR.01
|  |  | 1A-DRG-0.14 | As per - 1A-DR.01
|  |  | 1A-DRG-0.15 | As per - 1A-DR.01
|  |  | 1A-DRG-1.01 | As per - 1A-DR.01
|  |  | 1A-DRG-1.03 | As per - 1A-DR.01
|  |  | 1A-DRG-1.04 | As per - 1A-DR.01
|  |  | 1A-DRG-1.05 | As per - 1A-DR.01
|  |  | 1A-DRG-1.06 | As per - 1A-DR.01
|  |  | 1A-DRG-1.08 | As per - 1A-DR.01
|  |  | 1A-DRG-1.09 | As per - 1A-DR.01
|  |  | 1A-DRG-1.10 | As per - 1A-DR.01
|  |  | 1A-DRG-1.11 | As per - 1A-DR.01
|  |  | 1A-DRG-1.12 | As per - 1A-DR.01
|  |  | 1A-DRG-1.13 | As per - 1A-DR.01
|  |  | 1A-DRG-1.16 | As per - 1A-DR.01
|  |  | 1A-EM-1.01 | As per - 1A-DR.01
|  |  | 1A-EM-1.02 | As per - 1A-DR.01
|  |  | 1A-EM-1.03 | As per - 1A-DR.01
|  |  | 1A-EM-1.04 | As per - 1A-DR.01
|  |  | 1A-EM-1.04.1 | As per - 1A-DR.01
|  |  | 1A-EM-1.04.2 | As per - 1A-DR.01
|  |  | 1A-EM-1.07 | As per - 1A-DR.01
|  |  | 1A-EM-1.09 | As per - 1A-DR.01
|  |  | 1A-EM-1.09.1 | As per - 1A-DR.01
|  |  | 1A-EM-1.09.2 | As per - 1A-DR.01
|  |  | 1A-EM-1.15 | As per - 1A-DR.01
|  |  | 1A-EM-1.16 | As per - 1A-DR.01
|  |  | 1A-EM-2.08 | As per - 1A-DR.01
|  |  | 1A-EM-2.11 | As per - 1A-DR.01
|  |  | 1A-EM-2.14 | As per - 1A-DR.01
|  |  | 1A-ES-7.18 | As per - 1A-DR.01
|  |  | 1A-ES-1.01 | As per - 1A-DR.01
|  |  | 1A-ES-1.02 | As per - 1A-DR.01
|  |  | 1A-ES-1.03 | As per - 1A-DR.01
|  |  | 1A-ES-1.04 | As per - 1A-DR.01
|  |  | 1A-ES-1.05 | As per - 1A-DR.01
|  |  | 1A-ES-1.06 | As per - 1A-DR.01
|  |  | 1A-ES-1.07 | As per - 1A-DR.01
|  |  | 1A-ES-1.08 | As per - 1A-DR.01
|  |  | 1A-ES-1.10 | As per - 1A-DR.01
|  |  | 1A-ES-1.12 | As per - 1A-DR.01
|  |  | 1A-ES-1.13 | As per - 1A-DR.01
|  |  | 1A-ES-1.14 | As per - 1A-DR.01
|  |  | 1A-ES-1.15 | As per - 1A-DR.01
|  |  | 1A-ES-1.16 | As per - 1A-DR.01
|  |  | 1A-ES-1.17 | As per - 1A-DR.01
|  |  | 1A-ME-0.02 | As per - 1A-DR.01
|  |  | 1A-ME-0.03 | As per - 1A-DR.01
|  |  | 1A-ME-0.04 | As per - 1A-DR.01
|  |  | 1A-ME-1.01 | As per - 1A-DR.01
|  |  | 1A-NE-7.40 | As per - 1A-DR.01
|  |  | 1A-NE-7.10 | As per - 1A-DR.01
|  |  | 1A-NE-0.09 | As per - 1A-DR.01
|  |  | 1A-NE-0.12 | As per - 1A-DR.01
|  |  | 1A-NE-0.13 | As per - 1A-DR.01
|  |  | 1A-NE-0.19 | As per - 1A-DR.01
|  |  | 1A-NE-0.21 | As per - 1A-DR.01
|  |  | 1A-NE-0.22 | As per - 1A-DR.01
|  |  | 1A-NE-0.23 | As per - 1A-DR.01
|  |  | 1A-NE-0.25 | As per - 1A-DR.01
|  |  | 1A-NE-0.26 | As per - 1A-DR.01
|  |  | 1A-NE-0.29 | As per - 1A-DR.01
|  |  | 1A-NE-0.30 | As per - 1A-DR.01
|  |  | 1A-NE-0.31 | As per - 1A-DR.01
|  |  | 1A-NE-0.32 | As per - 1A-DR.01
|  |  | 1A-NE-0.36 | As per - 1A-DR.01
|  |  | 1A-NE-1.03 | As per - 1A-DR.01
|  |  | 1A-NE-1.04 | As per - 1A-DR.01
|  |  | 1A-NE-1.05 | As per - 1A-DR.01
|  |  | 1A-NE-1.06 | As per - 1A-DR.01
|  |  | 1A-NE-1.07 | As per - 1A-DR.01
|  |  | 1A-NE-1.08 | As per - 1A-DR.01
|  |  | 1A-NE-1.27 | As per - 1A-DR.01
|  |  | 1A-NE-2.02 | As per - 1A-DR.01
|  |  | 1A-NE-2.37 | As per - 1A-DR.01
|  |  | 1A-NE-7.01 | As per - 1A-DR.01
|  |  | 1A-NE-7.14 | As per - 1A-DR.01
|  |  | 1A-NE-7.15 | As per - 1A-DR.01
|  |  | 1A-NE-7.16 | As per - 1A-DR.01
|  |  | 1A-NE-7.17 | As per - 1A-DR.01
|  |  | 1A-NE-7.18 | As per - 1A-DR.01
|  |  | 1A-NE-7.20 | As per - 1A-DR.01
|  |  | 1A-NE-7.24 | As per - 1A-DR.01
PH1B
|  |  | 1B-CR-0.05 | As per - 1A-DR.01
|  |  | 1B-CR-0.06 | As per - 1A-DR.01
|  |  | 1B-CR-0.07 | As per - 1A-DR.01
|  |  | 1B-CR-0.13 | As per - 1A-DR.01
|  |  | 1B-CR-0.14 | As per - 1A-DR.01
|  |  | 1B-CR-0.17 | As per - 1A-DR.01
|  |  | 1B-CR-0.19 | As per - 1A-DR.01
|  |  | 1B-CR-1.03 | As per - 1A-DR.01
|  |  | 1B-CR-1.12 | As per - 1A-DR.01
|  |  | 1B-CR-1.20 | As per - 1A-DR.01
|  |  | 1B-EM-0.06 | As per - 1A-DR.01
|  |  | 1B-EM-0.16 | As per - 1A-DR.01
|  |  | 1B-EM-1.01 | As per - 1A-DR.01
|  |  | 1B-EM-1.02 | As per - 1A-DR.01
|  |  | 1B-EM-1.05 | As per - 1A-DR.01
|  |  | 1B-EM-1.05.1 | As per - 1A-DR.01
|  |  | 1B-EM-1.05.2 | As per - 1A-DR.01
|  |  | 1B-EM-1.05.3 | As per - 1A-DR.01
|  |  | 1B-EM-2.04 | As per - 1A-DR.01
|  |  | 1B-ES-1.01 | As per - 1A-DR.01
|  |  | 1B-ES-1.02 | As per - 1A-DR.01
|  |  | 1B-ES-1.03 | As per - 1A-DR.01
|  |  | 1B-ES-1.04 | As per - 1A-DR.01
|  |  | 1B-ES-1.05 | As per - 1A-DR.01
|  |  | 1B-ES-1.06 | As per - 1A-DR.01
|  |  | 1B-ES-1.08 | As per - 1A-DR.01
|  |  | 1B-ES-1.10 | As per - 1A-DR.01
|  |  | 1B-ES-1.11 | As per - 1A-DR.01
|  |  | 1B-ES-1.12 | As per - 1A-DR.01
|  |  | 1B-ES-1.13 | As per - 1A-DR.01
|  |  | 1B-ES-1.14 | As per - 1A-DR.01
|  |  | 1B-ES-1.15 | As per - 1A-DR.01
|  |  | 1B-LS-0.15 | As per - 1A-DR.01
|  |  | 1B-LS-0.25 | As per - 1A-DR.01
|  |  | 1B-LS-0.26 | As per - 1A-DR.01
|  |  | 1B-LS-0.27 | As per - 1A-DR.01
|  |  | 1B-LS-0.28 | As per - 1A-DR.01
|  |  | 1B-LS-0.63 | As per - 1A-DR.01
|  |  | 1B-LS-0.66 | As per - 1A-DR.01
|  |  | 1B-LS-0.67 | As per - 1A-DR.01
|  |  | 1B-LS-1.03 | As per - 1A-DR.01
|  |  | 1B-LS-1.04 | As per - 1A-DR.01
|  |  | 1B-LS-1.05 | As per - 1A-DR.01
|  |  | 1B-LS-1.06 | As per - 1A-DR.01
|  |  | 1B-LS-1.07 | As per - 1A-DR.01
|  |  | 1B-LS-1.08 | As per - 1A-DR.01
|  |  | 1B-LS-1.09 | As per - 1A-DR.01
|  |  | 1B-LS-1.10 | As per - 1A-DR.01
|  |  | 1B-LS-1.16 | As per - 1A-DR.01
|  |  | 1B-LS-1.17 | As per - 1A-DR.01
|  |  | 1B-LS-1.18 | As per - 1A-DR.01
|  |  | 1B-LS-1.19 | As per - 1A-DR.01
|  |  | 1B-LS-1.20 | As per - 1A-DR.01
|  |  | 1B-LS-1.21 | As per - 1A-DR.01
|  |  | 1B-LS-1.22 | As per - 1A-DR.01
|  |  | 1B-LS-1.23 | As per - 1A-DR.01
|  |  | 1B-LS-1.29 | As per - 1A-DR.01
|  |  | 1B-LS-1.31 | As per - 1A-DR.01
|  |  | 1B-LS-1.32 | As per - 1A-DR.01
|  |  | 1B-LS-1.33 | As per - 1A-DR.01
|  |  | 1B-LS-1.34 | As per - 1A-DR.01
|  |  | 1B-LS-1.35 | As per - 1A-DR.01
|  |  | 1B-LS-1.36 | As per - 1A-DR.01
|  |  | 1B-LS-1.37 | As per - 1A-DR.01
|  |  | 1B-LS-1.38 | As per - 1A-DR.01
|  |  | 1B-LS-1.39 | As per - 1A-DR.01
|  |  | 1B-LS-1.40 | As per - 1A-DR.01
|  |  | 1B-LS-1.41 | As per - 1A-DR.01
|  |  | 1B-LS-1.42 | As per - 1A-DR.01
|  |  | 1B-LS-1.43 | As per - 1A-DR.01
|  |  | 1B-LS-1.44 | As per - 1A-DR.01
|  |  | 1B-LS-1.45 | As per - 1A-DR.01
|  |  | 1B-LS-1.46 | As per - 1A-DR.01
|  |  | 1B-LS-1.47 | As per - 1A-DR.01
|  |  | 1B-LS-1.48 | As per - 1A-DR.01
|  |  | 1B-LS-1.49 | As per - 1A-DR.01
|  |  | 1B-LS-1.50 | As per - 1A-DR.01
|  |  | 1B-LS-1.51 | As per - 1A-DR.01
|  |  | 1B-LS-1.52 | As per - 1A-DR.01
|  |  | 1B-LS-1.53 | As per - 1A-DR.01
|  |  | 1B-LS-1.54 | As per - 1A-DR.01
|  |  | 1B-LS-1.55 | As per - 1A-DR.01
|  |  | 1B-LS-1.62 | As per - 1A-DR.01
|  |  | 1B-LS-1.64 | As per - 1A-DR.01
|  |  | 1B-LS-1.65 | As per - 1A-DR.01
|  |  | 1B-LS-4.30 | As per - 1A-DR.01
|  |  | 1B-LS-6.56 | As per - 1A-DR.01
|  |  | 1B-LS-6.57 | As per - 1A-DR.01
|  |  | 1B-LS-6.58 | As per - 1A-DR.01
|  |  | 1B-LS-6.59 | As per - 1A-DR.01
|  |  | 1B-LS-6.60 | As per - 1A-DR.01
|  |  | 1B-LS-6.61 | As per - 1A-DR.01
|  |  | 1B-LS-7.01 | As per - 1A-DR.01
|  |  | 1B-LS-7.02 | As per - 1A-DR.01
|  |  | 1B-LS-7.11 | As per - 1A-DR.01
|  |  | 1B-LS-7.12 | As per - 1A-DR.01
|  |  | 1B-LS-7.13 | As per - 1A-DR.01
|  |  | 1B-LS-7.14 | As per - 1A-DR.01
|  |  | 1B-ME-0.02 | As per - 1A-DR.01
|  |  | 1B-ME-0.03 | As per - 1A-DR.01
|  |  | 1B-ME-0.04 | As per - 1A-DR.01
|  |  | 1B-ME-0.05 | As per - 1A-DR.01
|  |  | 1B-ME-1.01 | As per - 1A-DR.01
|  |  | 1B-ME-7.06 | As per - 1A-DR.01
PH2A
|  |  | 2A.DR-0.03 | As per - 1A-DR.01
|  |  | 2A.DR-0.04 | As per - 1A-DR.01
|  |  | 2A-DR-0.01 | As per - 1A-DR.01
|  |  | 2A-DR-0.02 | As per - 1A-DR.01
|  |  | 2A-DR-0.05 | As per - 1A-DR.01
|  |  | 2A-DR-4.06 | As per - 1A-DR.01
|  |  | 2A-DRC-0.30 | As per - 1A-DR.01
|  |  | 2A-DRC-0.31 | As per - 1A-DR.01
|  |  | 2A-DRC-0.32 | As per - 1A-DR.01
|  |  | 2A-DRC-0.36 | As per - 1A-DR.01
|  |  | 2A-DRC-0.36.1 | As per - 1A-DR.01
|  |  | 2A-DRC-5.36.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.01 | As per - 1A-DR.01
|  |  | 2A-DRC-2.01.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.01.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.02 | As per - 1A-DR.01
|  |  | 2A-DRC-2.02.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.02.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.02.3 | As per - 1A-DR.01
|  |  | 2A-DRC-2.09 | As per - 1A-DR.01
|  |  | 2A-DRC-2.09.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.09.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.09.3 | As per - 1A-DR.01
|  |  | 2A-DRC-2.14 | As per - 1A-DR.01
|  |  | 2A-DRC-2.14.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.14.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.14.3 | As per - 1A-DR.01
|  |  | 2A-DRC-2.15 | As per - 1A-DR.01
|  |  | 2A-DRC-2.15.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.15.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.15.3 | As per - 1A-DR.01
|  |  | 2A-DRC-0.20 | As per - 1A-DR.01
|  |  | 2A-DRC-2.25 | As per - 1A-DR.01
|  |  | 2A-DRC-2.25.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.25.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.27 | As per - 1A-DR.01
|  |  | 2A-DRC-2.27.1 | As per - 1A-DR.01
|  |  | 2A-DRC-2.27.2 | As per - 1A-DR.01
|  |  | 2A-DRC-2.27.3 | As per - 1A-DR.01
|  |  | 2A-DRC-4.03 | As per - 1A-DR.01
|  |  | 2A-DRC-4.03.1 | As per - 1A-DR.01
|  |  | 2A-DRC-4.03.2 | As per - 1A-DR.01
|  |  | 2A-DRC-4.03.3 | As per - 1A-DR.01
|  |  | 2A-DRC-4.04 | As per - 1A-DR.01
|  |  | 2A-DRC-4.04.1 | As per - 1A-DR.01
|  |  | 2A-DRC-4.04.2 | As per - 1A-DR.01
|  |  | 2A-DRC-4.04.3 | As per - 1A-DR.01
|  |  | 2A-DRC-4.13 | As per - 1A-DR.01
|  |  | 2A-DRC-4.13.1 | As per - 1A-DR.01
|  |  | 2A-DRC-4.13.2 | As per - 1A-DR.01
|  |  | 2A-DRC-4.13.3 | As per - 1A-DR.01
|  |  | 2A-DRC-4.17 | As per - 1A-DR.01
|  |  | 2A-DRC-4.17.1 | As per - 1A-DR.01
|  |  | 2A-DRC-4.17.2 | As per - 1A-DR.01
|  |  | 2A-DRC-4.22 | As per - 1A-DR.01
|  |  | 2A-DRC-7.38 | As per - 1A-DR.01
|  |  | 2A-DRCR-0.01 | As per - 1A-DR.01
|  |  | 2A-DRCR-STS0.1 | As per - 1A-DR.01
|  |  | 2A-DRCR-0.05 | As per - 1A-DR.01
|  |  | 2A-DRCR-STS0.2 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.01.1 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.01.2 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.01.3 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.02 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.03 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.04 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.05.1 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.05.2 | As per - 1A-DR.01
|  |  | 2A-DRCR-2.05.3 | As per - 1A-DR.01
|  |  | 2A-DRG-0.11 | As per - 1A-DR.01
|  |  | 2A-DRG-0.09 | As per - 1A-DR.01
|  |  | 2A-DRG-4.02 | As per - 1A-DR.01
|  |  | 2A-DRG-2.04 | As per - 1A-DR.01
|  |  | 2A-DRG-2.06 | As per - 1A-DR.01
|  |  | 2A-DRG-4.01 | As per - 1A-DR.01
|  |  | 2A-DRG-4.03 | As per - 1A-DR.01
|  |  | 2A-DRG-4.05 | As per - 1A-DR.01
|  |  | 2A-DRG-4.07 | As per - 1A-DR.01
|  |  | 2A-DRG-4.08 | As per - 1A-DR.01
|  |  | 2A-DRG-5.10 | As per - 1A-DR.01
|  |  | 2A-EM-1.13 | As per - 1A-DR.01
|  |  | 2A-EM-2.04 | As per - 1A-DR.01
|  |  | 2A-EM-4.01 | As per - 1A-DR.01
|  |  | 2A-EM-4.02 | As per - 1A-DR.01
|  |  | 2A-EM-4.03 | As per - 1A-DR.01
|  |  | 2A-EM-4.03.1 | As per - 1A-DR.01
|  |  | 2A-EM-4.03.2 | As per - 1A-DR.01
|  |  | 2A-EM-4.05 | As per - 1A-DR.01
|  |  | 2A-EM-4.06 | As per - 1A-DR.01
|  |  | 2A-EM-4.08 | As per - 1A-DR.01
|  |  | 2A-EM-4.10 | As per - 1A-DR.01
|  |  | 2A-EM-4.11 | As per - 1A-DR.01
|  |  | 2A-EM-4.14 | As per - 1A-DR.01
|  |  | 2A-ES-2.04 | As per - 1A-DR.01
|  |  | 2A-ES-2.07 | As per - 1A-DR.01
|  |  | 2A-ES-4.01 | As per - 1A-DR.01
|  |  | 2A-ES-4.02 | As per - 1A-DR.01
|  |  | 2A-ES-4.03 | As per - 1A-DR.01
|  |  | 2A-ES-4.05 | As per - 1A-DR.01
|  |  | 2A-ES-4.06 | As per - 1A-DR.01
|  |  | 2A-ES-4.10 | As per - 1A-DR.01
|  |  | 2A-ME-0.04 | As per - 1A-DR.01
|  |  | 2A-ME-0.05 | As per - 1A-DR.01
|  |  | 2A-ME-1.03 | As per - 1A-DR.01
|  |  | 2A-PV4.1 | As per - 1A-DR.01
|  |  | 2A-PV4.2 | As per - 1A-DR.01
|  |  | 2A-PV4.3 | As per - 1A-DR.01
|  |  | 2A-TX2.A1 | As per - 1A-DR.01
|  |  | 2A-TX2.A2 | As per - 1A-DR.01
|  |  | 2A-STS-0.1 | As per - 1A-DR.01
|  |  | 2A-STS-0.2 | As per - 1A-DR.01
PH2B
|  |  | 2B-CR-0.03 | As per - 1A-DR.01
|  |  | 2B-CR-0.06 | As per - 1A-DR.01
|  |  | 2B-CR-0.07 | As per - 1A-DR.01
|  |  | 2B-CR-0.08 | As per - 1A-DR.01
|  |  | 2B-CR-0.11 | As per - 1A-DR.01
|  |  | 2B-CR-0.13 | As per - 1A-DR.01
|  |  | 2B-CR-0.17 | As per - 1A-DR.01
|  |  | 2B-CR-1.15 | As per - 1A-DR.01
|  |  | 2B-CR-1.16 | As per - 1A-DR.01
|  |  | 2B-CR-1.19 | As per - 1A-DR.01
|  |  | 2B-CR-1.20 | As per - 1A-DR.01
|  |  | 2B-CR-1.22 | As per - 1A-DR.01
|  |  | 2B-CR-1.23 | As per - 1A-DR.01
|  |  | 2B-CR-1.24 | As per - 1A-DR.01
|  |  | 2B-CR-2.02 | As per - 1A-DR.01
|  |  | 2B-CR-2.10 | As per - 1A-DR.01
|  |  | 2B-CR-4.01 | As per - 1A-DR.01
|  |  | 2B-CR-4.09 | As per - 1A-DR.01
|  |  | 2B-CR-4.12 | As per - 1A-DR.01
|  |  | 2B-CR-4.21 | As per - 1A-DR.01
|  |  | 2B-CR-4.25 | As per - 1A-DR.01
|  |  | 2B-EM-2.02 | As per - 1A-DR.01
|  |  | 2B-EM-2.04 | As per - 1A-DR.01
|  |  | 2B-EM-4.01 | As per - 1A-DR.01
|  |  | 2B-EM-4.03 | As per - 1A-DR.01
|  |  | 2B-EM-4.05 | As per - 1A-DR.01
|  |  | 2B-EM-4.06 | As per - 1A-DR.01
|  |  | 2B-EM-4.07 | As per - 1A-DR.01
|  |  | 2B-EM-4.08 | As per - 1A-DR.01
|  |  | 2B-EM-4.09 | As per - 1A-DR.01
|  |  | 2B-EM-4.10 | As per - 1A-DR.01
|  |  | 2B-EM-4.11 | As per - 1A-DR.01
|  |  | 2B-EM-4.13 | As per - 1A-DR.01
|  |  | 2B-EM-5.14 | As per - 1A-DR.01
|  |  | 2B-ES-2.03 | As per - 1A-DR.01
|  |  | 2B-ES-2.05 | As per - 1A-DR.01
|  |  | 2B-ES-2.07 | As per - 1A-DR.01
|  |  | 2B-ES-2.08 | As per - 1A-DR.01
|  |  | 2B-ES-4.01 | As per - 1A-DR.01
|  |  | 2B-ES-4.02 | As per - 1A-DR.01
|  |  | 2B-ES-4.04 | As per - 1A-DR.01
|  |  | 2B-ES-4.06 | As per - 1A-DR.01
|  |  | 2B-LS-0.28 | As per - 1A-DR.01
|  |  | 2B-LS-0.29 | As per - 1A-DR.01
|  |  | 2B-LS-0.39 | As per - 1A-DR.01
|  |  | 2B-LS-0.40 | As per - 1A-DR.01
|  |  | 2B-LS-0.41 | As per - 1A-DR.01
|  |  | 2B-LS-0.42 | As per - 1A-DR.01
|  |  | 2B-LS-2.03 | As per - 1A-DR.01
|  |  | 2B-LS-0.30 | As per - 1A-DR.01
|  |  | 2B-LS-0.31 | As per - 1A-DR.01
|  |  | 2B-LS-0.32 | As per - 1A-DR.01
|  |  | 2B-LS-3.33 | As per - 1A-DR.01
|  |  | 2B-LS-3.34 | As per - 1A-DR.01
|  |  | 2B-LS-3.35 | As per - 1A-DR.01
|  |  | 2B-LS-3.36 | As per - 1A-DR.01
|  |  | 2B-LS-4.37 | As per - 1A-DR.01
|  |  | 2B-LS-4.38 | As per - 1A-DR.01
|  |  | 2B-LS-4.46 | As per - 1A-DR.01
|  |  | 2B-LS-4.01 | As per - 1A-DR.01
|  |  | 2B-LS-4.02 | As per - 1A-DR.01
|  |  | 2B-LS-4.04 | As per - 1A-DR.01
|  |  | 2B-LS-4.05 | As per - 1A-DR.01
|  |  | 2B-LS-4.06 | As per - 1A-DR.01
|  |  | 2B-LS-4.11 | As per - 1A-DR.01
|  |  | 2B-LS-4.13 | As per - 1A-DR.01
|  |  | 2B-LS-4.14 | As per - 1A-DR.01
|  |  | 2B-LS-4.15 | As per - 1A-DR.01
|  |  | 2B-LS-4.16 | As per - 1A-DR.01
|  |  | 2B-LS-4.17 | As per - 1A-DR.01
|  |  | 2B-LS-4.18 | As per - 1A-DR.01
|  |  | 2B-LS-4.19 | As per - 1A-DR.01
|  |  | 2B-LS-4.20 | As per - 1A-DR.01
|  |  | 2B-LS-4.21 | As per - 1A-DR.01
|  |  | 2B-LS-4.22 | As per - 1A-DR.01
|  |  | 2B-LS-4.24 | As per - 1A-DR.01
|  |  | 2B-LS-4.43 | As per - 1A-DR.01
|  |  | 2B-LS-5.23 | As per - 1A-DR.01
|  |  | 2B-LS-5.25 | As per - 1A-DR.01
|  |  | 2B-LS-5.26 | As per - 1A-DR.01
|  |  | 2B-LS-5.27 | As per - 1A-DR.01
|  |  | 2B-NE-0.02 | As per - 1A-DR.01
|  |  | 2B-NE-0.11 | As per - 1A-DR.01
|  |  | 2B-NE-0.18 | As per - 1A-DR.01
|  |  | 2B-NE-0.19 | As per - 1A-DR.01
|  |  | 2B-NE-0.20 | As per - 1A-DR.01
|  |  | 2B-NE-0.21 | As per - 1A-DR.01
|  |  | 2B-NE-0.22 | As per - 1A-DR.01
|  |  | 2B-NE-0.23 | As per - 1A-DR.01
|  |  | 2B-NE-4.04 | As per - 1A-DR.01
|  |  | 2B-NE-4.05 | As per - 1A-DR.01
|  |  | 2B-NE-4.07 | As per - 1A-DR.01
|  |  | 2B-NE-4.09 | As per - 1A-DR.01
|  |  | 2B-NE-4.10 | As per - 1A-DR.01
|  |  | 2B-NE-4.14 | As per - 1A-DR.01
|  |  | 2B-NE-4.17 | As per - 1A-DR.01
|  |  | E-2B-PV5.1 | As per - 1A-DR.01
|  |  | E-2B-NE-0.03 | As per - 1A-DR.01
|  |  | E-2B-NE-5.04 | As per - 1A-DR.01
|  |  | E-2B-NE-5.05 | As per - 1A-DR.01
|  |  | E-2B-NE-0.06 | As per - 1A-DR.01
|  |  | E-2B-NE-5.07 | As per - 1A-DR.01
|  |  | E-2B-NE-5.08 | As per - 1A-DR.01
|  |  | E-2B-NE-5.10 | As per - 1A-DR.01
|  |  | E-2B-NE-5.10 | As per - 1A-DR.01
|  |  | E-2B-NE-5.10.1 | As per - 1A-DR.01
|  |  | E-2B-NE-5.10.2 | As per - 1A-DR.01
|  |  | E-2B-NE-5.10.3 | As per - 1A-DR.01
|  |  | E-2B-NE-5.10.4 | As per - 1A-DR.01
|  |  | E-2B-NE-5.09 | As per - 1A-DR.01
|  |  | E-2B-NE-5.09.1 | As per - 1A-DR.01
|  |  | E-2B-NE-5.09.1 | As per - 1A-DR.01
|  |  | E-2B-NE-5.09.2 | As per - 1A-DR.01
|  |  | E-2B-NE-5.13 | As per - 1A-DR.01
|  |  | E-2B-NE-5.13.1 | As per - 1A-DR.01
|  |  | E-2B-NE-5.13.2 | As per - 1A-DR.01
|  |  | E-2B-NE-5.01 | As per - 1A-DR.01
|  |  | E-2B-NE-5.01.1 | As per - 1A-DR.01
|  |  | E-2B-NE-5.01.2 | As per - 1A-DR.01
|  |  | E-2B-NE-5.02 | As per - 1A-DR.01
|  |  | E-2B-NE-5.02.1 | As per - 1A-DR.01
|  |  | E-2B-NE-5.02.2 | As per - 1A-DR.01
|  |  | 2B-TX2.B1 | As per - 1A-DR.01
|  |  | 2B-TX2.B2 | As per - 1A-DR.01
HV Feed
|  |  | HV-01 | AE-ITCX-007 - Conduit Checklist (Rev 0 +Names)
AE-ITCX-009 - Mains Cabling Reticulation Test Sheet (Rev 1 +Names)
AE-ITCX-015 - Mandatory Test Results (Rev 1 +Names)
AE-ITCX-010 - Torque Settings for Bolts (Rev 1 +Names)
|  |  | HV-02 | As per 1 - HV-01
HV
|  |  | HV-RM-01 | As per - 1A-DR.01
|  |  | HV-RM-02 | As per - 1A-DR.01
|  |  | HV-RM-03 | As per - 1A-DR.01
|  |  | HV-RM-04 | As per - 1A-DR.01
|  |  | HV-RM-05 | As per - 1A-DR.01
|  |  | HV-RM-06 | As per - 1A-DR.01
|  |  | HV-RM-07 | As per - 1A-DR.01
|  |  | HV-RM-08 | As per - 1A-DR.01
|  |  | HV-TX-01 | As per - 1A-DR.01
|  |  | HV-TX-02 | As per - 1A-DR.01
|  |  | HV-TX-03 | As per - 1A-DR.01
|  |  | HV-TX-04 | As per - 1A-DR.01
|  |  | HV-TX-05 | As per - 1A-DR.01
|  |  | HV-TX-06 | As per - 1A-DR.01
|  |  | HV-TX-07 | As per - 1A-DR.01
|  |  | HV-TX-08 | As per - 1A-DR.01
|  |  | HV-TX-09 | As per - 1A-DR.01
Generators
|  |  | G1.A1 | As per 1 - 1A-DR.01
|  |  | G1.B1 | As per 1 - 1A-DR.01
|  |  | DRUPS 1 | As per 1 - 1A-DR.01
|  |  | TEMP.GEN | As per 1 - 1A-DR.01
|  |  | BUSTIE | As per 1 - 1A-DR.01
|  |  | G2.A1 | As per 1 - 1A-DR.01
|  |  | G2.B1 | As per 1 - 1A-DR.01
|  |  | DRUPS 2 | As per 1 - 1A-DR.01
|  | Keep info that’s already on Conqa | TX1 | Existing information in Conqa
|  |  | HV ring main | Existing information in Conqa

## BusDuct -DELETE-
BusDuct Installation
Busduct
| Generator: G1A & G1B | AE-ITCX-033 - Busduct Installation (Rev 0 +Names)
AE-ITCX-015 - Mandatory Test Results (Rev 1 +Names)
AE-ITCX-010 - Torque Settings for Bolts (Rev 0 +Names)
| G1.A1 | As per - Generator: G1A & G1B
| G1.A2 | As per - Generator: G1A & G1B
| BUSTIE | As per - Generator: G1A & G1B
| Generator: G2A & G2B | As per - Generator: G1A & G1B
| G2.A1 | As per - Generator: G1A & G1B
| G2.A2 | As per - Generator: G1A & G1B

## Communications
Communications
Communications
Basements
|  | FD-ZC-LLG.1 | AE-ITCX-024 - Communications/Security Rack Installation QA (Rev 0)
AE-ITCX-029 - Rough-In Checklist (Rev 0 +Names)
AE-ITCX-31 - Fit-Off General Checklist (Rev 0 +Names)
|  | FD-ZC-LLG.4 | As per - FD-ZC-LLG.1
|  | FD-ZC-LLG.2 | As per - FD-ZC-LLG.1
|  | FD-ZC-LLG.5 | As per - FD-ZC-LLG.1
|  | FD-ZC-LLG.3 | As per - FD-ZC-LLG.1
|  | FD-ZC-LLG.6 | As per - FD-ZC-LLG.1
|  | FD-E-LLG.1 | As per - FD-ZC-LLG.1
Building A - Sub Acute
|  | FD-ZC-LB1.1 | As per - FD-ZC-LLG.1
|  | FD-A-LB1.2 | As per - FD-ZC-LLG.1
|  | FD-A-L00.2 | As per - FD-ZC-LLG.1
|  | FD-A-L01.2 | As per - FD-ZC-LLG.1
|  | FD-A-L02.1 | As per - FD-ZC-LLG.1
|  | FD-A-L02.2 | As per - FD-ZC-LLG.1
|  | FB-A-L03.1 | As per - FD-ZC-LLG.1
|  | FD-A-L03.2 | As per - FD-ZC-LLG.1
|  | FD-A-L04.1 | As per - FD-ZC-LLG.1
|  | FD-A-L04.2 | As per - FD-ZC-LLG.1
|  | FD-A-L05.2 | As per - FD-ZC-LLG.1
| Building B - IPU | FD-B-LLG.2 | As per - FD-ZC-LLG.1
|  | FD-B-LB1.2 | As per - FD-ZC-LLG.1
|  | FD-B-LLG.3 | As per - FD-ZC-LLG.1
|  | FD-B-L00.1 | As per - FD-ZC-LLG.1
|  | FD-B-L00.3 | As per - FD-ZC-LLG.1
|  | FD-B-L00.2 | As per - FD-ZC-LLG.1
|  | FD-B-L01.1 | As per - FD-ZC-LLG.1
|  | FD-B-L01.3 | As per - FD-ZC-LLG.1
|  | FD-B-L01.2 | As per - FD-ZC-LLG.1
|  | FD-B-L02.1 | As per - FD-ZC-LLG.1
|  | FD-B-L02.3 | As per - FD-ZC-LLG.1
|  | FD-B-L02.2 | As per - FD-ZC-LLG.1
|  | FB-B-L03.1 | As per - FD-ZC-LLG.1
|  | FD-B-L03.2 | As per - FD-ZC-LLG.1
|  | FD-B-L04.1 | As per - FD-ZC-LLG.1
|  | FD-B-L04.2 | As per - FD-ZC-LLG.1
|  | FD-B-L05.1 | As per - FD-ZC-LLG.1
|  | FD-B-L05.2 | As per - FD-ZC-LLG.1
|  | FD-B-L06.2 | As per - FD-ZC-LLG.1
|  | FD-B-L07.2 | As per - FD-ZC-LLG.1
|  | FD-B-L08.2 | As per - FD-ZC-LLG.1
|  | FD-B-L09.2 | As per - FD-ZC-LLG.1
|  | FD-B-L10.2 | As per - FD-ZC-LLG.1
|  | FD-B-L11.2 | As per - FD-ZC-LLG.1
Building C - Carpark
|  | FD-C-L00.1 | As per - FD-ZC-LLG.1
|  | FD-C-L00.2 | As per - FD-ZC-LLG.1
|  | FD-C-L02.1 | As per - FD-ZC-LLG.1
|  | FD-C-L02.2 | As per - FD-ZC-LLG.1
|  | FD-C-L04.1 | As per - FD-ZC-LLG.1
|  | FD-C-L04.2 | As per - FD-ZC-LLG.1
Building D - Tiernan Commercial
|  | FD-D-L00.1 | As per - FD-ZC-LLG.1
|  | FD-D-L02.1 | As per - FD-ZC-LLG.1
|  | FD-D-L04.1 | As per - FD-ZC-LLG.1
Building E - Victoria University
|  | FD-E-3LG.1 | As per - FD-ZC-LLG.1
|  | FD-E-L02.1 | As per - FD-ZC-LLG.1
|  | FD-E-L05.1 | As per - FD-ZC-LLG.1