## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Stormwater - 102 - Rev A | itp |  |  |  |  | ITP - Stormwater - 102 - Rev A
section | 4.09 Stormwater Aggregate Materials
checkpoint | 4.09.01 - Controlled Low Strength Materials - CLSM
label | Acceptance / Conformance Criteria - The use of CLSM by the Contractor will require approval from the Engineer on a case-by-case basis.
label | Standard / Specification - PS 16.8.1, PS 16.37
label | Verifying Document - An application submitted to the Engineer for approval, to use CLSM.
label | Frequency - An application submitted to the Engineer for approval, to use CLSM.
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.09.02 - AP65 Aggregate
label | Acceptance / Conformance Criteria - AP 65 Aggregate is to be a crushed product with a maximum granule size of 65mm and be a graded, clean durable aggregate which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requirements
label | Standard / Specification - PS 16.8.2.1, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.09.03 - AP40 Aggregate
label | Acceptance / Conformance Criteria - AP 40 aggregate is to be a crushed product with a maximum granule size of 40mm and be a graded, clean, durable aggregate and which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requitements
label | Standard / Specification - PS 16.8.2.2, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.09.04 - AP20 Aggregate
label | Acceptance / Conformance Criteria - AP 20 aggregate is to be a crushed product with a maximum granule size of 20mm and be a graded, clean, durable aggregate and which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requirements
label | Standard / Specification - PS 16.8.2.3, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.09.05 - Bed, Haunch Zone Material and Side Zone - Gap 7
label | Acceptance / Conformance Criteria - For bed and haunch zone well graded GAP 7 will be used and tested for Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities
label | Standard / Specification - PS 16.9.2.1, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.09.06 - Alternative Bedding
label | Acceptance / Conformance Criteria - If the Contractor wishes to propose a different material from that specified in this section, the Contractor shall submit to the Engineer
label | Standard / Specification - PS 16.9.2.1, PS 16.9.1.2, PS 16.37
label | Verifying Document - Statement from the concrete pipe supplier
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.09.07 - Overlay Zone Material (for concrete pipes)
label | Acceptance / Conformance Criteria - Materials for the overlay zone GAP 20 shall be used which has been tested for Grading, Weathering Index, Crushing Index
label | Standard / Specification - PS 16.9.2.2, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 4.10 Stormwater Pipe Materials
checkpoint | 4.10.01 - Steel Work
label | Acceptance / Conformance Criteria - All cut surfaces shall be protected with a corrosion protection coating i.e., zinc rich paint.
label | Standard / Specification - PS 16.8.4
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 4.10.02 - Steelwork
label | Acceptance / Conformance Criteria - Unless otherwise specified, all steel work shall be fabricated from mild steel conforming to the requirements of AS/NZS 3679.1:2010 and AS/NZS 4680:2006.
label | Standard / Specification - PS 16.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 4.10.03 - Welding
label | Acceptance / Conformance Criteria - All welding shall be carried out in compliance with AS/NZS 1554:2003-2017 and by suitably qualified welders.
label | Standard / Specification - PS 16.8.4
label | Verifying Document - Welders Certs
label | Frequency - Prior to Welding
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 4.10.04 - Steel Fitting Corrosion Protection
label | Acceptance / Conformance Criteria - Steel fittings shall be shop assembled as large as practicable before hot dip galvanising or zinc metal spray to AS/NZS 2312.2:2014 and AS/NZS 4680:2006, to minimise the number of field welds and bolted joints required.
label | Standard / Specification - PS 16.8.4.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 4.10.05 - Hot Dip Galvanised
label | Acceptance / Conformance Criteria - All ferrous metalwork except standard galvanised pipe shall be hot dip galvanised to HDG900 unless otherwise specified.
label | Standard / Specification - PS 16.8.4.1
label | Verifying Document - Datasheet / Cert
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 4.10.06 - Fastenings
label | Acceptance / Conformance Criteria - All fastenings associated with manholes or drainage structures shall be either hot dipped galvanised or stainless steel. Zinc Plated fastenings shall not be permitted
label | Standard / Specification - PS 16.8.4.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 4.10.07 - Concrete pipes and fittings
label | Acceptance / Conformance Criteria - Concrete pipes and fittings shall comply with the requirements of AS/NZS 4058:2007 for concrete pipes
label | Standard / Specification - PS 16.9.1.1, PS 16.37
label | Verifying Document - Datasheets
label | Frequency - Prior to use
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
checkpoint | 4.10.08 - Quality of Pipe and Precast Units
label | Acceptance / Conformance Criteria - IANZ Accredited Manufacturers certificate to NZTA F/3 (refer to Appendix F)
label | Standard / Specification - PS 16.34
label | Frequency - For every pipeline delivered (as soon as they are delivered)
section | Stormwater Structure Materials
checkpoint | Precast Catchpits
label | Acceptance / Conformance Criteria - All catchpits shall be precast concrete suitable for HN-HO-72 traffic loading.
label | Standard / Specification - PS 16.10.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Catchpit Lids
label | Acceptance / Conformance Criteria - Non-Rock 510mm Class D Heavy Duty type lids or similarly approved shall be used unless otherwise specified on the drawings. Heavy Duty type lids to be suitable for HN-HO-72 traffic loadings that are cycle friendly.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Precast concrete manhole
label | Acceptance / Conformance Criteria - All precast concrete manholes shall be manufactured in accordance with NZS 3109:1997. All manholes shall be suitable for HN-HO-72 traffic loading.
label | Standard / Specification - 16.15.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Catchpit Grates and Frames
label | Acceptance / Conformance Criteria - Catchpits grates and frames shall be grey cast iron suitable for HN-HO-72 traffic loadings.
label | Standard / Specification - PS 16.10.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Scruffy domes lids
label | Acceptance / Conformance Criteria - Scruffy domes lids shall be galvanised steel Hynds Type 2 scruffy domes (unless noted otherwise in the drawings), or similar approved.
label | Standard / Specification - PS 16.16.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Cement Mortar
label | Acceptance / Conformance Criteria - Cement mortar shall be Durability Class M4 in accordance with NZS 4210:2001, with a minimum compressive strength of 12.5MPa.
label | Standard / Specification - PS 16.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Epoxy Mortar
label | Acceptance / Conformance Criteria - Epoxy mortar for use in manhole riser joining or repairing of damaged or cut concrete (to provide cover to reinforcing due to cutting of precast units) shall be Hynds (MSR) or Humes Hume bond (or similar approved), applied in accordance with the manufacturer’s recommendations.
label | Standard / Specification - PS 16.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Precast Headwalls and Wingwalls
label | Acceptance / Conformance Criteria - Precast concrete headwalls or wingwall units shall be manufactured in accordance with NZS 3109:1997.
label | Standard / Specification - PS 16.13.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Erosion protection matting
label | Acceptance / Conformance Criteria - Erosion protection matting (coir Blanket or similar approved) is to be 100% biodegradable.
label | Standard / Specification - PS 16.13.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Precast Soakage Pit
label | Acceptance / Conformance Criteria - All precast concrete Soakage Pit manholes shall be manufactured in accordance with NZS 3109:1997.
label | Standard / Specification - PS 16.12.2.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Insitu Manhole Concrete
label | Acceptance / Conformance Criteria - Manholes shall be constructed 20MPa insitu concrete.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Datasheet / Mix Design
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Manhole Sealant
label | Acceptance / Conformance Criteria - All joints between ring segments of precast manholes and chambers shall be sealed with ‘Grey Butyl Manhole Sealant – Hynds (SM9020)’ or similar and approved.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Head and Wing wall Insitu Concrete
label | Acceptance / Conformance Criteria - Headwall and wingwall insitu reinforcing shall be steel grade 500E.
label | Standard / Specification - PS 16.13.2
label | Verifying Document - Mill Certs
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Head and Wing wall Reinforcing
label | Acceptance / Conformance Criteria - The headwall and wingwall cast in-situ concrete shall be 40MPa
label | Standard / Specification - PS 16.13.2
label | Verifying Document - Mix Design
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Soakage Pit Insitu Concrete
label | Acceptance / Conformance Criteria - Soakage Pits shall use 25MPa concrete.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Mix Design
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Benching Concrete
label | Acceptance / Conformance Criteria - Benching shall be 20MPa concrete
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Mix Design
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | Stormwater Rip Rap Materials
checkpoint | Rip Rap Rock Source Properties
label | Acceptance / Conformance Criteria - The Riprap Source shall be tested for Point Load Strength, UCS Rock, Weathering Index, Crushing Resistance, and Solid Density.
label | Standard / Specification - PS 16.8.3
label | Verifying Document - IANZ Lab Reports
label | Frequency - 1 per 1000m3
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | D50=150mm RipRap - Grading
label | Acceptance / Conformance Criteria - The D50=150mm RipRap grading for the drainage design shall be in general accordance with Auckland Council Technical Report TR2013/018
label | Standard / Specification - PS 16.8.3
label | Verifying Document - IANZ Lab Reports
label | Frequency - 1 per 1000m3
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | D50=250mm RipRap - Grading
label | Acceptance / Conformance Criteria - The D50=250mm RipRap grading for the drainage design shall be in general accordance with Auckland Council Technical Report TR2013/018
label | Standard / Specification - PS 16.8.3
label | Verifying Document - IANZ Lab Reports
label | Frequency - 1 per 1000m3
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | Subsoil Drainage Materials
checkpoint | Subsoil Drainage Pipe
label | Acceptance / Conformance Criteria - Pipes shall be high density polyethylene (HDPE) smooth bore perforated corrugated plastic pipe as shown on the Drawings and shall comply with the requirements of NZTA F/5.
label | Standard / Specification - PS 16.11.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Filter Material
label | Acceptance / Conformance Criteria - Filter material shall be placed around drainage pipe as shown on the Drawings and shall comprise no fines AP20/AP40 material.
label | Standard / Specification - PS 16.11.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | HDPE Liner
checkpoint | HDPE Liner
label | Acceptance / Conformance Criteria - The liner is to be 1mm thick HDPE material complying with GRI GM13 and fixed to the surface in accordance with the manufacturer’s specifications.
label | Standard / Specification - PS 16.19.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | HDPE Liner Bedding
label | Acceptance / Conformance Criteria - The sand membrane shall be clean sand free from contamination.
label | Standard / Specification - PS 16.19.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | Stormwater Geogrid and Geofabric
checkpoint | Geofabric
label | Acceptance / Conformance Criteria - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval at least two weeks before commencement of the works.
label | Standard / Specification - PS 16.29.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Biaxial Geogrid
label | Acceptance / Conformance Criteria - The biaxial geogrid shall be manufactured in accordance with a management system which complies with the requirements of BS EN ISO 9001, BS 14001. The Contractor shall submit the full details of the geogrid they propose to use for approval at least 2 weeks before commencement of the works.
label | Standard / Specification - PS16.29.3
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | Bioretention Soil Media
checkpoint | Bioretention Soil Media.
label | Acceptance / Conformance Criteria - Test results for soil filtration media material properties are submitted to the Engineer including ASTM F1815-06 test results, pH, clay content, organics content and material grading curve.
label | Standard / Specification - PS 16.38
label | Verifying Document - Datasheet
label | Frequency - Prior to installation
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
section | Directional Drill HDPE Pipe Materials
checkpoint | PE Pipe
label | Acceptance / Conformance Criteria - PE pipe is required to comply with AS/NZS 4130 and be PE100 or PE80B plain wall with an SDR as shown on the drawings, but no greater than SDR17.
label | Standard / Specification - PS 16.28.3
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | PE Fittings
label | Acceptance / Conformance Criteria - PE fittings must be manufactured in accordance with AS/NZS 4129 and be the same class and pipe material as the main pipe.
label | Standard / Specification - PS 16.28.3
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Electrofusion couplers
label | Acceptance / Conformance Criteria - Electrofusion couplers must comply with AS/NZS 4129 and be minimum PN16 pressure rating.
label | Standard / Specification - PS 16.28.3
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | PE Fitting Flanges
label | Acceptance / Conformance Criteria - Flanged connections between PE pipe and metal fittings (e.g. cast or ductile iron flanges on valves, spools, bends, etc) are to be made using PE stub flanges, full face gaskets (Tessnit or Klinger or equivalent approved by the Engineer), 316 grade stainless steel backing rings, and 316 grade stainless steel bolts and nuts.
label | Standard / Specification - T-EES: 04311 - 2.3
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Denso Tape
label | Acceptance / Conformance Criteria - Denso Tape (or equivalent) shall be used on buried flanged fittings
label | Standard / Specification - T-EES: 04311 - 2.3
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Grout
label | Acceptance / Conformance Criteria - Grout must be 1.5 MPa flowable concrete. The grout must be compatible with the pipe material and must have a service life matching the new pipe.
label | Standard / Specification - PS 16.28.6
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Welder Qualifications
label | Acceptance / Conformance Criteria - Evidence of welder certification is to be presented to the Engineer prior to starting welding.
label | Standard / Specification - T-EES: 04311 - 3.2.2
label | Verifying Document - Welding Qualifications
label | Frequency - Prior to starting welding.
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 5.02 Stormwater Drainage
checkpoint | 5.02.01 - Obsolete Stormwater Structures
label | Acceptance / Conformance Criteria - Obsolete catchpits, manholes, kerb and channel shall be demolished, uplifted and removed to an approved tip site.
label | Standard / Specification - PS 14.2.1
label | Verifying Document - Site Record
label | Frequency - Each Obsolete Structures
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 5.02.02 - Cutting Existing Pipes
label | Acceptance / Conformance Criteria - Where the catchpit will be replaced by a new drainage structure and/or constructed in a new location the existing stormwater pipe shall be neatly cut perpendicular to the line of the pipe to allow it to be easily extended.
label | Standard / Specification - PS 14.2.2
label | Verifying Document - Site Record
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 5.02.03 - Debris Removal and Void Filling
label | Acceptance / Conformance Criteria - All debris shall be removed to waste. The resulting void shall be backfilled with well compacted approved fill material.
label | Standard / Specification - PS 14.2.3
label | Verifying Document - Site Record
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 5.02.04 - Obsolete culverts
label | Acceptance / Conformance Criteria - Obsolete culverts shall be removed or may be left in place subject to the agreement of the Engineer. Abandoned culverts shall be plugged with concrete at each end or if the culvert is within 1.0m of the surface it shall be completely filled with a cement grout.
label | Standard / Specification - PS 14.2.4
label | Verifying Document - Site Record
label | Frequency - Each Occurrence
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 7.01 Services
checkpoint | 7.01.01 - Existing Services
label | Acceptance / Conformance Criteria - The Contractor is required to identify all known utility service crossings or encroachment, within 5m horizontally, of the proposed drainage alignments.
label | Standard / Specification - PS 16.5.4
label | Verifying Document - Survey Records
label | Frequency - Prior to excavation
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Service Support
label | Acceptance / Conformance Criteria - The Contractor shall support all existing services affected by the works whether these services cross-or are located alongside the excavation.
label | Standard / Specification - PS 16.5.4
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Utility Operators Approval
label | Acceptance / Conformance Criteria - Prior to commencing with any construction, the Contractor shall Obtain written approval from the relevant Utility Operators for any construction activities within the vicinity of their service(s).
label | Standard / Specification - PS 16.5.4
label | Verifying Document - Written Approval
label | Frequency - Prior to commencing with any construction
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Utility Operators Requirements
label | Acceptance / Conformance Criteria - Prior to commencing with any construction, the Contractor shall Undertake the construction activities within the vicinity of the service in compliance with the with the relevant Utility Operator’s requirements.
label | Standard / Specification - PS 16.5.4
label | Verifying Document - Site Records
label | Frequency - Prior to commencing with any construction
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Protection of Pipelines / Structures During Construction
label | Acceptance / Conformance Criteria - Where construction plant is required to be operated over pipelines Table B1 of AS/NZS 3725:2007 shall apply in determination of the minimum depth of fill (cover) required. A temporary embankment, extending not less than 15m on both sides of the pipe/culvert, shall be used to provide the necessary cover.
label | Standard / Specification - PS 16.5.5
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 Stormwater General
checkpoint | Setout
label | Acceptance / Conformance Criteria - Prior to the commencement of any drainage works for a particular drainage line, the Contractor shall set out the line, level, and position of the proposed drainage line, including inlet and outlet positions and levels, and present it to the Engineer for their consideration. The Contractor shall provide at least 48 hours’ notice to the Engineer ahead of set-out and allow 48 hours for the Engineer to respond prior to commencing work.
label | Standard / Specification - PS 16.6.1
label | Verifying Document - Survey Records
label | Frequency - Prior to the commencement
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Dealing with Water
label | Acceptance / Conformance Criteria - The Contractor shall maintain all trench inverts free from flowing or accumulated water. Water arising from, or draining into, the trench shall be drained or pumped. Any sumps required shall be refilled to formation level as directed by the Engineer.
label | Standard / Specification - PS 16.7.1
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Pipe Installation and Backfill
checkpoint | Open Trenches
label | Acceptance / Conformance Criteria - All open trench excavations for pipelines shall be to a minimum depth of 100mm below the pipe external walls. Where excavating in natural ground or existing carriageways, no more than 100 metres of trench (per drain laying operation) shall remain open at any one time.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Saw Cutting
label | Acceptance / Conformance Criteria - Where trenching through roads, prior to excavation, the surface shall be saw-cut a minimum of 100mm beyond the trench wall and parallel to the proposed alignment.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Stability check
label | Acceptance / Conformance Criteria - Where trenching is near new or existing structures (within 5m horizontally, or where the trench invert is below a plane projected downwards at 1(V) in 2(H) from the base of the structure), a stability check shall be undertaken to ensure undermining of the structure is avoided. The Contractor shall undertake a stability check in these situations.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Trench Width
label | Acceptance / Conformance Criteria - The minimum trench widths are as indicated on Drawing WD-0131 but not less than the external pipe diameter plus 600mm and not more than the external pipe diameter plus 1200mm.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Unsuitable Material
label | Acceptance / Conformance Criteria - All material deemed to be unsuitable shall be removed to a depth of 600mm or a greater depth as specified by the Engineer, until suitable material is reached.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Trench invert subgrade inspection
label | Acceptance / Conformance Criteria - The Engineer shall have the opportunity to complete a Visual Inspection to NZTA F/3:2010 on the trench subgrade each day on each pipeline during installation.
label | Standard / Specification - Suitability
label | Verifying Document - Engineers Record
label | Frequency - Daily
label | Verification Activity: Activity - WP
label | Verification Activity: By - ENG
checkpoint | Trench invert subgrade testing
label | Acceptance / Conformance Criteria - The subgrade shall be tested for CBR>5 by Scala or shear vane. This test shall be undertaken at the design subgrade level and at a depth of 300mm below the design subgrade level.
label | Standard / Specification - PS 16.9.1.3, PS 16.32.3
label | Verifying Document - Scala or Shear Vane Report
label | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Subgrade Undercut and Replacement
label | Acceptance / Conformance Criteria - The insitu trench base shall be tested and if CBR is less than 5, it shall be undercut and backfilled with AP65 compacted to compacted to lD=60% or correlated CIV.
label | Standard / Specification - PS 16.9.1.3
label | Verifying Document - Site Records / NDM / Clegg Report
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Pipe bedding and haunch zone inspection
label | Acceptance / Conformance Criteria - The Engineer shall complete a Visual Inspection to NZTA F/3: 2010 each strength length on Pipe bedding and haunch zone
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Engineers Record
label | Frequency - 1 per trench length (Between Chambers)
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Pipe bedding and haunch zone Density Testing
label | Acceptance / Conformance Criteria - Pipe surround material shall be placed and compacted over the full width of the trench to a finished minimum thickness of 150mm above the crown of the pipes. The pipe bedding and haunching zone shall be compacted to lD=60% or correlated CIV.
label | Standard / Specification - PS 16.32.3, PS 16.6
label | Verifying Document - NDM / Clegg Report
label | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Backfilling of pipes and culverts with embankment fill - QA Acceptance
label | Acceptance / Conformance Criteria - Prior to Backfilling of pipes and culverts with embankment fill the test results for bedding, haunching, side zone, and overlay zone material properties, grading curves and compaction tests are accepted by the Engineer.
label | Standard / Specification - PS 16.37
label | Verifying Document - Engineers Acceptance
label | Frequency - Prior to Backfilling of pipes and culverts with embankment fill
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Pipe laying in Embankments
label | Acceptance / Conformance Criteria - The Contractor shall have each pipe checked for level as it is laid, by a competent technician using an Engineer’s level, pipe laser or other approved equipment. Pipes shall be laid on uniform gradients between successive designated manholes at the gradients specified on the Drawings.
label | Standard / Specification - PS 16.9.2.8
label | Verifying Document - Survey Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | Pipe Connections
label | Acceptance / Conformance Criteria - A flexible joint shall be provided to the outside face of any structure (manholes, catchpits, catchpit manholes and headwalls) into which a pipe is built. The length of the next pipe (rocker pipe) join away from the structure shall be no more than 600mm for all concrete stormwater pipes and shall be constructed in accordance with Typical Details on the drawings.
label | Standard / Specification - PS 16.9.2.15
label | Verifying Document - Site Records
label | Frequency - Each Structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Cutting of Concrete Pipes
label | Acceptance / Conformance Criteria - Where it is necessary to cut a concrete pipe the pipe supplier should be informed of such requirement specifically where the dimensional tolerance for the pipe is deemed critical.
label | Standard / Specification - PS 16.9.2.16
label | Verifying Document - Supplier Approval
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Cut Pipe Sealing
label | Acceptance / Conformance Criteria - All cut surfaces, not encased within benching or other in-situ concrete, shall be coated with an epoxy resin mortar in accordance with the manufacturer/supplier recommendations, leaving no exposed reinforcement.
label | Standard / Specification - PS 16.9.2.16
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Side zones Density Testing
label | Acceptance / Conformance Criteria - Pipe surround material shall be placed and compacted over the full width of the trench to a finished minimum thickness of 150mm above the crown of the pipes. The Side zones shall be compacted to lD=60% or correlated CIV.
label | Standard / Specification - PS 16.32.3, PS 16.6
label | Verifying Document - NDM / Clegg Report
label | Frequency - 1 per backfill layer per 15m trench length. Minimum of 2 tests backfill layer per trench between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Compaction above Pipe
label | Acceptance / Conformance Criteria - Only hand operated compaction tools shall be used until the backfill has achieved a depth of 300mm above the crown of the pipe.
label | Standard / Specification - PS 16.32
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Pipe overlay zone inspection
label | Acceptance / Conformance Criteria - The Engineer shall complete a Visual Inspection to NZTA F/3: 2010 each strength length on Pipe overlay zone
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Engineers Record
label | Frequency - 1 per trench length (Between Chambers)
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Pipe overlay zone Density Testing
label | Acceptance / Conformance Criteria - Backfill material shall be built up in layers not exceeding 200mm. The Pipe overlay zone shall be compacted to lD=60% or correlated CIV.
label | Standard / Specification - PS 16.32.3, PS 16.6
label | Verifying Document - NDM / Clegg Report
label | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Pipe invert levels/lid levels at all drainage structures
label | Acceptance / Conformance Criteria - Pipes shall be installed within 20mm of stated invert level (vertical tolerance) and within 50mm or 5% of the pipe diameter of proposed horizontal alignment (whichever is greater). Catchpits and catchpit manholes shall be located to align with proposed kerb and channel (or dish channel) and finished to be flush with the finished road surface unless otherwise specified on the Drawings.
label | Standard / Specification - PS 16.34.2
label | Verifying Document - Survey Records
label | Frequency - At the completion of each stormwater pipeline
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
section | 4.02 Subsoil Drain
checkpoint | Trench Grade
label | Acceptance / Conformance Criteria - Unless otherwise specified trenches shall have: a minimum gradient of not less than 1 in 100; vertical sides from the trench bottom to a minimum of 300 mm above the top of the pipe; and a minimum depth that will ensure that, when the pipes are laid, the invert level shall be not less than one metre below finished subgrade level.
label | Standard / Specification - NZTA F/5 PS 16.11.2
label | Verifying Document - Note only
label | Frequency - Each Pipe
checkpoint | Bedding and Installation of Drainage Pipe
label | Acceptance / Conformance Criteria - Prior to laying the drain pipes, the Constructor shall ensure that pipes do not become contaminated with clay or soil and that pipe slots are not blocked. Any such blockages shall be removed before pipes are laid.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Bedding Placement
label | Acceptance / Conformance Criteria - The filter material shall be placed, and the drain pipe installed such that the pipe is at a uniform grade and is underlain by a minimum of 50 mm and overlaid by a minimum of 150mm of filter material which completely surrounds the drain pipe. The filter material shall be placed in a manner to achieve a generally uniform dense state.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Pipe Orientation
label | Acceptance / Conformance Criteria - Pipes should generally be laid so that the perforations are oriented as shown in accordance with the manufacturer’s recommendations for corrugated HDPE pipes.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Pipe Jointing
label | Acceptance / Conformance Criteria - The drain pipe lengths shall be joined following the manufacturer’s instructions or as approved by the Engineer, with the pipe jointing carried out to leave a smooth flush internal surface. The top ends of the pipes shall be capped.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Joint
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Pipe Installation Inspection
label | Acceptance / Conformance Criteria - The drain pipe installation shall be inspected and approved by the Engineer before placing filter material and backfill.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Engineers Acceptance
label | Frequency - Prior to backfilling
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Lose Debris Removal
label | Acceptance / Conformance Criteria - Prior to placing filter material and backfill, the base and sides of the trench shall be cleaned of loose debris so far as is practical.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Prior to backfilling
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Subsoil Backfilling
label | Acceptance / Conformance Criteria - The backfill shall be filter sand as detailed in clause 2.2 of this specification. The backfill material shall be placed in layers not exceeding 150 mm loose depth and shall be positively compacted around the sides of the pipe to provide support of not less than that of the adjacent material
label | Standard / Specification - NZTA F/5 PS 16.11.2
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Overlaying
label | Acceptance / Conformance Criteria - The completed drains shall be backfilled with an overlying capping layer to prevent the ingress of surface water.
label | Standard / Specification - PS 16.11.4
label | Verifying Document - Site Records
label | Frequency - On Completed Drains
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Stormwater Structures General
checkpoint | Stormwater Structures Subgrade
label | Acceptance / Conformance Criteria - A hand Auger Scala / Shear Vane up to 4m deep shall be completed in the base of the excavation and the results submitted to the Engineer. The subgrade shall be CBR>5.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Scala / Shear Vane Results
label | Frequency - 1 per structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Stormwater Structures Bedding material
label | Acceptance / Conformance Criteria - Stormwater Structures Bedding granular material shall be compacted to MDD of 95%.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - NDM Results
label | Frequency - 1 per structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Stormwater Structures Backfill
label | Acceptance / Conformance Criteria - Stormwater Structures Backfill granular material shall be compacted to MDD of 95%.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - NDM Results
label | Frequency - 1 per backfill layer per structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Subgrade Clay
label | Acceptance / Conformance Criteria - If clay is present at subgrade level, then this should be supplemented with soaked CBR laboratory testing.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Soaked CBR
label | Frequency - Each Occurrence
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Culvert CBR Approval
label | Acceptance / Conformance Criteria - The contractor is to provide CBR testing of trench subgrade prior to placement of bedding and laying of culverts.
label | Standard / Specification - PS 16.38
label | Verifying Document - CBR
label | Frequency - Each culvert prior to bedding
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
checkpoint | Field Welding
label | Acceptance / Conformance Criteria - Field welded joints shall be filed to remove rough surfaces and shall receive a protective coating of an approved zinc rich paint.
label | Standard / Specification - PS 16.8.4.1
label | Verifying Document - Site records
label | Frequency - Each Weld
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 Catchpits (Structure)
checkpoint | Catchpits Base
label | Acceptance / Conformance Criteria - Catchpits shall be constructed on a compacted, 50mm blinding sand underlain by 150mm layer of AP65 granular material.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Precast Catchpit Sealant
label | Acceptance / Conformance Criteria - All joints between segments of precast catchpit risers shall be sealed with ‘Black Butyl Mastic Sealant – Hynds (MSR)’ or similar and approved.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Catchpits Grates
label | Acceptance / Conformance Criteria - Cast-iron grates and frames shall be set no more than 30mm lower than, but parallel to the cross fall and grade of the surrounding, finished pavement surface level. All grates and frames shall be haunched to lids.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Catchpits Sumps
label | Acceptance / Conformance Criteria - Catchpits must have sumps at least 450mm deep (below the invert of the outlet pipe level)
label | Standard / Specification - PS 16.10
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Catchpits Inlets
label | Acceptance / Conformance Criteria - All catchpits receiving stormwater from the highway shall be constructed with a back-entry inlet.
label | Standard / Specification - PS 16.10
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
section | 4.02 Manholes (Structure)
checkpoint | Manholes Base
label | Acceptance / Conformance Criteria - Manholes shall be constructed on a 50mm blinding sand layer underlain by 150mm layer of compacted AP65 granular material.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Manholes Sealant
label | Acceptance / Conformance Criteria - All joints between ring segments of precast manholes and chambers shall be sealed with ‘Grey Butyl Manhole Sealant – Hynds (SM9020)’ or similar and approved.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Benching
label | Acceptance / Conformance Criteria - Benching is required in all manhole structures unless noted otherwise on Drawings. Benching shall be 20MPa concrete and to a F4 finish. Manhole benching shall accommodate pavement subsoil drain connections where required.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Benching Fall
label | Acceptance / Conformance Criteria - All side benching shall be formed with a fall towards the channel unless otherwise stated.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Sealant
label | Acceptance / Conformance Criteria - All pipe work penetrations through manhole walls shall be sealed using Epoxy Mortar or an approved equivalent type of permanent sealant.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Lids
label | Acceptance / Conformance Criteria - All solid cast-iron covers and frames shall be set flush with the cross fall and grade of the surrounding finished surfaces. All grates and frames shall be haunched to lids.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Raised cover levels
label | Acceptance / Conformance Criteria - For new or existing manholes with raised cover levels, the height of the manhole access shaft (throat) shall be no greater than 600mm where access is required (all non-catchpit manholes).
label | ○ The shaft and any subsequent extensions to the shaft shall be constructed using either:
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Adjust Manhole Service Lid Covers
label | Acceptance / Conformance Criteria - Following adjustment, the service cover shall be firmly held in place and shall not be 5mm higher or 0mm lower than the adjoining surface. The item shall cover adjustments + or – 300mm from the original height. Any adjustments exceeding these measurements shall be treated as a variation.
label | Standard / Specification - PS 16.12.1
label | Verifying Document - Site Records
label | Frequency - Each Lid
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Visual inspection of all Manholes
label | Acceptance / Conformance Criteria - 3-6 months following construction, Each manhole shall be inspected. No evidence of identifiable flow infiltration, settlement and riser displacement or cracking shall be present
label | Standard / Specification - PS 16.34
label | Verifying Document - Inspection Record
label | Frequency - Each Manhole 3-6 months after Construction
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
section | 4.02 Headwalls and Wingwalls (Structure)
checkpoint | Headwall Bedding
label | Acceptance / Conformance Criteria - Headwall aprons shall be constructed on a compacted, 75mm bedding sand underlay by 150mm layer of AP65 (or similar material as approved by the Engineer) granular material and compacted to a MDD of 95%.
label | Standard / Specification - PS 16.13.2
label | Verifying Document - NDM Results
label | Frequency - Every Unit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
label | Comments / Closeout Details - 1 per Apron
checkpoint | Precast and Cast in-situ Headwall and Wingwall tolerance
label | Acceptance / Conformance Criteria - +/- 10mm variance to vertical design set-out
label | ○ +/- 10mm variance to horizontal design set-out (values in accordance with NZS 3109: 1997)
label | Standard / Specification - PS 16.34
label | Verifying Document - Survey Records
label | Frequency - Every Unit
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
section | 5.01 Stormwater Insitu Concrete Pour
checkpoint | Construction Joint Locations
label | Acceptance / Conformance Criteria - Proposed location of construction joints to be submitted to the engineer for review prior to concrete pour.
label | Standard / Specification - Downer
label | Verifying Document - Approval
label | Frequency - Prior to Pour
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Dry Pack Mortar
label | Acceptance / Conformance Criteria - Dry pack mortar where specified on the drawings shall be places as per the manufactures instructions.
label | Standard / Specification - Downer
label | Verifying Document - Pre pour
label | Frequency - Before Works
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | Reinforcement Pre Pour Inspection
label | Acceptance / Conformance Criteria - Handling, Fabrication, Placing and Fixing shall be inspected prior to pouring concrete.
label | Standard / Specification - Downer
label | Verifying Document - Pre pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | Pre-Pour Inspection
label | Acceptance / Conformance Criteria - Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area.
label | Standard / Specification - Downer
label | Verifying Document - Signed Pre-Pour
label | Frequency - 48 Hours Notice Prior to Each Occurrence
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Delivery Dockets
label | Acceptance / Conformance Criteria - The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size.
label | Standard / Specification - Downer
label | Verifying Document - Dockets
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | Slump Testing
label | Acceptance / Conformance Criteria - Slump tests shall be taken for each delivery of concrete and the results recorded by the Contractor.
label | Standard / Specification - Downer
label | Verifying Document - Pre Pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | 5.02 Stormwater Insitu Concrete Post Pour
checkpoint | Post Pour Inspection
label | Acceptance / Conformance Criteria - Following the concrete pour, the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
label | Standard / Specification - Downer
label | Verifying Document - Post Pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | Construction joints
label | Acceptance / Conformance Criteria - Construction joints shall be placed as per the drawings / agreement.
label | Standard / Specification - Downer
label | Verifying Document - Post Pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | Defective Concrete Finishes
label | Acceptance / Conformance Criteria - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
label | Standard / Specification - NZS 3114
label | Verifying Document - NCR
label | Frequency - Prior to non Minor Repair
label | Verification Activity: Activity - V
label | Verification Activity: By - SE
section | 4.02 Soakage Pits and Infiltration Trench
checkpoint | Soakage Pit Sealing
label | Acceptance / Conformance Criteria - All pipe work penetrations through manhole walls shall be sealed using Epoxy Mortar or an approved equivalent type of permanent sealant.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Site Records
label | Frequency - Each Hole
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Soakage Pit Benching
label | Acceptance / Conformance Criteria - All side benching shall be formed with a fall towards the channel unless otherwise stated.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Soakage Pit Lids
label | Acceptance / Conformance Criteria - All solid cast-iron covers and frames shall be set flush with the cross fall and grade of the surrounding finished surfaces. All grates and frames shall be haunched to lids.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Infiltration Trench Excavation
label | Acceptance / Conformance Criteria - The trench/excavation shall be free of roots and projections or obstructions. Where over excavation has occurred, the bottom shall be brought back to grade using excavated material which is only lightly compacted in position to the same extent as the undisturbed surrounding soil. No loose soil shall be left in the excavation after restoration to finished grade.
label | Standard / Specification - PS 16.12.3.1
label | Verifying Document - Site Records
label | Frequency - Each Trench
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Trench Inspection
label | Acceptance / Conformance Criteria - All trenches in existing ground shall be inspected by the Engineer prior to commencement of laying filter cloth. Any unsuitable foundation material shall be removed at the Engineers direction.
label | Standard / Specification - PS 16.12.3.1
label | Verifying Document - Engineers Approval
label | Frequency - Prior to commencement of laying filter cloth
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Groundwater
label | Acceptance / Conformance Criteria - If groundwater is encountered in the trench/excavation the Contractor shall seek instructions from the Engineer on how to proceed.
label | Standard / Specification - PS 16.12.3.1
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Drainage Media
checkpoint | Placement of Drainage Media
label | Acceptance / Conformance Criteria - The drainage media (100-150mm rock) shall be carefully placed in the clean, excavated area after the excavated material has been removed and the excavation site cleared of potentially contaminating material and the excavation lined with filter cloth. The drainage media shall be lightly and uniformly compacted. No mechanical compaction equipment shall be used. The drainage media shall not be placed or lightly compacted if the excavation is flooded or the in-situ soils saturated.
label | Standard / Specification - PS 16.12.3.3
label | Verifying Document - Site Records
label | Frequency - Each Area
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Place D50 250mm Rip Rap
checkpoint | Rip Rap Placement
label | Acceptance / Conformance Criteria - The Contractor shall place D50 = 250mm size rock rip rap in areas shown on the contract drawings and as instructed by the Engineer. The rock shall be placed to ensure rock is tightly knit with no movement.
label | Standard / Specification - PS 16.14.2
label | Verifying Document - Site Records
label | Frequency - Each Area
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Rip Rap Rock Flumes
checkpoint | Rip Rap Placement
label | Acceptance / Conformance Criteria - The Contractor shall place D50 rock rip rap in areas shown on the contract drawings and as instructed by the Engineer. The rock shall be placed to ensure rock is tightly knit with no movement.
label | Standard / Specification - PS 16.17.2
label | Verifying Document - Site Records
label | Frequency - Each Area
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Geotextile Protection
label | Acceptance / Conformance Criteria - The contractor shall minimise the height from which rock is placed on order to reduce the risk of damage to the filter fabric layer. Rock shall not be dropped from >0.5m height.
label | Standard / Specification - PS 16.17.2
label | Verifying Document - Site Records
label | Frequency - Each Area
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Face Alignment
label | Acceptance / Conformance Criteria - The face of the rock rip rap shall be placed at the gradient shown on the drawings and the termination at each end against existing slopes is to be keyed into and to approximately match the adjacent slope and placed in general accordance with ‘Section 10 Filling’ of TNZ F/1:1997 to achieve a compact mass with minimal voids and good interlock of rock fragments.
label | Standard / Specification - PS 16.17.2
label | Verifying Document - Survey Records
label | Frequency - Each Area
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Geofabric
checkpoint | Geotextile Filter Fabric Protection
label | Acceptance / Conformance Criteria - Construction plant shall not travel over exposed fabric. A minimum cover of 200mm of fill material shall be in place before construction plant is operated above the fabric.
label | Standard / Specification - PS 16.18.1, PS 16.12.3.2
label | Verifying Document - Site Records
label | Frequency - Before Trafficking
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Geotextile Filter Fabric Lab
label | Acceptance / Conformance Criteria - Geotextile filter fabric shall have a minimum overlap of 500mm at any joins.
label | Standard / Specification - PS 16.18.1, PS 16.12.3.2
label | Verifying Document - Site Records
label | Frequency - Each Joint
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 GeoGrid
checkpoint | GeoGrid Installation Approval
label | Acceptance / Conformance Criteria - The installation of biaxial geogrid shall not commence until the Engineer has inspected the proposed geogrid on site and confirmed that the correct types of geogrid have been supplied and that the foundation soils meet with those assumed in the detailed design calculations.
label | Standard / Specification - PS16.29.3
label | Verifying Document - Engineers Approval
label | Frequency - Prior to installation
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Biaxial Geogrid Placement
label | Acceptance / Conformance Criteria - Geogrid is to be placed in accordance with the Manufacturer’s instructions, to the lines and levels shown on the drawings. Geogrid shall have a minimum overlap of 1000mm at any joins. The geogrid shall be placed perpendicular to the road orientation and shall run in a continuous unbroken length from one side to the other.
label | Standard / Specification - PS 16.29.3
label | Verifying Document - Site Records
label | Frequency - Each Joint
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | Biaxial Geogrid Backfilling
label | Acceptance / Conformance Criteria - At no time shall more reinforcing geogrid be laid than cant be covered in the same day. Each run of geogrid shall be firmly secured in place to maintain the grid in position and ensure that the geogrid is taut over the face. Care shall be taken to ensure that the geogrid is not damaged during fill placement. Construction plant shall not travel over exposed geogrid. A minimum cover of 150mm of fill material shall be in place before construction plant is operated above the geogrid.
label | Standard / Specification - PS 16.29.3
label | Verifying Document - Site Records
label | Frequency - Daily
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 4.02 Bioretention Soil Media
checkpoint | Exclusion Zones (Bioretention and Infiltration Devices)
label | Acceptance / Conformance Criteria - The contractor is to establish fenced-off exclusion zones at the start of the works to avoid plant / machinery tracking and over-compacting bioretention and infiltration device formations such that the hydraulic conductivity of the existing ground is not compromised. The exclusion zone shall at a minimum cover the extent of the device base area.
label | Standard / Specification - PS 16.39.1
label | Verifying Document - Site Records
label | Frequency - At the start of the works
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Interface Finish
label | Acceptance / Conformance Criteria - Bioretention devices operation as it provides a poor interface with the media. A rough finish such as that achieved with a toothed digger bucket is preferred.
label | Standard / Specification - PS 16.21
label | Verifying Document - Site Records
label | Frequency - Each Device
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Suitability of existing soil for infiltration and bioretention areas.
label | Acceptance / Conformance Criteria - Bioretention device and infiltration device formations are to be inspected by the Engineer prior to laying of bioretention or filtration media to confirm the suitability of the existing ground.
label | Standard / Specification - PS 16.38
label | Verifying Document - Site Records
label | Frequency - prior to laying of bioretention or filtration media
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
checkpoint | Bioretention Soil Media placement
label | Acceptance / Conformance Criteria - The soil media layer is required to line the invert of all bioretention devices and placed in a single lift to 50 mm above the finished level. The finished surface shall be reasonably smooth, uniform and free of obvious hollows and humps. Care shall be taken to avoid overhandling the soi
label | Standard / Specification - PS 16.21.1
label | Verifying Document - Site Records
label | Frequency - Each Device
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Compaction
label | Acceptance / Conformance Criteria - The soil media shall be raked without any form of mechanical compaction.
label | Standard / Specification - PS 16.21
label | Verifying Document - Site Records
label | Frequency - Each Device
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Infiltration testing
label | Acceptance / Conformance Criteria - Once the bioretention devices have been completed, it shall be tested by double-ring infiltrometer for permeability. The rate shall be >50 mm/hr and not exceed 500 mm/hr. Alternative testing means must be approved by the Engineer.
label | Standard / Specification - PS 16.21.1
label | Verifying Document - Site Records
label | Frequency - Each Device upon completion
label | Verification Activity: Activity - i
label | Verification Activity: By - SE
checkpoint | Landscaping Approval
label | Acceptance / Conformance Criteria - Once the media is placed the Contractor shall notify the Engineer. If the Engineer is satisfied with the soil placement, they will advise the Contractor that landscaping can commence. Stabilisation with grass seed shall be carried out within seven days once approval is obtained from the Engineer.
label | Standard / Specification - PS 16.21
label | Verifying Document - Engineers Approval
label | Frequency - Prior to Landscaping
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 4.02 Wetland and Bioretention Access Track
checkpoint | Access Track Subgrade
label | Acceptance / Conformance Criteria - The access track for the wetland and bioretention device 01 shall have a Compact Subgrade (minimum CBR 5).
label | Standard / Specification - PS 16.22.1
label | Verifying Document - Scala Results
label | Frequency - TBC
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
label | Comments / Closeout Details - Frequency TBC
checkpoint | Access Track Subbase
label | Acceptance / Conformance Criteria - The access track for the wetland and bioretention device 01 shall be formed as a 3m wide all-weather access track constructed with a 150mm GAP 65 Subbase.
label | Standard / Specification - PS 16.22.1
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
label | Comments / Closeout Details - Frequency and testing TBC
checkpoint | Access Track Basecourse
label | Acceptance / Conformance Criteria - The access track for the wetland and bioretention device 01 shall be formed as a 3m wide all-weather access track constructed with a 50mm GAP 20 Basecourse (Gravel Road Spec)
label | Standard / Specification - PS 16.22.1
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
label | Comments / Closeout Details - Frequency and testing TBC
section | 4.02 Design and Construct Outfall Access Track
checkpoint | Outfall Access Track Design
label | Acceptance / Conformance Criteria - The design including producer statements are to be submitted to the Engineer for approval. The Engineer will have 5 working days to review the design and provide approval or feedback (this is not a design review).
label | Standard / Specification - PS 16.23.6
label | Verifying Document - Approved Design
label | Frequency - Prior to Works
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 4.02 Construct Wetlands
checkpoint | Geotextile fabric installation
label | Acceptance / Conformance Criteria - Geotextile fabric shall be laid directly on the existing ground to protect the liner from damage due to punctures. It is assumed that the existing ground will be sand from the existing geotechnical information provided. If this is not the case the Engineer must be notified to allow for remedial treatment prior to the placement of the geofabric.
label | Standard / Specification - PS 16.24.6
label | Verifying Document - Site Records
label | Frequency - During Placement
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Impermeable liner installation
label | Acceptance / Conformance Criteria - An impermeable liner is required to line the entire wetland base and batters to avoid ground stability issues near the gully embankment. Particular care should be taken to ensure water tightness around inlet and outlet structures as per the Drawing details.
label | Standard / Specification - PS 16.24.5
label | Verifying Document - Site Records
label | Frequency - During Placement
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 Rock Riprap for Erosion Protection
checkpoint | Organic Material Removal
label | Acceptance / Conformance Criteria - Prior to placement of rock riprap, all organic material is to be removed, followed by the placement and anchorage of a Class E geotextile (in accordance with TNZ Specification F/7 Geotextile).
label | Standard / Specification - PS 16.25.1
label | Verifying Document - Site Records
label | Frequency - Prior to placement of rock riprap
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 Void Filled Riprap
checkpoint | Rip Rap Mixing
label | Acceptance / Conformance Criteria - Mix the material thoroughly using additional moisture and control procedures that ensure a homogenous mixture where the fines fill the inherent voids in the riprap without displacing riprap.
label | Standard / Specification - PS 16.26.3
label | Verifying Document - Site Records
label | Frequency - Prior to Placement
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Rip Rap Placement
label | Acceptance / Conformance Criteria - Place the blended mixture of approximate 2 x D50 thickness, minimising segregation of material. Some additional mixing may be required after the initial placement where there is segregation or areas that consist of smaller void fill materials.
label | Standard / Specification - PS 16.26.4
label | Verifying Document - Site Records
label | Frequency - During Placement
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Rip Rap Compaction
label | Acceptance / Conformance Criteria - The mixture shall be consolidated by driving over it with a loader or tamping with an excavator bucket to create a tight, dense interlocking mass.
label | Standard / Specification - PS 16.26.5
label | Verifying Document - Site Records
label | Frequency - During Placement
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Rip Rap Surface
label | Acceptance / Conformance Criteria - Where a surface layer of topsoil is specified, moist topsoil shall be placed over the void filled riprap and compacted to a dense stable state. Prior to placement of topsoil, the riprap placement must be reviewed by the Engineer. Additional topsoil shall be added to any areas that settle.
label | Standard / Specification - PS 16.26.9
label | Verifying Document - Engineers Approval
label | Frequency - Prior to placement of topsoil
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 4.02 Establish and Reinstatement of the Temporary Access Track
checkpoint | Access Track Design
label | Acceptance / Conformance Criteria - The Contractor shall submit a design of the access track which shall include consideration of runoff, erosion and sediment control measures, health and safety risk assessment to the Engineer a minimum 20 days prior to the work commencing.
label | Standard / Specification - PS 16.27.1
label | Verifying Document - Design
label | Frequency - 20 days prior to the work commencing
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Topsoil Installation
label | Acceptance / Conformance Criteria - Topsoil shall be spread uniformly over the areas as defined to a depth noted on the drawings
label | Standard / Specification - PS 16.27.2.1
label | Verifying Document - Photos
label | Frequency - During installation
label | Verification Activity: Activity - D
label | Verification Activity: By - SE
checkpoint | Fertilisers
label | Acceptance / Conformance Criteria - Fertilisers shall be lightly arrowed into the topsoil, 2-3 days prior to seed sowing, at the following rates at 200kg/ha.
label | Standard / Specification - PS 16.27.2.2
label | Verifying Document - Site Records
label | Frequency - Each Sown Area
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Grass sowing
label | Acceptance / Conformance Criteria - The seed mixture shall be an industry standard quality. On large areas the seed shall be “check” sown in at least two directions and surface rolled with suitable flat roller. On small areas the grass seed shall be evenly applied and raked into the soil.
label | Standard / Specification - PS 16.27.2.2
label | Verifying Document - Site Records
label | Frequency - Each Sown Area
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Establishment of sown areas
label | Acceptance / Conformance Criteria - Newly established grass shall be protected from damage by pedestrian and vehicular traffic until grass has reached a self-sustaining state. Grassed areas shall be watered as required to achieve an efficient germination of the seed. Newly grassed areas shall be maintained with regular mowing (90mm-30mm) ensuring that all clippings are removed from adjacent hard surfaces.
label | Standard / Specification - PS 16.27.2.2
label | Verifying Document - Site Records
label | Frequency - Each Sown Area
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Grassed areas adjacent hardscape
label | Acceptance / Conformance Criteria - All grassed areas adjacent hardscape - such as paths, kerbs, hardstand areas – to ensure base of grass is flush with adjacent path. If base of grass level is 30mm lower or more than adjacent hardstand, grass will need to be removed min 1m back from path, soil put back in, levelled and re-consolidated to spec and grass re-sown to correct level. If less than 30mm top dressing at 10mm each time, over time will be acceptable until the correct level is achieved.
label | Standard / Specification - PS 16.27.2.2
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Slope Area Preparation
label | Acceptance / Conformance Criteria - In all sites, except natural gully systems, where the slope gradient is steeper than 1:3 (one metre high by three metres long), it is preferable that the embankment is either scarified or grooved on an angle to a depth of 200mm, from the top of the bank to the base. This assists topsoil adhesion and prevents separation of the top 150mm topsoil from the base material due to gravity and/or glazed/planning of base material.
label | Standard / Specification - PS 16.27.2.2
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 Directional Drill HDPE Pipe
checkpoint | Methodology Statement
label | Acceptance / Conformance Criteria - The Contractor is required to submit to the Engineer a Methodology Statement that addresses the requirements of the process covered by this Standard Technical Specification.
label | Standard / Specification - T-EES: 04311 - 3.3 PS 16.28.4
label | Verifying Document - Approved Method Statement
label | Frequency - Prior to Works
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Ground Investigation
label | Acceptance / Conformance Criteria - Carry out additional ground investigation as necessary to confirm the feasibility of the trenchless method proposed for installation.
label | Standard / Specification - PS 16.28.5
label | Verifying Document - Report
label | Frequency - Prior to Works
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Pipe Jointing
label | Acceptance / Conformance Criteria - Join PE pipe sections by butt fusion welding, in compliance with Section 3.2.2 of T-EES 04311. Remove all external and internal welding beads. Clean dirt and loose material from the pipe and examine it for any damage to the surface before drawing it into the reamed hole.
label | Standard / Specification - PS 16.28.6 T-EES: 04311 - 3.2.2
label | Verifying Document - Welding Records
label | Frequency - Each Weld
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
label | Comments / Closeout Details - Review if Internal beads need to be removed
checkpoint | Pipe String Inspection
label | Acceptance / Conformance Criteria - Prior to being drawn into the back-reamed hole PE pipes are to be welded together to form a continuous “string” using a butt welding process. The pipe string to be installed is to be fully assembled and inspected by the Engineer prior to commencing the installation.
label | Standard / Specification - T-EES: 04311 - 3.2.2
label | Verifying Document - Engineers Approval
label | Frequency - Each String
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Weld Identification
label | Acceptance / Conformance Criteria - Each weld is to be positively and uniquely identified (including the welding operators code) and the printout generated by the welding machine cross referenced and retained. The location of each weld is to be recorded so that its installed position can be identified.
label | Standard / Specification - T-EES: 04311 - 3.2.2
label | Verifying Document - Weld Records
label | Frequency - Each Weld
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | Weld Testing Pre-construction Welds
label | Acceptance / Conformance Criteria - The Contractor is required to perform specimen welds observed by the Engineer. At least 2 complying welds are to be completed for each pipe size. These welded joints are to be tested prior to commencing drilling and installation of the pipelines.
label | Standard / Specification - T-EES: 04311 - 3.4.1
label | Verifying Document - Weld Reports
label | Frequency - 2 welds per pipe size prior to works.
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Weld Testing Production Welds
label | Acceptance / Conformance Criteria - The Contractor is required to perform specimen welds observed by the Engineer. Further weld tests are required at the rate of 1 % of welds completed on each size of pipe.
label | Standard / Specification - T-EES: 04311 - 3.4.1
label | Verifying Document - Weld Reports
label | Frequency - Every 1 in 100 welds for each pipe size.
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Pipe Damage Inspection
label | Acceptance / Conformance Criteria - Check each pipe for notching and gouging. The maximum gouge depth is 10% of the pipe wall thickness.
label | Standard / Specification - PS 16.28.6
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Bolt Torquing
label | Acceptance / Conformance Criteria - The bolts are to be inserted and tightened following an appropriate methodology.
label | Standard / Specification - T-EES: 04311 - 2.3
label | Verifying Document - Torque Sheet
label | Frequency - Each Flange
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Denso Wrapping Joints
label | Acceptance / Conformance Criteria - Where the flanged connection is to be buried the completed connection is to be wrapped in Denso Tape before backfilling.
label | Standard / Specification - T-EES: 04311 - 2.3
label | Verifying Document - Site Records
label | Frequency - Each Buried Fitting
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Grouting
label | Acceptance / Conformance Criteria - Seal the reamed annulus around the pipe with grout for a minimum distance of 500 mm from the outside face of the launch and reception pits.
label | Standard / Specification - PS 16.28.6
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | Post-Installation Inspections
label | Acceptance / Conformance Criteria - The Contractor is required to cause inspection of the pipeline after installation and measure the ovality of the pipe. Deviation from circular greater than 7% of the nominal diameter of the pipe is unacceptable. The Contractor is required to inspect the interior of the installed pipeline using CCTV. CCTV Inspection Reports are to record the location of all laterals to an accuracy of +/-0.1m.
label | Standard / Specification - T-EES: 04311 - 3.4.2
label | Verifying Document - CCTV Video and Report
label | Frequency - Each Pipeline
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | As Built Records
label | Acceptance / Conformance Criteria - Prior to acceptance as-built records of completed sections of installed pipeline shall be submitted to the Engineer. The format of the as-built records shall comply with specific requirements of the Contract Specification.
label | Standard / Specification - T-EES: 04311 - 3.4.4
label | Verifying Document - Survey Records
label | Frequency - Each Pipeline
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | Pressure Test: M5 Water Loss Method
label | Acceptance / Conformance Criteria - Pressure testing of mains 355PE and larger to be M5 Water Loss Method. The final tests are to be witnessed by Council prior to the pipe being connected to the ‘live’ network. No further connections will be permitted after this stage.
label | Standard / Specification - ASNZS: 2566.2 T-EES: 04311 - 3.5
label | Verifying Document - Test Report
label | Frequency - Prior to livening of new main
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
label | Comments / Closeout Details - Do we need to pressure test gravity lines?
holdpoint | AUTHORITY HOLDPOINT
section | 4.02 Swales
checkpoint | Swale invert
label | Acceptance / Conformance Criteria - Swale invert shall have a uniform gradient and the line and level at any point shall not vary by more than ±20mm from the vertical set-out position and ±50mm for the horizontal set-out position
label | Standard / Specification - 16.34.4
label | Verifying Document - Survey
label | Frequency - Each Swale
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | Swale batters
label | Acceptance / Conformance Criteria - Swale batters shall be uniform slope and the line and level of the top of the batter shall uniform slope and not vary by more than ±50mm from the vertical set-out position and ±50mm for the horizontal set-out position.
label | Standard / Specification - 16.34.4
label | Verifying Document - Survey
label | Frequency - Each Swale
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | Grated Trench Drain
label | Acceptance / Conformance Criteria - Grated Trench Drains shall be installed as per Manufacturers specifications
label | Standard / Specification - PS 16.34
label | Verifying Document - Site Records
label | Frequency - As per manufacturers specifications
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 4.02 16.35 CCTV Inspections
checkpoint | CCTV stormwater pipe
label | Acceptance / Conformance Criteria - Every stormwater pipeline 300mm and greater shall be inspected by means of CCTV camera at the completion of each pipe trench backfill and compaction and at the completion of Earthworks operations (or at a time otherwise agreed with the Engineer).
label | Standard / Specification - PS 16.34, PS 16.35.1
label | Verifying Document - CCTV Video and Report
label | Frequency - At completion of pipes laying, backfilling but prior to final surfacing (Pavements, etc.)
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | Pavement Construction CCTV Review
label | Acceptance / Conformance Criteria - Prior to pavement construction, The Contractor shall submit the pipe condition inspection report to the Engineer for acceptance. The pipe condition inspection report is to be based on CCTV for all pipes upon completion of backfilling the trench.
label | Standard / Specification - PS 16.37
label | Verifying Document - Engineers Acceptance
label | Frequency - Prior to pavement construction above Stormwater pipelines
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 4.02 As Built Records
checkpoint | Survey Requirements - Stormwater Systems - Underground:
label | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings.: Trench invert. Pipe/structure bedding and backfill compaction. Pipe/structure size, class, alignment, and level. Manhole and catchpit position, levels (lid and inverts). Outlet structures including position, levels, erosion provisions and fish passages.
label | Standard / Specification - PS 16.33
label | Verifying Document - Survey
label | Frequency - All underground Stormwater Systems
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | Survey Requirements - Stormwater Systems – Above ground:
label | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings: Treatment swales, wetlands, basin’s location, profile and grade. Diversion Drain location, profile, and grade. Trench excavation and invert. Line, levels and grade of kerb and channels. Rodding eye locations.
label | Standard / Specification - PS 16.33
label | Verifying Document - Survey
label | Frequency - All above ground Stormwater Systems
label | Verification Activity: Activity - I
label | Verification Activity: By - SV