## Project Structure
Folders |  |  |  |  | Notes | Checklists
Site QA |  | please change all levels + rooms into folders so that additional checklists can be added to areas as required
| Authority Water Connection |  |  |  |  | Authority Main to Meter Installation
In-Ground Services
Basement Level
|  |  | Drainage Installation (In-Ground) |  |  | Drainage Installation (In-ground)
|  |  | Water Service Installation (In-ground) |  |  | Water Service Installation (In-ground)
|  |  | Gas Service Installation (In-ground) |  |  | Gas Service Installation (In-ground)
Ground Level
|  |  | Drainage Installation (In-Ground) |  |  | Drainage Installation (In-ground)
|  |  | Water Service Installation (In-ground) |  |  | Water Service Installation (In-ground)
|  |  | Gas Service Installation (In-ground) |  |  | Gas Service Installation (In-ground)
Penetrations
|  | Ground Level |  |  |  | Penetration Installation
|  | Level 1 |  |  |  | Penetration Installation
|  | Level 2 |  |  |  | Penetration Installation
|  | Level 3 |  |  |  | Penetration Installation
|  | Level 4 |  |  |  | Penetration Installation
|  | Level 5 |  |  |  | Penetration Installation
|  | Level 6 |  |  |  | Penetration Installation
Stacks & Vents
|  | Ground Level |  |  |  | Stack & Vent Installation
|  | Level 1 |  |  |  | Stack & Vent Installation
|  | Level 2 |  |  |  | Stack & Vent Installation
|  | Level 3 |  |  |  | Stack & Vent Installation
|  | Level 4 |  |  |  | Stack & Vent Installation
|  | Level 5 |  |  |  | Stack & Vent Installation
|  | Level 6 |  |  |  | Stack & Vent Installation
Downpipes
|  | Ground Level |  |  |  | Downpipe & Overflow Installation
|  | Level 1 |  |  |  | Downpipe & Overflow Installation
|  | Level 2 |  |  |  | Downpipe & Overflow Installation
|  | Level 3 |  |  |  | Downpipe & Overflow Installation
|  | Level 4 |  |  |  | Downpipe & Overflow Installation
|  | Level 5 |  |  |  | Downpipe & Overflow Installation
|  | Level 6 |  |  |  | Downpipe & Overflow Installation
Water Mains/Risers
|  | Ground Level |  |  |  | Water Service Installation (Mains/Risers)
|  | Level 1 |  |  |  | Water Service Installation (Mains/Risers)
|  | Level 2 |  |  |  | Water Service Installation (Mains/Risers)
|  | Level 3 |  |  |  | Water Service Installation (Mains/Risers)
|  | Level 4 |  |  |  | Water Service Installation (Mains/Risers)
|  | Level 5 |  |  |  | Water Service Installation (Mains/Risers)
|  | Level 6 |  |  |  | Water Service Installation (Mains/Risers)
Gas Mains/Risers
|  | Ground Level |  |  |  | Gas Service Installation (Mains/Risers)
|  | Level 1 |  |  |  | Gas Service Installation (Mains/Risers)
|  | Level 2 |  |  |  | Gas Service Installation (Mains/Risers)
|  | Level 3 |  |  |  | Gas Service Installation (Mains/Risers)
|  | Level 4 |  |  |  | Gas Service Installation (Mains/Risers)
|  | Level 5 |  |  |  | Gas Service Installation (Mains/Risers)
|  | Level 6 |  |  |  | Gas Service Installation (Mains/Risers)
Wastes & Vents
Ground Level
|  |  | T1 (Lwr) |  |  | Waste & Vent Installation
|  |  | T2 (Lwr) |  |  | Waste & Vent Installation
|  |  | Break down into each room G.01 - G.11 |  |  | Waste & Vent Installation
Level 1
|  |  | T1 (Lwr) |  |  | Waste & Vent Installation
|  |  | T2 (Lwr) |  |  | Waste & Vent Installation
|  |  | Break down into each room 1.01 - 1.12 |  |  | Waste & Vent Installation
|  | Level 2 | Break down into each room 2.01 - 2.12 |  |  | Waste & Vent Installation
|  | Level 3 | Break down into each room 3.01 - 3.10 |  |  | Waste & Vent Installation
|  | Level 4 | Break down into each room 4.01 - 4.07 |  |  | Waste & Vent Installation
|  | Level 5 | Break down into each room 5.01 - 5.04 |  |  | Waste & Vent Installation
|  | Level 6 | Break down into each room 6.01 - 6.02 |  |  | Waste & Vent Installation
Water Rough-Ins
Ground Level
|  |  | T1 (Lwr) |  |  | Water Service Installation (Rough-ins)
|  |  | T2 (Lwr) |  |  | Water Service Installation (Rough-ins)
|  |  | Break down into each room G.01 - G.11 |  |  | Water Service Installation (Rough-ins)
Level 1
|  |  | T1 (Lwr) |  |  | Water Service Installation (Rough-ins)
|  |  | T2 (Lwr) |  |  | Water Service Installation (Rough-ins)
|  |  | Break down into each room 1.01 - 1.12 |  |  | Water Service Installation (Rough-ins)
|  | Level 2 | Break down into each room 2.01 - 2.12 |  |  | Water Service Installation (Rough-ins)
|  | Level 3 | Break down into each room 3.01 - 3.10 |  |  | Water Service Installation (Rough-ins)
|  | Level 4 | Break down into each room 4.01 - 4.07 |  |  | Water Service Installation (Rough-ins)
|  | Level 5 | Break down into each room 5.01 - 5.04 |  |  | Water Service Installation (Rough-ins)
|  | Level 6 | Break down into each room 6.01 - 6.02 |  |  | Water Service Installation (Rough-ins)
Gas Rough-Ins
|  | Ground Level |  |  |  | Gas Service Installation (Rough-ins)
|  |  | T1 (Lwr) |  |  | Gas Service Installation (Rough-ins)
|  |  | T2 (Lwr) |  |  | Gas Service Installation (Rough-ins)
|  |  | Break down into each room G.01 - G.11 |  |  | Gas Service Installation (Rough-ins)
Level 1
|  |  | T1 (Lwr) |  |  | Gas Service Installation (Rough-ins)
|  |  | T2 (Lwr) |  |  | Gas Service Installation (Rough-ins)
|  |  | Break down into each room 1.01 - 1.12 |  |  | Gas Service Installation (Rough-ins)
|  | Level 2 | Break down into each room 2.01 - 2.12 |  |  | Gas Service Installation (Rough-ins)
|  | Level 3 | Break down into each room 3.01 - 3.10 |  |  | Gas Service Installation (Rough-ins)
|  | Level 4 | Break down into each room 4.01 - 4.07 |  |  | Gas Service Installation (Rough-ins)
|  | Level 5 | Break down into each room 5.01 - 5.04 |  |  | Gas Service Installation (Rough-ins)
|  | Level 6 | Break down into each room 6.01 - 6.02 |  |  | Gas Service Installation (Rough-ins)
Fixtures & Tapware Installation
Ground Level
T1 (Lwr)
|  |  |  | Toilet & Cistern Installation |  | Toilet & Cistern Installation
|  |  |  | Wash Basin & Tapware Installation |  | Wash Basin & Tapware Installation
|  |  |  | Shower & Tapware Installation |  | Shower & Tapware Installation
|  |  |  | Bath & Tapware Installation |  | Bath & Tapware Installation
|  |  |  | Kitchen Sink & Tapware Installation |  | Kitchen Sink & Tapware Installation
|  |  |  | Dish/Glass Washer Installation |  | Washer Machine Installation
|  |  |  | Laundry Trough & Tapware Installation |  | Laundry Trough & Tapware Installation
|  |  |  | Tundish Installation |  | Tundish Installation
|  |  |  | Hose Tap Installation |  | Hose Tap Installation
|  |  | T2 (Lwr) |  | same as T1
|  |  | Break down into each room G.01 - G.11 |  | same as T1
Level 1
|  |  | T1 (Lwr) |  | as per Ground Level
|  |  | T2 (Lwr) |  | as per Ground Level
|  |  | Break down into each room 1.01 - 1.12 |  | as per Ground Level
|  | Level 2 | Break down into each room 2.01 - 2.12 |  | as per Ground Level
|  | Level 3 | Break down into each room 3.01 - 3.10 |  | as per Ground Level
|  | Level 4 | Break down into each room 4.01 - 4.07 |  | as per Ground Level
|  | Level 5 | Break down into each room 5.01 - 5.04 |  | as per Ground Level
|  | Level 6 | Break down into each room 6.01 - 6.02 |  | as per Ground Level
Plant & Equipment Installation
|  | Basement Level |  |  |  | Plant & Equipment Installation
|  | Ground Level |  |  |  | Plant & Equipment Installation
|  | Level 4 |  |  |  | Plant & Equipment Installation
Testing
| Commissioning |  |  |  | ability to add
ability to add

## Checklists
| Type | Name | Values | Prefix | Postfix
Checklist 240122
1 | checklist | Add New Task
1 | checkpoint | This new task has been checked off & documented as noted below:
1
2 | checklist | Drainage Installation (In-ground)
2 | checkpoint | Installation complies with current AS/NZS-3500
2 | checkpoint | Installation complies with current drawings & specifications
2 | checkpoint | Installation & materials were used, comply with manufacturer requirements
2 | checkpoint | Check for damage & leaks
2 | checkpoint | Check materials & joining methods
2 | checkpoint | Check alignments & levels
2 | checkpoint | Check bedding & clearances
2 | checkpoint | Check connections to pits, tanks, etc
2 | checkpoint | Check covers, venting & conduits to pits, tanks, etc
2 | checkpoint | Check pipework & traps are clear of debris
2 | checkpoint | Check inspection openings
2 | checkpoint | Check open ends are sealed
2 | checkpoint | Check pipe trench marking tape (if specified)
2 | checkpoint | Check trench backfill & compaction
2 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
2
3 | checklist | Stack & Vent Installation
3 | checkpoint | Installation complies with current AS/NZS-3500
3 | checkpoint | Installation complies with current drawings & specifications
3 | checkpoint | Installation & materials were used, comply with manufacturer requirements
3 | checkpoint | Check for damage & leaks
3 | checkpoint | Check materials & joining methods
3 | checkpoint | Check alignments & levels
3 | checkpoint | Check clip spacing & pipe separation
3 | checkpoint | Check expansion joints
3 | checkpoint | Check inspection openings
3 | checkpoint | Check pipework is clear of debris
3 | checkpoint | Check open ends are sealed
3 | checkpoint | Check acoustic insulation (if specified)
3 | checkpoint | Check pipe labelling
3 | checkpoint | Check floor/wall penetration fire proofing
3 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
3
4 | checklist | Waste & Vent Installation
4 | checkpoint | Installation complies with current AS/NZS-3500
4 | checkpoint | Installation complies with current drawings & specifications
4 | checkpoint | Installation & materials were used, comply with manufacturer requirements
4 | checkpoint | Check for damage & leaks
4 | checkpoint | Check materials & joining methods
4 | checkpoint | Check alignments & levels
4 | checkpoint | Check clip spacing & pipe separation
4 | checkpoint | Check expansion joints
4 | checkpoint | Check in-wall fixture mounting brackets
4 | checkpoint | Check in-wall waste pipes & vents
4 | checkpoint | Check inspection openings
4 | checkpoint | Check pipework & traps are clear of debris
4 | checkpoint | Check open ends are sealed
4 | checkpoint | Check acoustic insulation (if specified)
4 | checkpoint | Check pipe labelling
4 | checkpoint | Check floor/wall penetration fire proofing
4 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
4
5 | checklist | Cast-in Waste & Vent
5 | checkpoint | Installation complies with current AS/NZS-3500
5 | checkpoint | Installation complies with current drawings & specifications
5 | checkpoint | Installation & materials were used, comply with manufacturer requirements
5 | checkpoint | Check for damage & leaks
5 | checkpoint | Check materials & joining methods
5 | checkpoint | Check alignments & levels
5 | checkpoint | Check clip spacing & pipe separation
5 | checkpoint | Check pipework & traps are clear of debris
5 | checkpoint | Check open ends are sealed
5 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
5
6 | checklist | Downpipe & Overflow Installation
6 | checkpoint | Installation complies with current AS/NZS-3500
6 | checkpoint | Installation complies with current drawings & specifications
6 | checkpoint | Installation & materials were used, comply with manufacturer requirements
6 | checkpoint | Check for damage & leaks
6 | checkpoint | Check materials & joining methods
6 | checkpoint | Check alignments & levels
6 | checkpoint | Check clip spacing & pipe separation
6 | checkpoint | Check expansion joints
6 | checkpoint | Check connection to roof & floor outlets
6 | checkpoint | Check inspection openings
6 | checkpoint | Check pipework is clear of debris
6 | checkpoint | Check open ends are sealed
6 | checkpoint | Check acoustic insulation (if specified)
6 | checkpoint | Check pipe labelling
6 | checkpoint | Check floor/wall penetration fire proofing
6 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
6
7 | checklist | Pump Line Installation
7 | checkpoint | Installation complies with current AS/NZS-3500
7 | checkpoint | Installation complies with current drawings & specifications
7 | checkpoint | Installation & materials were used, comply with manufacturer requirements
7 | checkpoint | Check for damage & leaks
7 | checkpoint | Check materials & joining methods
7 | checkpoint | Check alignments & levels
7 | checkpoint | Check clip spacing & pipe separation
7 | checkpoint | Check pipework is clear of debris
7 | checkpoint | Check open ends are sealed
7 | checkpoint | Check pipe labelling
7 | checkpoint | Check floor/wall penetration fire proofing
7 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
7
8 | checklist | Suction Line Installation
8 | checkpoint | Installation complies with current AS/NZS-3500
8 | checkpoint | Installation complies with current drawings & specifications
8 | checkpoint | Installation & materials were used, comply with manufacturer requirements
8 | checkpoint | Check for damage & leaks
8 | checkpoint | Check materials & joining methods
8 | checkpoint | Check alignments & levels
8 | checkpoint | Check clip spacing & pipe separation
8 | checkpoint | Check pipework is clear of debris
8 | checkpoint | Check open ends are sealed
8 | checkpoint | Check pipe labelling
8 | checkpoint | Check floor/wall penetration fire proofing
8 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
8
9 | checklist | Authority Main to Meter Installation
9 | checkpoint | Installation complies with current AS/NZS-3500
9 | checkpoint | Installation complies with current drawings & specifications
9 | checkpoint | Installation & materials were used, comply with manufacturer requirements
9 | checkpoint | Check for damage & leaks
9 | checkpoint | Check materials & joining methods
9 | checkpoint | Check alignments & levels
9 | checkpoint | Check bedding & clearances
9 | checkpoint | Check valve connections
9 | checkpoint | Check pipework is clear of debris
9 | checkpoint | Check pipe trench marking tape (if specified)
9 | checkpoint | Check trench backfill & compaction
9 | checkpoint | Check water meter assemblies
9 | checkpoint | Check RPZD assemblies
9 | checkpoint | Check pipe labelling
9 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
9
10 | checklist | Water Service Installation (In-ground)
10 | checkpoint | Installation complies with current AS/NZS-3500
10 | checkpoint | Installation complies with current drawings & specifications
10 | checkpoint | Installation & materials were used, comply with manufacturer requirements
10 | checkpoint | Check for damage & leaks
10 | checkpoint | Check materials & joining methods
10 | checkpoint | Check alignments & levels
10 | checkpoint | Check bedding & clearances
10 | checkpoint | Check valve connections
10 | checkpoint | Check pipework is clear of debris
10 | checkpoint | Check open ends are sealed
10 | checkpoint | Check pipe trench marking tape (if specified)
10 | checkpoint | Check trench backfill & compaction
10 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
10
11 | checklist | Water Service Installation (Mains/Risers)
11 | checkpoint | Installation complies with current AS/NZS-3500
11 | checkpoint | Installation complies with current drawings & specifications
11 | checkpoint | Installation & materials were used, comply with manufacturer requirements
11 | checkpoint | Check for damage & leaks
11 | checkpoint | Check crimp fittings
11 | checkpoint | Check materials & joining methods
11 | checkpoint | Check alignments & levels
11 | checkpoint | Check clip spacing & pipe separation
11 | checkpoint | Check expansion joints and anchor points
11 | checkpoint | Check valves & meter assemblies
11 | checkpoint | Check valves & meter assemblies fixings & brackets
11 | checkpoint | Check hot water pipe clips & thermal insulation (if specified)
11 | checkpoint | Check pipework is clear of debris
11 | checkpoint | Check for cross connections
11 | checkpoint | Check open ends are sealed
11 | checkpoint | Check pipe labelling
11 | checkpoint | Check floor/wall penetration fire proofing
11 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
11
12 | checklist | Water Service Installation (Rough-ins)
12 | checkpoint | Installation complies with current AS/NZS-3500
12 | checkpoint | Installation complies with current drawings & specifications
12 | checkpoint | Installation & materials were used, comply with manufacturer requirements
12 | checkpoint | Check for damage & leaks
12 | checkpoint | Check crimp fittings
12 | checkpoint | Check for cross connections
12 | checkpoint | Check alignment & levels
12 | checkpoint | Check materials & joining methods
12 | checkpoint | Check clip spacing & pipe separation
12 | checkpoint | Check TMV/TV
12 | checkpoint | Check mixer bodies & lugged elbows
12 | checkpoint | Check in-wall pan & cistern brackets
12 | checkpoint | Check noggings for future fixture
12 | checkpoint | Check sharp edge pipe protection
12 | checkpoint | Check heat trace (if specified)
12 | checkpoint | Check hot water pipe clips & thermal insulation (if specified)
12 | checkpoint | Check pipe colour coding
12 | checkpoint | Check floor/wall penetration fire proofing
12 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
12
13 | checklist | Backflow Prevention Device Installation
13 | checkpoint | Installation complies with current AS/NZS-3500
13 | checkpoint | Installation complies with current drawings & specifications
13 | checkpoint | Installation & materials were used, comply with manufacturer requirements
13 | checkpoint | Check for damage & leaks
13 | checkpoint | Check materials & joining methods
13 | checkpoint | Check alignments & levels
13 | checkpoint | Check clip spacing & pipe separation
13 | checkpoint | Check pressure relief pipe to tundish
13
14 | checklist | Water Meter Installation
14 | text | Meter Type:
14 | text | Meter Number:
14 | text | Meter Location:
14 | text | Meter Size:
14 | checkpoint | Installation complies with current AS/NZS-3500
14 | checkpoint | Installation complies with current drawings & specifications
14 | checkpoint | Installation & materials were used, comply with manufacturer requirements
14
15 | checklist | Gas Service Installation (In-ground)
15 | checkpoint | Installation complies with current AS/NZS-3500
15 | checkpoint | Installation complies with current drawings & specifications
15 | checkpoint | Installation & materials were used, comply with manufacturer requirements
15 | checkpoint | Check for damage & leaks
15 | checkpoint | Check materials & joining methods
15 | checkpoint | Check alignments & levels
15 | checkpoint | Check bedding & clearances
15 | checkpoint | Check valve connections
15 | checkpoint | Check pipework is clear of debris
15 | checkpoint | Check open ends are sealed
15 | checkpoint | Check pipe trench marking tape (if specified)
15 | checkpoint | Check trench backfill & compaction
15 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
15
16 | checklist | Gas Service Installation (Mains/Risers)
16 | checkpoint | Installation complies with current AS/NZS-3500
16 | checkpoint | Installation complies with current drawings & specifications
16 | checkpoint | Installation & materials were used, comply with manufacturer requirements
16 | checkpoint | Check for damage & leaks
16 | checkpoint | Check materials & joining methods
16 | checkpoint | Check crimp fittings
16 | checkpoint | Check alignments & levels
16 | checkpoint | Check clip spacing & pipe separation
16 | checkpoint | Check valves & meter assemblies
16 | checkpoint | Check valves & meter assemblies fixings & brackets
16 | checkpoint | Check pipework is clear of debris
16 | checkpoint | Check for cross connections
16 | checkpoint | Check open ends are sealed
16 | checkpoint | Check pipe labelling
16 | checkpoint | Check floor/wall penetration fire proofing
16 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
16
17 | checklist | Gas Service Installation (Rough-ins)
17 | checkpoint | Installation complies with current AS/NZS-3500
17 | checkpoint | Installation complies with current drawings & specifications
17 | checkpoint | Installation & materials were used, comply with manufacturer requirements
17 | checkpoint | Check for damage & leaks
17 | checkpoint | Check crimp fittings
17 | checkpoint | Check for cross connections
17 | checkpoint | Check alignment & levels
17 | checkpoint | Check materials & joining methods
17 | checkpoint | Check clip spacing & pipe separation
17 | checkpoint | Check lugged elbows
17 | checkpoint | Check noggings for future fixture
17 | checkpoint | Check sharp edge pipe protection
17 | checkpoint | Check pipe colour coding
17 | checkpoint | Check floor/wall penetration fire proofing
17 | checkpoint | Testing by approved method has been complete (must provide test pressure photos)
17
18 | checklist | Penetration Installation
18 | checkpoint | Installation complies with current AS/NZS-3500
18 | checkpoint | Installation complies with current drawings & specifications
18 | checkpoint | Installation & materials were used, comply with manufacturer requirements
18 | checkpoint | Check for damage & missing penos
18 | checkpoint | Check penetration sizes, locations & finished levels are corrrect
18 | checkpoint | Check fire collars types & ratings are correct
18 | checkpoint | Check blank sleeves are correct
18 | checkpoint | Check cast-in outlets location & finished levels are correct
18 | checkpoint | Check open ends are sealed
18
19 | checklist | Toilet & Cistern Installation
19 | checkpoint | Installation complies with current AS/NZS-3500
19 | checkpoint | Installation complies with current drawings & specifications
19 | checkpoint | Installation & materials were used, comply with manufacturer requirements
19 | checkpoint | Check for damage or leaks
19 | checkpoint | Check level & alignment
19 | checkpoint | Check mini stops
19 | checkpoint | Check flexible connections are not twisted or kinked
19 | checkpoint | Check button assembly is securely fitted
19 | checkpoint | Check seat & lid function
19 | checkpoint | Check special DDA accessories (if applicable)
19 | checkpoint | Check operation, controls & remote sensors
19 | checkpoint | Check trap is clear of debris
19 | checkpoint | Check caulking
19
20 | checklist | Urinal & Cistern Installation
20 | checkpoint | Installation complies with current AS/NZS-3500
20 | checkpoint | Installation complies with current drawings & specifications
20 | checkpoint | Installation & materials were used, comply with manufacturer requirements
20 | checkpoint | Check for damage or leaks
20 | checkpoint | Check level & alignment
20 | checkpoint | Check mini stops
20 | checkpoint | Check flexible connections are not twisted or kinked
20 | checkpoint | Check button assembly
20 | checkpoint | Check operation, controls & remote sensors
20 | checkpoint | Check trap is clear of debris
20 | checkpoint | Check caulking is correct
20
21 | checklist | Wash Basin & Tapware Installation
21 | checkpoint | Installation complies with current AS/NZS-3500
21 | checkpoint | Installation complies with current drawings & specifications
21 | checkpoint | Installation & materials were used, comply with manufacturer requirements
21 | checkpoint | Check for damage or leaks
21 | checkpoint | Check level & alignment
21 | checkpoint | Check mini stops
21 | checkpoint | Check flexible connections are not twisted or kinked
21 | checkpoint | Check special DDA accessories (if applicable)
21 | checkpoint | Check waste & trap connections
21 | checkpoint | Check operation, controls & remote sensors
21 | checkpoint | Check trap is clear of debris
21 | checkpoint | Check caulking
21
22 | checklist | Shower & Tapware Installation
22 | checkpoint | Installation complies with current AS/NZS-3500
22 | checkpoint | Installation complies with current drawings & specifications
22 | checkpoint | Installation & materials were used, comply with manufacturer requirements
22 | checkpoint | Check for damage or leaks
22 | checkpoint | Check level & alignment
22 | checkpoint | Check wall plates, mixers & diversion valves
22 | checkpoint | Check outlets, wall rails & hand showers
22 | checkpoint | Check special DDA accessories (if applicable)
22 | checkpoint | Check waste & trap connections
22 | checkpoint | Check operation & controls
22 | checkpoint | Check floor grate level & alignment
22 | checkpoint | Check trap is clear of debris
22 | checkpoint | Check caulking
22
23 | checklist | Bath & Tapware Installation
23 | checkpoint | Installation complies with current AS/NZS-3500
23 | checkpoint | Installation complies with current drawings & specifications
23 | checkpoint | Installation & materials were used, comply with manufacturer requirements
23 | checkpoint | Check for damage or leaks
23 | checkpoint | Check level & alignment
23 | checkpoint | Check wall plates, mixers & diversion valves
23 | checkpoint | Check outlets, wall rails & hand showers
23 | checkpoint | Check special DDA accessories (if applicable)
23 | checkpoint | Check waste & trap connections
23 | checkpoint | Check operation & controls
23 | checkpoint | Check floor grate level & alignment
23 | checkpoint | Check trap is clear of debris
23 | checkpoint | Check caulking
23
24 | checklist | Kitchen Sink & Tapware Installation
24 | checkpoint | Installation complies with current AS/NZS-3500
24 | checkpoint | Installation complies with current drawings & specifications
24 | checkpoint | Installation & materials were used, comply with manufacturer requirements
24 | checkpoint | Check for damage or leaks
24 | checkpoint | Check level & alignment
24 | checkpoint | Check mini stops
24 | checkpoint | Check flexible connections are not twisted or kinked
24 | checkpoint | Check waste & trap connections
24 | checkpoint | Check dishwasher waste & water connections
24 | checkpoint | Check stop valves for future connections are capped
24 | checkpoint | Check operation & controls
24 | checkpoint | Check trap is clear of debris
24 | checkpoint | Check caulking
24
25 | checklist | Washer Machine Installation
25 | checkpoint | Installation complies with current AS/NZS-3500
25 | checkpoint | Installation complies with current drawings & specifications
25 | checkpoint | Installation & materials were used, comply with manufacturer requirements
25 | checkpoint | Check for damage or leaks
25 | checkpoint | Check level & alignment
25 | checkpoint | Check mini stops are correct
25 | checkpoint | Check wall tundish & waste connections
25 | checkpoint | Check stop valves are capped
25 | checkpoint | Check operation & controls
25
26 | checklist | Laundry Trough & Tapware Installation
26 | checkpoint | Installation complies with current AS/NZS-3500
26 | checkpoint | Installation complies with current drawings & specifications
26 | checkpoint | Installation & materials were used, comply with manufacturer requirements
26 | checkpoint | Check for damage or leaks
26 | checkpoint | Check level & alignment
26 | checkpoint | Check mini stops
26 | checkpoint | Check flexible connections are not twisted or kinked
26 | checkpoint | Check waste & trap connections
26 | checkpoint | Check dishwasher waste & water connections
26 | checkpoint | Check stop valves for future connections are capped
26 | checkpoint | Check operation & controls
26 | checkpoint | Check trap is clear of debris
26 | checkpoint | Check caulking
26
27 | checklist | Tundish Installation
27 | checkpoint | Installation complies with current AS/NZS-3500
27 | checkpoint | Installation complies with current drawings & specifications
27 | checkpoint | Installation & materials were used, comply with manufacturer requirements
27 | checkpoint | Check for damage or leaks
27 | checkpoint | Check level & alignment
27 | checkpoint | Check waste & trap connections
27 | checkpoint | Check trap is clear of debris
27
28 | checklist | Hose Tap Installation
28 | checkpoint | Installation complies with current AS/NZS-3500
28 | checkpoint | Installation complies with current drawings & specifications
28 | checkpoint | Installation & materials were used, comply with manufacturer requirements
28 | checkpoint | Check for damage or leaks
28 | checkpoint | Check pipe colour coding
28
30 | checklist | Gas Appliance Installation
30 | checkpoint | Installation complies with current AS/NZS-3500
30 | checkpoint | Installation complies with current drawings & specifications
30 | checkpoint | Installation & materials were used, comply with manufacturer requirements
30 | checkpoint | Check for damage or leaks
30 | checkpoint | Check level & alignment is correct
30 | checkpoint | Check surrounding wall material is fire rated
30 | checkpoint | Check distance from cook-top to range hood complies with manufacturer specification
30 | checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification
30 | checkpoint | Check flexible connections are not twisted or kinked
30 | checkpoint | Check gas isolation valve
30 | checkpoint | Check gas pressure regulator
30 | checkpoint | Check operation & controls
30
32 | checklist | Cleaners Sink & Tapware Installations
32 | checkpoint | Installation complies with current AS/NZS-3500
32 | checkpoint | Installation complies with current drawings & specifications
32 | checkpoint | Installation & materials were used, comply with manufacturer requirements
32 | checkpoint | Check for damage or leaks
32 | checkpoint | Check level & alignment
32 | checkpoint | Check tapware for fit & function
32 | checkpoint | Check wall brackest & fixings
32 | checkpoint | Check bucket grate
32 | checkpoint | Check waste & trap connections
32 | checkpoint | Check trap is clear of debris
32 | checkpoint | Check caulking
32
33 | checklist | Water Heating, Boiling, Chilling, Unit Installation
33 | checkpoint | Installation complies with current AS/NZS-3500
33 | checkpoint | Installation complies with current drawings & specifications
33 | checkpoint | Installation & materials were used, comply with manufacturer requirements
33 | checkpoint | Check for damage or leaks
33 | checkpoint | Check level & alignment
33 | checkpoint | Check mini stops
33 | checkpoint | Check isolation valves & non-return valves
33 | checkpoint | Check pressure reduction valve (if specified)
33 | checkpoint | Check flexible connections are not twisted or kinked
33 | checkpoint | Check waste connections
33 | checkpoint | Check operation & controls
33 | checkpoint | Check water temperatures are as specified
33
34 | checklist | Plant & Equipment Installation
34 | checkpoint | Plant & Equipment Installation checked off as below
34 | checkpoint | Installation complies with current AS/NZS-3500
34 | checkpoint | Installation complies with current drawings & specifications
34 | checkpoint | Installation & materials were used in accordance with manufacturer requirements
34 | checkpoint | Check for damage & leaks
34 | checkpoint | Check tundishes are correct
34 | checkpoint | Check electrical power is available
34 | checkpoint | Check BMS is available
34
35 | checklist | Testing Drainage Pipework (Air Test)
35 | checkpoint | Installation complies with current AS/NZS-3500
35 | checkpoint | Installation complies with current drawings & specifications
35 | checkpoint | Installation & materials were used, comply with manufacturer requirements
35 | checkpoint | Check installation is clean and ready for testing
35 | checkpoint | Apply air test as per AS/NZS-3500 (Provide test process photos)
35
36 | checklist | Testing Drainage Pipework (Water Test)
36 | checkpoint | Installation complies with current AS/NZS-3500
36 | checkpoint | Installation complies with current drawings & specifications
36 | checkpoint | Installation & materials were used, comply with manufacturer requirements
36 | checkpoint | Check installation is clean and ready for testing
36 | checkpoint | Apply water test as per AS/NZS-3500 (Provide test process photos)
36
37 | checklist | Testing Water Pipework (Water Test)
37 | checkpoint | Installation complies with current AS/NZS-3500
37 | checkpoint | Installation complies with current drawings & specifications
37 | checkpoint | Installation & materials were used, comply with manufacturer requirements
37 | checkpoint | Check installation is clean and ready for testing
37 | checkpoint | Apply water test as per AS/NZS-3500 (Provide test process photos)
37
38 | checklist | Testing Gas Service (Air Test)
38 | checkpoint | Installation complies with current AS/NZS-5600
38 | checkpoint | Installation complies with current drawings & specifications
38 | checkpoint | Installation & materials were used, comply with manufacturer requirements
38 | checkpoint | Check installation is clean and ready for testing
38 | checkpoint | Apply air test as per AS/NZS-5600 (Provide test process photos)
38
39 | checklist | Commission Drainage Pump Station
39 | checkpoint | Installation complies with current AS/NZS-3500
39 | checkpoint | Installation complies with current drawings & specifications
39 | checkpoint | Installation & materials were used, comply with manufacturer requirements
39 | checkpoint | Check lifting rails & chains
39 | checkpoint | Check water level sensor set points
39 | checkpoint | Check pump motor rotation
39 | checkpoint | Check dry pump fault
39 | checkpoint | Check low water level fault
39 | checkpoint | Check high water level fault
39 | checkpoint | Check auto pump roll-over
39 | checkpoint | Check pump package operational set points
39 | checkpoint | Check control panel display & set points
39 | checkpoint | Check fault warning alarms
39 | checkpoint | Check BMS connection as specified
39 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
39
40 | checklist | Commission Water Pressure Pump Set
40 | checkpoint | Installation complies with current AS/NZS-3500
40 | checkpoint | Installation complies with current drawings & specifications
40 | checkpoint | Installation & materials were used, comply with manufacturer requirements
40 | checkpoint | Check water supply fault
40 | checkpoint | Check pump motor rotation
40 | checkpoint | Check dry pump fault
40 | checkpoint | Check auto pump roll-over
40 | checkpoint | Check pump package operational set points
40 | checkpoint | Check control panel display & set points
40 | checkpoint | Check fault warning alarms
40 | checkpoint | Check BMS connection as specified
40 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
40
41 | checklist | Commission Rain Water Pressure Pump Set
41 | checkpoint | Installation complies with current AS/NZS-3500
41 | checkpoint | Installation complies with current drawings & specifications
41 | checkpoint | Installation & materials were used, comply with manufacturer requirements
41 | checkpoint | Check water supply fault
41 | checkpoint | Check pump motor rotation
41 | checkpoint | Check dry pump fault
41 | checkpoint | Check auto pump roll-over
41 | checkpoint | Check ultra violet lamps
41 | checkpoint | Check filters & backwash
41 | checkpoint | Check back-up water supply
41 | checkpoint | Check pump package operational set points
41 | checkpoint | Check control panel display & set points
41 | checkpoint | Check fault warning alarms
41 | checkpoint | Check BMS connection as specified
41 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
41
42 | checklist | Commission Water Storage Tank
42 | checkpoint | Installation complies with current AS/NZS-3500
42 | checkpoint | Installation complies with current drawings & specifications
42 | checkpoint | Installation & materials were used, comply with manufacturer requirements
42 | checkpoint | Check valves are fully open
42 | checkpoint | Check water level sensor set points
42 | checkpoint | Check tank fill valve
42 | checkpoint | Check low level fault
42 | checkpoint | Check high level fault
42 | checkpoint | Check passive over-flow
42 | checkpoint | Check statutory warning signage
42 | checkpoint | Check control panel display & set points
42 | checkpoint | Check BMS connection as specified
42 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
42
43 | checklist | Commission Hot Water Generating Plant
43 | checkpoint | Installation complies with current AS/NZS-3500 & AS/NZS-5600
43 | checkpoint | Installation complies with current drawings & specifications
43 | checkpoint | Installation & materials were used, comply with manufacturer requirements
43 | checkpoint | Check valves are fully open
43 | checkpoint | Check water filters are clean
43 | checkpoint | Check gas supply
43 | checkpoint | Check circulating pumps
43 | checkpoint | Check flue operation
43 | checkpoint | Check system auto start
43 | checkpoint | Check flow & return temperatures
43 | checkpoint | Check control panel display & set points
43 | checkpoint | Check BMS connection as specified
43 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
43
44 | checklist | Commission Rain Water Diversion Valve
44 | checkpoint | Installation complies with current AS/NZS-3500
44 | checkpoint | Installation complies with current drawings & specifications
44 | checkpoint | Installation & materials were used, comply with manufacturer requirements
44 | checkpoint | Check valve operation
44 | checkpoint | Check valve defaults to storm-water if no power or tank full
44 | checkpoint | Check control panel display & set points
44 | checkpoint | Check BMS connection as specified
44 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
44
45 | checklist | Commission Thermostatic Mixing Valves
45 | checkpoint | Installation complies with current AS/NZS-3500
45 | checkpoint | Installation complies with current drawings & specifications
45 | checkpoint | Installation & materials were used, comply with manufacturer requirements
45 | checkpoint | Check water temperature does not exceed 45°C (Provide photo)
45
46 | checklist | Commission Reduced Pressure Zone Device
46 | checkpoint | Installation complies with current AS/NZS-3500
46 | checkpoint | Installation complies with current drawings & specifications
46 | checkpoint | Installation & materials were used, comply with manufacturer requirements
46 | checkpoint | Commissioning by certified persons only
46 | checkpoint | Check valves are fully open
46 | checkpoint | Check inlet water pressure does not exceed manufacturer specification
46 | checkpoint | Check outlet water pressure is as per manufacturer specification
46 | checkpoint | Check exhaust tundish drain sized to accept a full flush
46 | checkpoint | Provide the commissioning report & all plant documentation to this checkpoint
46
| z | z |  | z | z
checkpoint | Check electrical power is available (if applicable)
checkpoint | Check BMS is available (if applicable)
checklist | Testing Drainage Pipework (Static Air Test)
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check internal bore clear of blockages, constrictions or debris
checkpoint | Check pipe-work is secure to eliminate movement during test
checkpoint | Plug & seal open ends of pipe-work section to be tested
checkpoint | Connect pressure testing device to temporary valve point
checkpoint | Commence testing by slowly increasing pressure up to 30 kPa and hold
checkpoint | Discontinue pressurization & allow system to stabilization over 3 minutes
checkpoint | Testing is deemed successful if pressure drop is ≤ 5kPa over at least 30 minutes
checkpoint | Take a photo at the start & end of static pressure test
checkpoint | Following a succussful test, slowly release the pressure and return the system back to operational condition
checklist | Testing Drainage Pipework (Static Water Test)
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check internal bore is clear of blockages, constrictions or debris
checkpoint | Check pipe-work is secure to eliminate movement during test
checkpoint | Plug & seal open ends of pipe-work section to be tested
checkpoint | Extend a test riser 1 metre above the highest overflow point
checkpoint | Slowly fill the test riser with water until full and hold
checkpoint | Testing is deemed successful if the water level remains unchanged after at least 30 minutes
checkpoint | Take a photo at the start & end of static pressure test
checkpoint | Following a succussful test, slowly release the pressure and return the system back to operational condition
checklist | Testing Water Pipework (1500 kPa)
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves isolating the test zone are securely shut off & tagged
checkpoint | Nominate an air purging valve point
checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint | Check valves within the test zone are open as required
checkpoint | Check lugged elbows & open ends are capped
checkpoint | Check pressure sensitive mixing valves & meters are isolated from the test zone
checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint | Connect pressure testing device to the nominated test point
checkpoint | Shut off the water feeder valve
checkpoint | Commence testing by slowly increasing pressure up to 1500 kPa and hold
checkpoint | Testing is deemed successful if the water pressure remains unchanged after at least 30 minutes
checkpoint | Take a photo at the start & end of static pressure test
checkpoint | Following a succussful test, slowly release the pressure and return the system back to operational condition
checklist | Testing Potable Water (1.5 x MWP)
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves isolating the test zone are securely shut off & tagged
checkpoint | Nominate an air purging valve point
checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint | Check valves within the test zone are open as required
checkpoint | Check lugged elbows & open ends are capped
checkpoint | Check pressure sensitive mixing valves & meters are isolated from the test zone
checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint | Connect pressure testing device to the nominated test point
checkpoint | Shut off the water feeder valve
checkpoint | Commence testing by slowly increasing pressure up to one & half (1.5) x working pressure and hold
checkpoint | Testing is deemed successful if the water pressure remains unchanged after at least 30 minutes
checkpoint | Take a photo at the start & end of static pressure test
checkpoint | Following a succussful test, slowly release the pressure and return the system back to operational condition
checklist | Testing Potable Water Including Pressure Sensitive Valves (900 kPa)
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves isolating the test zone are securely shut off & tagged
checkpoint | Nominate an air purging valve point
checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint | Check valves within the test zone are open as required
checkpoint | Check lugged elbows & open ends are capped
checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint | Connect pressure testing device to the nominated test point
checkpoint | Shut off the water feeder valve
checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold
checkpoint | Testing is deemed successful if the water pressure remains unchanged after at least 30 minutes
checkpoint | Take a photo at the start & end of static pressure test
checkpoint | Following a succussful test, slowly release the pressure and return the system back to operational condition
checklist | Testing Gas Service
checkpoint | Installation complies with current AS/NZS-5600 (2013)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves isolating the test zone are securely shut off & tagged
checkpoint | Nominate an air purging valve point
checkpoint | Nominate a pressure testing valve point
checkpoint | Check valves isolating the test zone are securely shut off & tagged
checkpoint | Check lugged elbows & open ends are capped
checkpoint | Connect pressure testing device to the nominated test point
checkpoint | Slowly open test feeder valve & fill the test zone with inert gas until completely purged
checkpoint | Shut off the gas feeder valve
checkpoint | For high pressure test: Commence testing by slowly increasing pressure to 1.5 kPa above working pressure
checkpoint | For low pressure test: Commence testing by slowly increasing pressure up to no greater than 7kPa
checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint | Take a photo at the start & end of static pressure test
checkpoint | Following a succussful test, slowly release the pressure and return the system back to operational condition
checklist | Commission Drainage Pump Station
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check rails & lifting chains
checkpoint | Check level sensor or float tree settings
checkpoint | Check pump motor rotation
checkpoint | Check dry pump fault
checkpoint | Check low water level fault
checkpoint | Check each pumps specified pressure or level set points
checkpoint | Check auto pump roll-over on fault or system programming
checkpoint | Check system operations & fault status in control panel digital display
checkpoint | Check high water level fault
checkpoint | Check access covers for correct fitment
checkpoint | Check audio/visual alarm functions
checkpoint | Check BMS connection as specified
checkpoint | Check statutory warning signage is visible
checkpoint | Attach a PDF copy or photo of the suppliers test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Water Pressure Pump Set
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check dry pump fault
checkpoint | Check low water level fault
checkpoint | Check each pumps specified pressure set points
checkpoint | Check auto pump roll-over on fault or system programming
checkpoint | Check system operations & fault status in control panel digital display
checkpoint | Check audio/visual alarm functions
checkpoint | Check BMS connection as specified
checkpoint | Attach a PDF copy or photo of the suppliers test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Rain Water Pressure Pump Set
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check dry pump fault
checkpoint | Check low water level fault
checkpoint | Check each pumps specified pressure set points
checkpoint | Check pump auto roll-over function on system fault or pre-programming
checkpoint | Check system operations & fault status in control panel digital display
checkpoint | Check audio/visual alarm functions
checkpoint | Check ultra violet lamps are functioning correctly
checkpoint | Check filters & backwash are functioning correctly
checkpoint | Check back-up water and auto roll-over functions
checkpoint | Check BMS connection connection as specified
checkpoint | Attach a PDF copy or photo of the suppliers test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Water Storage Tank
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check water level sensor or float tree is set correctly
checkpoint | Check water auto fill valve or ball valve is set correctly
checkpoint | Check tank-fill pipe physical air break is correct
checkpoint | Check low water level fault
checkpoint | Check high water level fault
checkpoint | Check passive over-flow at least 100mm below outlet
checkpoint | Check system operations & fault status in control panel digital display
checkpoint | Check BMS connection as specified
checkpoint | Check access ladders are installed
checkpoint | Check statutory warning signage is visible
checkpoint | Attach a PDF copy or photo of the suppliers test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Hot Water Generating Plant
checkpoint | Installation complies with current AS/NZS-3500 (2018) or AS/NZS-5600 (2013)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check water filters are clean
checkpoint | Check gas supply inlet pressure
checkpoint | Check burners roll-over on system fault or pre-program
checkpoint | Check circulating pumps roll-over on system fault or pre-programming
checkpoint | Check room ventilation (Mech)
checkpoint | Check power flue operation
checkpoint | Check system shut-down on ventilation or gas fault
checkpoint | Check system auto re-start
checkpoint | Check system operations & fault status in control panel digital display
checkpoint | Check hot water flow & return temperature sensors or gauges
checkpoint | Check BMS connection as specified
checkpoint | Attach a PDF copy or photo of the suppliers test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Rain Water Drainage Diversion Valve
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check valve fault defaults to storm-water drainage
checkpoint | Check pneumatic connections to the compressor
checkpoint | Check data connection to the storage tanks
checkpoint | Check storage tank high level alarm defaults valve to storm-water drainage
checkpoint | Check BMS connection as specified
checkpoint | Attach a PDF copy or photo of the suppliers test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Thermostatic Mixing Valves
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check inlet water pressure does not exceed 500 kPa
checkpoint | Check warm water temperature does not exceed 45°C (Commercial DDA)
checkpoint | Check warm water temperature does not exceed 43°C (Special needs DDA)
checkpoint | Check warm water delivery time maximum temperature does not exceed 30 seconds
checkpoint | Check minimum warm water delivery volume to furthest point
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Reduced Pressure Zone Device
checkpoint | Installation complies with current AS/NZS-3500 (2018)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check valves are fully open
checkpoint | Check valve flow directions
checkpoint | Check inlet water pressure does not exceed manufacturer specification
checkpoint | Check outlet water pressure is as per manufacturer specification
checkpoint | Check exhaust tundish drain sized to accept a full flush
checkpoint | Use only a licensed RPZD tester for the commissioning
checkpoint | Attach a PDF copy or photo of the test report to this ITP
checkpoint | Following successful commissioning, return the system back to operational condition
checklist | Commission Fixture Groups
checkpoint | Installer is a Registered Plumber (VIC) with endorsements for this work
checkpoint | Installation complies with current AS/NZS-3500 (2018) or AS/NZS-5600 (2013)
checkpoint | Installation complies with current drawings & specifications
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Check all installation for any damage, leaks or missing components
checkpoint | Check for correct level & alignment of all fixtures
checkpoint | Check all fixtures, seats & covers are securely fastened
checkpoint | Check all valves are fully open
checkpoint | Check all valve flow directions
checkpoint | Check all flexible connections are not twisted or kinked
checkpoint | Check for water for cross connections
checkpoint | Check fixture wastes & connections
checkpoint | Check pipework & all traps are clear of debris
checkpoint | Check floor waste grates are installed
checkpoint | Check AAV is installed to correct height
checkpoint | Check future connection water valves are securely capped
checkpoint | Check water pressures do not exceed 500 kPa
checkpoint | Check tempering valves do not exceed 50°C
checkpoint | Check thermostatic mixing valves do not exceed 45°C
checkpoint | Check hot or warm water delivery does not exceed 30 seconds
checkpoint | Check dishwasher function through a short cycle
checkpoint | Check gas valves & regulators flow direction
checkpoint | Check all gas burner functions and correct flame settings
checkpoint | Check balcony hose tap
checkpoint | Check balcony floor grate & downpipe
checkpoint | Check all fixtures & tapware are operating as specified
checkpoint | Confirm area has been left clean