## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | EFPQF08 - Fire Alarms Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | Detectors
tickbox | Strobes
tickbox | Speakers
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint | Confirm segregation from other electrical services
checkpoint | Confirm detector fit off locations
checkpoint | Confirm speaker fit off locations
checkpoint | Confirm strobe fit off locations
checkpoint | Confirm fire interfaces connected to sprinkler installation
checkpoint | Confirm fire interfaces connected to security
checkpoint | Confirm fire interfaces connected to mechanical
checkpoint | Confirm fire interfaces connected to BMS
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF09 - MASDS Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | MASDS units
tickbox | MASDS pipework
tickbox | MASDS Power supplies
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint | Confirm segregation from other electrical services
checkpoint | Confirm MASDS pipework installed as per drawing
checkpoint | Confirm MASDS sampling points size & spacing
checkpoint | Confirm MASDS unit fit off locations
checkpoint | Confirm MASDS power supply fit off locations
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF10 - FDCIE Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | FDCIE Panel
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
checkpoint | Confirm cable support/conduit fixings and spacings
checkpoint | Confirm segregation from other electrical services
checkpoint | Confirm FDCIE mounted in correct location
checkpoint | Loop cables terminated to correct output
checkpoint | Confirm OWS cables terminated to correct output.
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF11 - Fire Hydrant & Hosereel Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Pipework.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Isolation valves.
tickbox | Hydrant valves.
tickbox | Hosereels
section | Installation Rough In / Fit Off
checkpoint | Confirm hanger spacing.
label | 100mm - max 5m spacing.
label | ≥ 150mm - max 6m spacing.
checkpoint | Confirm support at change of direction at 1m max.
checkpoint | Confirm support of pipework no more than 1m from end.
checkpoint | Confirm support of horizontal branch from vertical riser no more than 300mm from riser
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Confirm hydrant height at handle between 750mm and 1200mm
checkpoint | Confirm minimum clearance around hydrant handle 100mm
checkpoint | Confirm hydrant valve outlet not inclined more than 35° from horizontal
checkpoint | Confirm outlet has 300mm clearance for a minimum 225 degrees
checkpoint | Confirm hosereel mounting height 1400- 2400mm to centre of barrel
checkpoint | Isolation valve height is 900 – 1100mm
checkpoint | Maintain 100mm clearance around barrel
checkpoint | Confirm hydrant cap and chain installed
checkpoint | Confirm installation pressure gauge installed at top of most remote hydrant
checkpoint | Confirm pipe identification labels installed
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF12 - Fire Tank Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Tank Panels.
tickbox | Roof Purlins.
tickbox | Roof Sheet.
tickbox | Access ladder.
tickbox | Vortex.
tickbox | Pipe nozzles.
section | Installation
checkpoint | Confirm tank slab tolerance within +/- 3mm
checkpoint | Build first panel ring
checkpoint | Build roof including access hatch
checkpoint | Hang tank liner
checkpoint | Fix tank jacks and lift for next panel install
checkpoint | Install ladder sections at each lift
checkpoint | Fix base ring and remove jacks
checkpoint | Ensure internal tank base free of debris
checkpoint | Install geo fabric to base
checkpoint | Stretch tank liner to tank base
checkpoint | Connect pipe nozzles and vortex
checkpoint | Confirm tank level indicator installed
checkpoint | Confirm tank capacity labels installed
checkpoint | Confirm warning labels installed
checkpoint | Confirm ladder guards and inspection hatches installed
checkpoint | Confirm no leaks when tank full
checkpoint | Copy of Installers statement attached
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF13 - Fire Booster Assembly Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire Boosters
tickbox | Suction Connections
tickbox | Feed Hydrants
tickbox | Isolation valves
section | Installation
checkpoint | Confirm height of booster outlets between 750mm and 1200mm above standing surface in front of booster
checkpoint | Confirm height of feed hydrant outlets between 750mm and 1200mm above standing surface in front of booster
checkpoint | Confirm height of large bore suction connection between 450mm and 600mm above standing surface in front of booster
checkpoint | Confirm height of small bore suction connection minimum of 400mm above large bore suction connection
checkpoint | Maintain minimum 450mm centre to centre clearance between outlets
checkpoint | Confirm front face of all connections within 150mm of the front of cabinet
checkpoint | Confirm caps and chains installed
checkpoint | Confirm isolation valves chained and locked
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF14 - Gas Suppression Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fabricated pipework.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Nozzles
tickbox | Cylinders
tickbox | Actuators
tickbox | Hoses
tickbox | Gauges
section | Installation Rough In / Fit Off
checkpoint | Confirm maximum hanger spacing.
label | 25mm - max 4m spacing.
label | 32 – 100mm - max 5m spacing.
label | ≥ 150mm - max 6m spacing.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm support at change of direction at 1m max.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm support of pipework no more than 1m from end.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm support of armpiece exceeding 500mm.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm first support of range pipe within 2m of mains.
label | Acceptance Criteria - AS:2414
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Cap installation and perform pressure test
label | Acceptance Criteria - AS:2414
checkpoint | Confirm discharge nozzles installed.
checkpoint | Confirm gas cylinder mounting as per manufacturer instruction
checkpoint | Confirm cylinder hoses fitted to discharge manifolds
checkpoint | Confirm cylinder pressure gauges fitted and indicating correctly
checkpoint | Confirm discharge actuators fitted
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
section | Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), PNEUMATIC TEST – 300kpa 10 MINS - PERMITTED LOSS 20% (60kpa)
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist | EFPQF15 - Water Mist Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Pipe.
tickbox | Fittings.
tickbox | Hangers.
tickbox | Nozzles
tickbox | Valves
section | Installation Rough In / Fit Off
checkpoint | Confirm maximum hanger spacing.
label | ≤25mm - max 4m spacing.
label | 32 – 100mm - max 5m spacing.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm support at change of direction at 1m max.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm support of pipework no more than 1m from end.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm support of armpiece exceeding 500mm.
label | Acceptance Criteria - AS:4587
checkpoint | Confirm pipework installed as per drawing.
checkpoint | Confirm isolation and test valves installed
checkpoint | Cap installation and perform pressure test
label | Acceptance Criteria - AS:4587
checkpoint | Confirm discharge nozzles installed.
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
section | Pressure Test Report Sheet
checkpoint | Test Details & Results
text | Test number
dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), HYDRAULIC TEST - 3300kpa 2 HOURS - NO LOSS
text | Start Date
text | Start Time
text | Start Pressure
text | Finish Time
text | Finish Pressure
text | Gauge Reference
checkpoint | Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | Entire Fire Sign-Off (attach signature)
checklist | EFPQF16 - Fire Extinguisher & Blanket Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire Extinguisher.
tickbox | Fire Blanket.
tickbox | Signage.
section | Installation
checkpoint | Confirm top of extinguisher handle ≤1200mm above floor level
label | Acceptance Criteria - AS:2444
checkpoint | Confirm extinguisher type signage located just above handle
label | Acceptance Criteria - AS:4587
checkpoint | Confirm extinguisher location signage located at ≥2000mm above floor level
label | Acceptance Criteria - AS:4587
checkpoint | Confirm fire blanket located in a readily accessible location
label | Acceptance Criteria - AS:4587
checkpoint | Confirm fire blanket signage provided adjacent to the fire blanket
label | Acceptance Criteria - AS:4587
checkpoint | Confirm fire blanket location signage located at ≥2000mm above floor level
label | Acceptance Criteria - AS:4587
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF20 - Calibration Record (x5)
section | Details
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist | EFPQF18 - Fire Penetrations (x 10)
section | Details
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checkpoint | Fire Penetration details
text | Location
text | Diameter
text | Wall/Slab Thickness
checkpoint | Sleeve installed satisfactorily
text | Date
checklist | EFPQF19 - Occupant Warning System Install
section | Documentation
checkpoint | Confirm construction drawings approved for use.
section | Incoming Inspection
checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
tickbox | Fire rated cable
tickbox | TPS cable
tickbox | OWS Panel
tickbox | Speakers
tickbox | Strobes
tickbox | VAD
section | Installation Rough In / Fit Off
checkpoint | Confirm correct cable type run
label | Acceptance Criteria - AS:1670
checkpoint | Confirm cable support/conduit fixings and spacings
label | Acceptance Criteria - AS:3000
checkpoint | Confirm segregation from other electrical services
label | Acceptance Criteria - AS:1670
checkpoint | Confirm OWS mounted in correct location
checkpoint | Loop cables terminated to correct output
checkpoint | Confirm FDCIE cables terminated to correct output.
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
checklist | EFPQF21 - Action Request
checkpoint | Action Request Details - Pass once entered
text | Action Request Number
label | This action request is a result of (Tick below)
bool | Audit
bool | Failure
bool | Non-Conformance
bool | Process Improvement Idea
bool | Customer Complaint
bool | Corrective/Preventative Action
checkpoint | Description of failure/Non Conformance/Improvement Idea/Customer Complaint
label | Send to Quality Manager for allocation of number and passing to appropriate person for action
text | Details
text | Reported By
text | Date
checkpoint | Investigate cause and list details
label | State action when and if there is a deeper underlying issue or problem
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | List details of deeper underlying issue and corrective action
label | This section only applicable if above indicates the need
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | Verification/Follow-up
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Quality Manager Signature Sign-Off added below | Yes, No
checklist | EFPQF22 - Register of Non-Conformance Reports x10
section | Details
checkpoint | Item 1. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 2. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 3. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 4. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 5. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 6. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 7. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 8. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 9. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Item 10. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes, No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes, No
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist | EFPQF17 - Fire Electrical Commissioning Test Report
section | Pre-Start
checkpoint-no-status | Pre-Start:
text | drawing reference
text | level and area
section | Installation
checkpoint | Secure cabinet
label | Specification Ref: drawing
checkpoint | Extinguishers installed
label | Specification Ref: drawing & AS:2444
checkpoint | Signage to meet code compliance
label | Specification Ref: drawing & AS:2941
checkpoint | Hangers location and spacing
label | Specification Ref: drawing & AS:2941
checkpoint | Fire blankets
label | Specification Ref: AS:2444
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes, No
checklist | EFPQF27 - EWIS Commissioning
section | Details
checkpoint | Download, fill in and upload completed EWIS Commissioning sheet
checklist | EFPQF28 - Fire Matrix
section | Details
checkpoint | Download, fill in and upload completed EWIS Commissioning sheet