## Master List Templates
Id | Type | Name | Values | Prompting Name
719339c2-b674-4139-a24b-dce3581e7913 | checklist | Add Stainless Steel Drainage valve rebuild Checklist |  | Stainless Steel Drainage valve rebuild
10103ae7-a929-46b0-ab3e-da6d7941243d | section | Details
e12fc8ba-94cf-4634-9656-c2f7fb89ae28 | checkpoint | Photo of any pre existing damage to valve or penetration seal
e152c49b-7656-5860-9f81-f0357ee9f632 | textbox | Valve No.
2c7c9829-57d9-41fb-87b5-ffa0197a806c | checkpoint | Photo of valve before
0dcf6e5b-2e30-45f5-933f-17283733875d | checkpoint | Photo of old valve seals
2441ea2f-9c3e-4d9e-8bf3-20f64a774b4b | checkpoint | Photo of inside of the valve
3a220e98-e8a3-4242-81d0-963bbb0baa99 | checkpoint | Photo of new seals installed
e3fa560b-da13-4850-9f07-77751259f360 | checkpoint | Tightend to correct torque list newton meters
6e617f22-f32f-5fb4-b297-f4fe6cbf009b | tickbox | All Bolts Tightend in a cross pattern
f0a5caec-eac5-5cb6-afc3-80bf17f280d0 | number | Newton Meters
c1b21c1f-0d88-424d-a5c8-d3d58ee48d16 | checkpoint-no-value | Installing Plumber
a0b79cff-946a-5f60-8569-18693e782c47 | button | Plumber: | Richard Bell, Brendan Head, Guy Mcelholum

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
fac5bbcd-23d6-40f5-87e0-64d7fceeb321 | checklist | Backflow Prevention Device Test Report |  | Backflow Prevention Device Test Report
475b4b43-3e41-4432-91e8-0e9775159e92 | checkpoint | Backflow Prevention Device Test Report Details:
67c3afb3-931c-5e0e-bd65-c498964057bf | textbox | Owner/Occupier:
e10cabe7-10e2-5d72-8a39-38678dd7a078 | textbox | Address:
75fce7ab-ff53-5451-938e-a85cb0143e81 | note | Licence: 50043
3554b583-7728-507b-998f-7b550e6ec7ca | button | Type of Test: | Annual Test, Installation Test
3e3086cb-54c9-511a-b988-57832185db91 | textbox | Location of Device:
d78be035-10f9-5382-b2b3-8ef7d6a5dc09 | textbox | Authorized Tester Name:
f55eac32-f7c4-57f9-89d3-d1fd6d241e29 | textbox | Test Kit Serial No.
83f6b9dd-de3a-5566-8051-6035393a2344 | textbox | Tester Licence No.:
23ac6744-a0c3-5419-9468-fa905631830e | textbox | Test Kit Calibration Date:
0b2a78f6-417b-5d7c-8851-ab1a4e380194 | textbox | Date of Test:
55c70ba6-e32b-486d-a53d-100722bf2a44 | checkpoint | Device Details and Test Results
d9e325e0-ddfd-50b0-b1e5-194baf22ecbb | button | Permission to Isolate Water Supply | No,Yes
3b4ab525-8203-57e0-a886-404a4d7e25b3 | note | Device:
c59e56be-9e0a-547e-bf37-a497c49aac3d | textbox | Make:
523f2b48-d7ee-5591-acf0-e5e466fd4c7d | textbox | Size:
f43e0f47-eb7e-5985-83c2-23ec54458d93 | textbox | Model No.:
c84a94a4-0fcb-5ccb-8e03-9626dba1f940 | textbox | Serial No.:
a28175f2-9011-594c-a091-24fd5451d869 | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
4e52035b-5e76-5505-8343-cee86d2751c5 | tickbox | Containment Protection
188d4917-1bba-5ff6-9eb5-2011c4b1baaf | tickbox | Individual Protection
007672d4-d032-55a0-8974-ae69fca47b83 | tickbox | Zone Protection
a3bf82ea-1395-5dd5-bcc6-1c81b0ef0e38 | button | Strainer Installed | No,Yes
76913e2d-db50-5e70-b128-0cb133615ecb | button | Strainer Cleaned | No,Yes
01b6ff83-d898-5a77-889c-f467fc75a681 | button | Device Type | Double Check Valve, RPZD (Reduced Pressure Zone Device)
3540eb3a-76fb-5c79-9486-5bc770e7c4c3 | note | Valve
15ae4cf5-5dd6-5e83-b552-fd385b6e9858 | textbox | Check Valve 1
1f03bb24-1246-50e3-b875-31ae15611c87 | textbox | Check Valve 2
6ece9994-1e48-5cd7-86ef-364d5f75dece | textbox | Relief Valve
616dc30d-79b1-5d9b-8f97-8f59e00a8c72 | note | Testing Results
f86ba0fe-a9cc-528a-8f78-c9d6757a4305 | textbox | Close tight at:
30111eed-1aee-5f27-94af-ef7ecd13ba36 | tickbox | Leaked
96e381b1-a14c-5595-be31-a2691fa74983 | textbox | Close tight at:
5f13e29c-3c0d-50cb-a776-9b271d1ccaa3 | tickbox | Leaked
8715d7cd-cbac-54ea-9df2-7cd22ddf0f46 | textbox | Opened at:
9d42c137-ae2c-50ef-acbf-52bd53107fd9 | tickbox | Leaked
5b33c1a7-36ec-5a9f-a9a1-ebc046993b31 | note | Reason for the device failure
35fc6280-fd5b-5e45-a4ec-36f1e62b4e7c | tickbox | Incorrect position
1f274407-3082-5a1a-b602-2dc2851ea5b0 | tickbox | Incorrect installation
050bd856-aa47-5ef3-8815-8adab241ebdd | tickbox | Foreign material in the device
b84e7cf8-e959-57fa-b063-25996c3ba6b9 | tickbox | Spring wear damage
4aababab-5bab-5830-8e98-fc5e1b69ad98 | tickbox | Seal or Rubber Damage
996a26d9-b307-59b6-a4df-cf5ee267c182 | tickbox | Other
7a53139e-1241-50b9-9972-35b87f296d98 | textbox | Other:
442a17d3-5471-538d-b679-4fceace5f395 | note | Test after maintenance
5c7f4f17-1b0f-57eb-a214-512c1a4dba83 | textbox | Close tight at:
ee4235a6-2f77-5c42-950f-0b360231230e | tickbox | Leaked
e03b852e-19ea-55d7-8869-3145fa7b6301 | textbox | Close tight at:
ccddefa3-0392-5960-a925-85357c3824e3 | tickbox | Leaked
9721fd2e-e544-5112-b89e-0ef553c0d55f | textbox | Opened at:
ba5db936-1b6a-5b23-aaae-c15e99f5b331 | tickbox | Leaked
e456f074-c9ec-5436-9769-0aeb1543c04d | button | Water turned back on | Yes, No
87a069cc-f760-57e7-86c8-16d68e64cc95 | textbox | Describe the maintenance:
3c3eafc8-fd63-5c3b-83a2-09858641323b | textbox | Parts used in repair:
96cea6fe-56b9-5fd9-88d4-9815789fb0eb | button | Is the device installed correctly | Yes, No
218824d0-9a29-4623-b9ad-0e6219204efb | checkpoint | Test Result
a5b173f3-58f8-5bc9-a3d3-9d99e2945fde | textbox | Tester Name:
2d335df4-e6bb-524b-b807-1dc2a154c2b7 | textbox | Date:
964df302-8774-4b27-9480-67ecc8904f5e | signoff | Add Signature
c72f7cf7-1e98-496e-976f-444a4c046878 | checklist | Backflow Test Report |  | Backflow Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1f8eb692-01f5-43f1-bd46-975d4f358f01 | checkpoint | Description of property or vehicle
019d45ab-b677-51b7-91b4-d4e9a9276042 | note | The description must identify all land or vehicles covered in the application
05fb37d9-f189-5cb1-8c11-16c6f341f9c1 | textbox | Street address (number, street, suburb and postcode)
70968609-5c01-5696-8827-eec935a277b0 | textbox | Water authority property service / installation number
e340f986-cc67-5d88-ad1e-06ee0f9d905a | textbox | Water meter number
53dfc430-cf23-439b-9d55-e872d1471e2c | checkpoint | Type of test
f6a5f430-1454-5b21-a407-c8af61e781f2 | tickbox | Commissioning of new device
764a7b70-e543-5390-87eb-b3df0680d0ce | tickbox | Replacement
0e42f7fb-0da9-59e4-9317-c8d56ac50c52 | tickbox | Annual
4dd7d6ff-8f3d-5012-9054-4aadde3bb19c | tickbox | Repairs
e1bf969f-4897-5595-97d1-939c1180e944 | tickbox | Decommission
7ec6a4ea-919a-4491-96ea-0215eee99e1a | checkpoint | Backflow prevention device location
07e9dd2f-de44-52ee-9c1d-da2aef525318 | textbox | Location of device (eg: Northwest side of building @ FHR external)
c3b12d56-9daa-5b31-a39c-643a11826b06 | textbox | Mains pressure (kPa)
4f14040e-ae53-5b6c-8ed5-f8cb2d40dce8 | textbox | Time and date of test
d07d5ead-b725-4795-ad72-28e9bc545ff4 | checkpoint | Main device
4ae4671c-0bd6-5b4c-9b99-04a34110f254 | tickbox | RPZD (E)
e611ba2b-c8ca-506f-bf92-4aef7f0b008a | tickbox | DCV (F)
d30b0188-0839-57ba-b979-c132d10a295c | tickbox | SCVT (I)
429c8c23-8363-5067-8438-a45482891b49 | tickbox | Containment
0247c696-4b07-5e94-8fb1-d0440d01a6c1 | tickbox | Zone
61100d71-d9ce-5ee5-9e93-2a7b5226fae4 | tickbox | Individual
c5dc5891-ebf5-5ce9-8d7f-cd7214be1ec2 | textbox | Make
ae4aa02f-562f-56b3-a98e-58c991f2763f | textbox | Size mm
53ec8350-e671-54aa-8564-122e3dae2110 | textbox | Model
a2cc860c-7069-5c10-8d35-bb5a0fd59cbf | textbox | Serial number
1d0cc1f5-4961-5b07-8414-cee130414192 | button | Cleaned strainer | Yes,No,N/A
31194ecc-f4f7-5bc3-9ead-46696acf71d8 | button | Upstream IV | Leaked,Tight
4cb27f69-20a1-5018-9ee6-720b86e882e2 | button | Downstream IV | Leaked,Tight
9d240fca-b85f-514e-93ce-ee06ced5408b | textbox | Check valve #1 (kPa)
51c0d8c3-a23b-5220-8337-a9bee0ea38a1 | textbox | Check valve #2 (kPa)
83e2f946-5af2-5d4d-9567-f7594e720f17 | textbox | Relief valve opened
ff51ad31-4fd1-4e5f-b502-7fc06140a047 | checkpoint | Device installation notes
52e82b40-efe2-560f-8524-248bdc4aa234 | button | Isolating padlocks installed | Yes,No
b98beafe-ffe9-50b9-9f0c-fc319b1dcedf | button | Installation complies with AS/NZS 3500.1 | Yes,No
0ecc6993-fa60-4664-b2ee-57e754ba452f | checkpoint | Test kit
bdf68632-a368-5bc9-8f71-61d127fe480c | textbox | Test kit serial number
a1204746-ddcd-50ad-b1b4-83830213c6e3 | date | Date last calibrated
fe094434-9f58-4a84-9d8a-1c8777c14681 | checkpoint | Authorised testers details
bb51a5cc-b4cc-508a-841b-192fe32b3f2a | textbox | Testers name
a5dd5277-1a50-546d-9d9d-ca2b1c91d661 | textbox | Registration licence number
756b6c8b-828d-5b85-b9f2-3cc0689782c5 | textbox | Phone number
c4645a85-1aae-403a-b42d-f41ad2bea7ee | checkpoint-no-value | Licence person
70b09178-5e16-59ca-a228-95f2dd058ba2 | note | Full company name - Geschke plumbing
9246a2cb-330d-5cb2-b302-03bb08f51146 | note | Licensed tester name – David Geschke
49350d3f-20a0-5e95-8b4a-84e789e6880c | note | Licence number -50043
2bef8b60-1986-46ff-8cfb-2b923172531d | checkpoint | I hereby state that the information provided in this form is a true and accurate record. I have tested the above device/s in accordance with AS/NZS 2845.3:2020
3bf66611-f372-52ad-851f-e46f7babb37c | note | Note: Failed devices must be repaired and retested within 20 business days as per the Water (Estimation, Supply and Sewerage) Regulation 2014.
62e1bc02-52d9-53c1-b444-8929823ea17f | textbox | Signature licenced plumber
65a0580f-f25a-55c9-9551-b0712fb76508 | date | Date
45dbf71e-8d7c-5d62-8cad-cbced6932807 | textbox | Signature tester
c8e090f6-eff8-5b63-b306-126cf00a8358 | date | Date
59255111-cbfe-4d98-aae8-1f39bd4d1f16 | checklist | Below Ground Pipework Checklist - Fire |  | Below Ground Pipework Checklist - Fire
bca80394-247a-4681-b60e-c0457fed5adf | checkpoint | Principal Contractor Permits Issued
02186070-864a-41e0-94e6-cebbafa24317 | checkpoint | Set out pits depths and trench runs.
5c4af112-67e2-57b4-998a-4434d9f42684 | note | As per DRG#
2869982c-8a1a-4c28-a585-0d05f10c0c80 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
ddc7ad3d-b217-58f2-ac31-62a2e35b0d18 | note | Spec#: AS3500
8ec5533d-b5f4-5dcb-85f4-bcc6296ddf5d | note | MDPE SDR11 PE100 PN16
f5626df6-67af-48cb-becc-8a1290fe67d1 | checkpoint | Bedding placement and compaction and material meets specification.
21578712-1eca-52f1-8123-c53396911f4b | note | Spec#: AS3500
ad42db2b-cec8-5294-880d-da532e3c4536 | note | Packing sand encased pipe
2898a701-f576-4ad2-b5c3-a3b12afed08a | checkpoint | Jointing of pipes
ad33460c-fb19-52a5-abf6-324d360f74c2 | note | Electrofusion and/or Butt Welds
c795a52b-f088-5c91-bb9d-63e9711b7d70 | note | GPLQA16 form
b67a265d-2166-4872-996f-c99fcfe3d718 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
2072a0e3-9117-43a2-b60f-a0510ed21d45 | checkpoint | Hydrostatic tests are carried out as required.
b1ca60e1-a783-56c4-921f-d43161dfa869 | note | GPL QA6 form completed
14bb6e1b-df5c-57b5-946b-3adf84a563db | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
b559e032-c108-4d8d-97ee-575e66e608da | checkpoint | Placement and compaction of backfill and material meets spec.
0449cfa3-9b8a-5822-90a0-6abe542c3d24 | note | Compacted crushed rock backfill 80% to 100% compaction
0a36c2db-0b43-54de-936b-36c3169989ae | note | Detectable marker tape
22ef808d-861d-4c46-9d8f-a247ad77baf5 | checkpoint | Temporary cover provided to open drain.
09ebbdde-bc60-4f77-8502-3f09a6d5571c | checkpoint | PVC/ Plastic caps to open ends
bd70d805-7ee0-4963-8f30-0cdb20e3da76 | checkpoint | As built information updated onto drawings
0bb7855c-92ab-5f52-8d5c-8890fb49b6bc | note | Ongoing
b8d6f3f4-2274-56d7-a8cf-ee9c8cb4bb1c | note | To be provided
08e37a33-bc35-4afd-a173-93cdca39f88c | checklist | Below Ground Pipework Checklist - Sewer |  | Below Ground Pipework Checklist - Sewer
899070a5-ba34-49ef-b5d9-f61046dde234 | checkpoint | Principal Contractor Permits Issued
b881cd2b-1210-4802-aab7-24c500c48395 | checkpoint | Set out pits depths and trench runs.
91561acf-49fa-5fd0-9c95-54d1c28a4716 | note | As per DRG#
a33d60b2-6fcd-4110-8afd-1552e67565ce | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
3fc5c27d-1c4d-5e72-ac7e-216cedcb0dde | note | Spec#: AS3500
c0bf8c2d-06be-54bd-95bb-88e6124320aa | note | UPVC BEP Type ISO 14001
1f077186-02e4-4d9a-a50d-98ce81a99e2e | checkpoint | Bedding placement and compaction and material meets specification.
2ad61a53-6fe1-5488-9fb1-2ab538e5f4ee | note | Spec#: AS3500
56f25092-1e87-5bdd-9a8f-0626bfd212ed | note | 75mm Q-Minus Bedding and Encasement to top of pipe
27659075-128e-4ab9-a98a-6a28a8a94ec0 | checkpoint | Laying and jointing of pipes R.Ls and falls
f2b77963-f8fc-5260-ae0c-02424cfd84d7 | note | PVC solvent welded
9f6ec143-6e56-50b9-a530-62c42a39001e | note | 1:60 fall
6402b1bb-a213-5472-bf8a-eb5301ee10c6 | note | AS3500
5941e7c8-ab35-5b4d-8970-d5bfd0ac75a6 | note | RLs as per hyd drgs
d12ea49e-2efa-4651-9e0f-8f1a5e747911 | checkpoint | Connections to pits and existing services
4d8c6a5b-51c7-4948-aa17-ac0943579e33 | checkpoint | Hydrostatic tests are carried out as required.
7c58d2f7-6d91-59a9-a492-1d9a19837681 | button | Air or Water? | Water,Air
da15e025-fd79-5183-9501-042f08f680ce | note | Inspected and recorded by Independent Certifier or PIC
80e71bb2-3b50-49f9-a0b4-271495e523c4 | checkpoint | Mirror tests are completed if required.
400d1f2b-3086-46d7-89c3-8e3b0fdc0dae | checkpoint | Placement and compaction of backfill and material meets spec.
d6266966-c41d-5191-ae35-985283b5ca19 | note | Compacted crushed rock backfill 80% to 100% compaction
bec85ff0-47cc-4f52-9f95-322b6d1f6f67 | checkpoint | Temporary cover provided to open drain.
ea487844-bdf3-43c3-a78b-ec162f2a6197 | checkpoint | PVC/ Plastic caps to open ends
309bef6d-a3f5-4e69-b8b7-3316746e52e7 | checkpoint | As built information updated onto drawings
ec2215e0-8960-584e-887d-688de75ef519 | note | Ongoing
439a0717-f8a6-5d3d-bf0b-921130728592 | note | To be provided
49e9101b-fc6f-4532-9590-586a5524de2b | checklist | Below Ground Pipework Checklist - Water |  | Below Ground Pipework Checklist - Water
53de5773-5003-4397-baac-16879c321041 | checkpoint | Principal Contractor Permits Issued
d4e130f5-da09-428b-ab2d-08ff874d3871 | checkpoint | Set out pits depths and trench runs.
feb8be58-90ee-5496-ad49-e993a4661c78 | note | As per DRG#
cf9119ff-3a72-4916-a323-6b7b5e594b2c | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
ef65f9e3-8735-5cb8-8aa4-16027f07314f | note | Spec#: AS3500
248e2cde-0971-5f4f-b94d-804bcf68c81e | note | MDPE SDR11 PE100 PN16
9c4961fd-fccb-4259-a848-1a2d52dc0485 | checkpoint | Bedding placement and compaction and material meets specification.
4c6dd7ea-9b9f-5f36-a365-0068534f8add | note | Spec#: AS3500
a60ecdc7-cb1a-5ef6-8865-df0b383bb496 | note | Packing sand encased pipe
6f1256ec-714b-4d6e-9bee-e13c452fc3f7 | checkpoint | Jointing of pipes
ee11ccfa-08f9-581b-bc04-5879383baa4e | note | Electrofusion and/or Butt Welds
347246b7-1e59-572a-88f7-1d3458b0296a | note | GPLQA16 form
841f15ae-74c1-459f-8702-b800e28c9b6d | checkpoint | Connections to pits and existing services as per spec and Australian Standards
47c8a9ee-55ba-42e0-880c-26a6e65fb8f3 | checkpoint | Hydrostatic tests are carried out as required.
4baed8c3-6432-56f0-bdcf-512847aaf760 | note | GPL QA6 form completed
048141c6-2f56-5862-ba75-67bf588a7a67 | note | Water system tested to 1400 kpa regularly prior to finished surfaces are completed.
96588801-eee6-4513-acda-b824c38ba561 | checkpoint | Placement and compaction of backfill and material meets spec.
d9200c05-48a6-54a1-9195-ea4a372c4578 | note | Compacted crushed rock backfill 80% to 100% compaction
b1e91d01-7000-5788-9343-e39dd5bd2dbf | note | Detectable marker tape
f0145108-878e-4ead-95e3-ff5115053099 | checkpoint | Temporary cover provided to open drain.
8fbf119b-219b-4807-93e3-0795af03f592 | checkpoint | PVC/ Plastic caps to open ends
46ccef07-be91-431d-a8c7-a60caebc5c4b | checkpoint | As built information updated onto drawings
78198980-0b31-5a4b-8155-bf1fd28143a8 | note | Ongoing
c291e868-54c1-513c-8519-cf735bbe6cf0 | note | To be provided
48b7a968-2f03-4daf-bb94-eaad9513baec | checklist | Boiling Water Service Maintenance Log |  | Boiling Water Service Maintenance Log
c173d80f-c1db-4ab9-ae35-59c8e6a6c74c | checkpoint | Boiling Water Unit Service Details
63d2dd07-f5e0-54b9-aef1-2ea0ebc6f195 | textbox | Purchased from:
a0b5248d-0729-51fc-aac4-5f15c751f7e3 | textbox | Make:
f149b42a-cce3-52a7-83b4-bfa5ffc55dac | textbox | Model No.:
7509c231-069f-53df-b64e-ebea062e5927 | textbox | Location:
bb6dbc3a-c040-5437-85fc-e1cf02ce4ec5 | textbox | Room Designation:
827155d2-329c-5c3a-989e-2b9567cd336c | textbox | Installed by:
002ef4e2-7e33-5eb0-b806-938cee9985ff | textbox | Installation Date:
477f053e-105f-496c-8953-2f1289697ffd | checkpoint | Does installation comply with manufacturers instructions
2ec087b0-83bc-40d4-b212-4b2ec960c47c | checkpoint | Does the installation appear in good working order.
dc7c98af-5cd8-495c-88a3-e4177beaf2b8 | checkpoint | Confirm all warning lights working correctly
3b6429f0-10fb-43b9-a919-f57eee7866d8 | checkpoint | Confirm filter is clean
05346d47-1b7f-46ee-8ded-4cc6c23ed04c | checkpoint | Confirm Unit is Fully Operational
bff349db-52df-4a1b-923d-9f0e7b800e0c | checkpoint | Commissioned By:
2dc27619-80bb-5d05-976c-ea41778e4388 | textbox | Name:
ebec8939-0c96-5398-b0ea-636487d0b4e3 | textbox | Date:
11118849-518d-4a76-a4a9-6b35b1464a00 | checklist | Butt Welding |  | Butt Welding
adeff316-d628-498d-9c5c-8b9cdf455ad4 | checkpoint | Operator Details:
90d408bd-24da-584c-a175-d621cfc1e911 | textbox | Name:
88115cdb-b205-5cce-8cf6-5cf24f64a597 | textbox | Company:
e093bd19-71a1-5872-8479-50ec2930ae22 | textbox | Phone:
ce8aa678-43c0-5fa0-881e-3c45ffce98d7 | textbox | Address:
c1b168f9-d343-4e67-b6d1-9afc7a64d392 | checkpoint | Welding Machine Details:
b1f8b8f6-a317-5868-a44a-472169fd5eb2 | textbox | Manufacturer:
73ccf4cd-de47-5cbe-9a03-6eebce347f02 | textbox | Type/Model:
4162f926-d4c1-5e0d-8ea3-4a61429fa697 | textbox | Serial Number:
8732e8d2-281f-5f3f-a638-3f184c62d584 | textbox | Year Built:
1e9f1207-0e9a-4df4-92bc-37e6869cec60 | checkpoint | Pipe / Material Details:
fe3a971b-c48d-5e56-8e75-f75fa22244a5 | textbox | Dn (OD)
73d7683f-1913-538a-8194-137be7637d5f | textbox | SDR
f607540b-9c42-571f-ac65-fc2b7e2ec3b4 | textbox | En
bce15aba-8f6f-55f4-beb7-0798fab5ea9d | textbox | Type
272e7a77-f84c-56b0-9742-6c3be5fd6fe8 | textbox | Parameter
21848681-1402-54be-a4ab-1f9f2f7cd8f1 | textbox | SLP
b85115cf-9ce0-5107-a34e-b9f3b026d413 | textbox | SHP
48533a52-1e0f-4990-84dd-b8a441ddde48 | checkpoint | 1
39355005-86b7-5893-8b61-da10093bae7f | textbox | Time
7a38a777-9ca6-5d8d-96f4-c06c4b5c9e8a | textbox | Ambient °C
90ae1838-4317-5454-89bd-91eec5be54d6 | textbox | Heater Plate °C
7d642243-5a2a-59a0-9c5d-b6d8787d6abe | textbox | Drag Pressure
8322afd8-f9b6-51e5-8f1c-db07b6fdd5fc | textbox | Bead Up: P1 (Kpa/Bar)
6f4cbfb8-b1c7-5f7f-a041-74bb1b4572ea | textbox | Bead Up: t1 (Evidence)
be4efd0e-fe5e-5e5f-a78b-8b691b0aa316 | textbox | Heat Soak: P2 (Kpa/Bar)
56c3bd4b-59aa-5a10-895e-af4ceb08d6f5 | textbox | Heat Soak: t2 (Seconds)
8127f338-129b-5d86-9dfd-fc58164c7da9 | textbox | Change Over: t3 (Seconds)
4ef33e89-2e4c-5e0e-84d7-14e1c61fd93d | textbox | Pressure Up: t4* (Seconds)
9356d649-d2b9-5a03-bb6d-bae36094957d | note | *t4 not applicable for SHP situations
486d9da7-132c-582f-8fc8-7234e39b13b1 | textbox | Weld and Cool: P3 (Kpa/Bar)
95cbf398-f4ce-5a62-bc1e-9d7651b03e57 | textbox | Weld and Cool: t5 (h:m)
cbfc9453-fe1f-54e7-ab02-a73fd11d97b7 | textbox | Rough Handling: t6 (h:m)
10deaacd-c617-5752-90cc-97e9b4cb7901 | textbox | Bead Size: Min
cd4be2ac-b3a5-5255-8fdc-d39c4618409d | textbox | Bead Size: Max
208c8c38-90da-546e-9d7f-aeb625566ede | textbox | Comments
02d27c59-e831-41f5-a99b-60b76d77ca83 | signoff | Add Operator Signature
108584f5-4769-4b85-8c73-3df89f5440c3 | checkpoint | 2
014c830e-f23f-5164-8e94-cc88502c00e2 | textbox | Time
76f408c1-3d3f-55e4-8815-6ed5254c2445 | textbox | Ambient °C
4c18d993-b016-52dd-91a0-74030683ad82 | textbox | Heater Plate °C
7d55e0bd-d71d-56e7-baa1-1c932db753fe | textbox | Drag Pressure
a1195b9b-b12a-51fb-ba2a-f85c86ec8053 | textbox | Bead Up: P1 (Kpa/Bar)
ca55de63-85d5-59ce-8c8b-dc17c53ebf4c | textbox | Bead Up: t1 (Evidence)
b6b47590-0858-509a-abbd-5b32ed8e285f | textbox | Heat Soak: P2 (Kpa/Bar)
ac1781b9-09ed-5873-9b56-97504e167995 | textbox | Heat Soak: t2 (Seconds)
f0ef4151-d830-5533-bc6d-f12e23034f91 | textbox | Change Over: t3 (Seconds)
da563f3e-87ad-50ed-8df2-85867ea3e314 | textbox | Pressure Up: t4* (Seconds)
92c998fe-57f0-58f0-848e-5ca82f4040d7 | note | *t4 not applicable for SHP situations
45483d02-4757-587a-8139-a233be4c676d | textbox | Weld and Cool: P3 (Kpa/Bar)
59f1de70-2e23-59af-a5ed-fcf2ee56f163 | textbox | Weld and Cool: t5 (h:m)
6bba6d8d-65e6-5bd1-819a-c7c77bdfd1ed | textbox | Rough Handling: t6 (h:m)
22fd1e3f-d42d-53c6-b9b0-379191b96645 | textbox | Bead Size: Min
74fade41-df8e-550b-930e-e3c07d75a5f4 | textbox | Bead Size: Max
8e6dead3-6f6e-5867-9dbf-7db4a17cb556 | textbox | Comments
ba0433f4-b19f-4766-b85e-e8b72a5c3f59 | signoff | Add Operator Signature
d7ce9ec4-34ca-4861-8fdf-aa8ee31a558a | checkpoint | 3
39bf307a-4b39-5876-b690-e247787ebe13 | textbox | Time
944b9377-d38e-582b-a11d-5801f56e144a | textbox | Ambient °C
10979b0f-c2b8-5ce7-8207-ba743364e6f7 | textbox | Heater Plate °C
1c17cd8d-ae98-5897-8d59-03b28c65e2e5 | textbox | Drag Pressure
fd0420f1-9c77-545d-bfc8-2ee58f5a61d4 | textbox | Bead Up: P1 (Kpa/Bar)
6cd73049-295a-5d05-8aa1-9afd3221660e | textbox | Bead Up: t1 (Evidence)
9a3eee27-b08b-5fdf-9b0a-03ca020c77c0 | textbox | Heat Soak: P2 (Kpa/Bar)
545c97ab-96d8-522f-8aa5-a6482ba87842 | textbox | Heat Soak: t2 (Seconds)
78ec2bb5-6279-5936-8b15-dbf284923460 | textbox | Change Over: t3 (Seconds)
77280739-7786-5017-98dd-c8b915ca49fa | textbox | Pressure Up: t4* (Seconds)
ee154f7f-a132-5a96-9667-8c3c53de8374 | note | *t4 not applicable for SHP situations
ce89791c-d4a9-5440-8f63-efb2b58afd49 | textbox | Weld and Cool: P3 (Kpa/Bar)
a73a8aea-aeb1-563e-9240-ae6413ad76e9 | textbox | Weld and Cool: t5 (h:m)
a969ba6b-8c58-50be-a1c5-6fc1cae2ec0a | textbox | Rough Handling: t6 (h:m)
247f0c58-f005-5ddc-81b6-f60f64086d95 | textbox | Bead Size: Min
187f54f4-58e0-56b7-b31d-6822a2f90f20 | textbox | Bead Size: Max
20454e1f-65d9-534b-b642-9034e3fd3321 | textbox | Comments
a052efb9-007c-45f5-9ab1-4431a313587c | signoff | Add Operator Signature
cf96a7e6-dff4-4c70-8a64-b990f116e87a | checkpoint | 4
dd56c0e9-e2a2-567e-a585-bdfb4a8f62fa | textbox | Time
441d839a-d5da-5af5-88b3-dd4351589d19 | textbox | Ambient °C
d9a6cdf0-9f6a-5545-a095-faa0afe33bbd | textbox | Heater Plate °C
b234e4cb-fd83-547e-b384-0ca50962aee0 | textbox | Drag Pressure
4db80497-a147-5017-9d4d-147ce0a64483 | textbox | Bead Up: P1 (Kpa/Bar)
99d137f1-6310-5426-950e-6d70e3d5c67b | textbox | Bead Up: t1 (Evidence)
ec3a5fcf-3035-5bbc-abff-ea8e604df151 | textbox | Heat Soak: P2 (Kpa/Bar)
74201814-8908-51ad-bb2e-a5016f87f9a5 | textbox | Heat Soak: t2 (Seconds)
01cd982a-8e5e-5a38-af31-c336c88813a3 | textbox | Change Over: t3 (Seconds)
c5399d1d-e3fb-5459-9d2e-e192d2e5fc74 | textbox | Pressure Up: t4* (Seconds)
284c46d1-3f2a-5241-ac10-f034bfad6f1d | note | *t4 not applicable for SHP situations
b15fcbd3-9b38-5f58-95f4-1a01d31c91eb | textbox | Weld and Cool: P3 (Kpa/Bar)
81035859-2cc4-5b0f-a0e3-4eeb6fce45df | textbox | Weld and Cool: t5 (h:m)
4283ef3a-daa7-58d6-9a54-b2dd87eddef5 | textbox | Rough Handling: t6 (h:m)
771be64f-8f66-57f0-9e3e-1d53da9b1a8d | textbox | Bead Size: Min
7e9e07e1-9521-507e-b610-16c23063bc91 | textbox | Bead Size: Max
2740f299-9a74-5918-bd12-5fd3e2793a4a | textbox | Comments
3f6e3783-d330-4e82-a216-7ab985191d74 | signoff | Add Operator Signature
f226d7ff-1125-4fa5-992d-18fe03411d2a | checkpoint | 5
69bc1f01-95c6-55bd-b887-b31530c3be3c | textbox | Time
b6d14249-afde-58bf-828c-9575e1cd446e | textbox | Ambient °C
bf96f1b8-2626-5ba9-a4d9-b26e46cff50e | textbox | Heater Plate °C
c67ff2b4-e8db-5d1a-b2be-31b94a633695 | textbox | Drag Pressure
e5aa1bd9-34a2-58f2-8e77-a298040db2aa | textbox | Bead Up: P1 (Kpa/Bar)
cedd231c-8929-5c3a-8c9a-d0617f81c59b | textbox | Bead Up: t1 (Evidence)
65512163-df8a-5311-9754-2b4811eb4ca2 | textbox | Heat Soak: P2 (Kpa/Bar)
fc5a3130-59c0-5716-84a8-fa421cf83997 | textbox | Heat Soak: t2 (Seconds)
a5997859-8139-568a-99e4-d7ab8fb19c0a | textbox | Change Over: t3 (Seconds)
fd64297b-3374-520c-9df6-25e42f68590c | textbox | Pressure Up: t4* (Seconds)
67c35373-bb5b-5d37-a454-28ae47fb03c7 | note | *t4 not applicable for SHP situations
c6792811-200a-595d-8bfe-1bc982f90f52 | textbox | Weld and Cool: P3 (Kpa/Bar)
a337956e-f506-54f6-9be3-61e351f121b1 | textbox | Weld and Cool: t5 (h:m)
2ec0a231-f276-538a-9cce-ac0f3f6c9ee8 | textbox | Rough Handling: t6 (h:m)
03ee8eb3-e39f-5de1-b5b0-ab338077fb95 | textbox | Bead Size: Min
85f227a3-9f91-58c0-b80a-1bdaca481562 | textbox | Bead Size: Max
3cab636e-5003-5283-b849-a6d676b3d2ec | textbox | Comments
4b2698ec-f4d0-4c88-a67f-a06c10fcc9cb | signoff | Add Operator Signature
7d9fe374-92c9-4fac-9950-1713e6449a75 | checkpoint | 6
a23f1307-9484-5fd9-b238-a6b3134408c6 | textbox | Time
accd3e64-41eb-5ad2-8ae9-8e62fad99146 | textbox | Ambient °C
f28a0688-f193-52ff-80fd-c14dd317d588 | textbox | Heater Plate °C
fbcdbf5b-4a34-557e-8b08-cb28d54daae6 | textbox | Drag Pressure
2a056604-e17b-5389-9d26-08bc59334f54 | textbox | Bead Up: P1 (Kpa/Bar)
8f717547-fed8-520a-b8eb-2dbd36b5eef4 | textbox | Bead Up: t1 (Evidence)
37686f27-a73d-5ebd-bfa6-9c6d7e4f8cc7 | textbox | Heat Soak: P2 (Kpa/Bar)
ba611528-e0b2-5750-a010-3409041ab5ce | textbox | Heat Soak: t2 (Seconds)
f732a889-9719-5f7b-adf0-c60afae245ff | textbox | Change Over: t3 (Seconds)
89dddf73-ea2a-5e01-b9db-e990ae1ccb0f | textbox | Pressure Up: t4* (Seconds)
ee83b1b7-f729-5410-98d4-86af3c15dff3 | note | *t4 not applicable for SHP situations
64fd781d-14df-5e15-b977-d72ed81d0e9d | textbox | Weld and Cool: P3 (Kpa/Bar)
53912f23-b5ad-518d-b511-5bfd917554ba | textbox | Weld and Cool: t5 (h:m)
3a6c5992-a980-5396-843b-27ddabef9623 | textbox | Rough Handling: t6 (h:m)
bcf48abe-b4da-5d9a-9cbb-9f737424d824 | textbox | Bead Size: Min
c9309dd9-579b-5a73-994d-107a4888d3dc | textbox | Bead Size: Max
7581ab74-c284-5802-91a6-f62ad3f34c6e | textbox | Comments
0f4621a1-e118-43f4-926e-1885f84485fd | signoff | Add Operator Signature
51abcd03-87ab-4111-866a-ce4687887418 | checkpoint | 7
576a7d07-6210-5c45-9d7c-012c9a51ca73 | textbox | Time
10177ab7-81b3-5a16-bae4-4b4018737c9b | textbox | Ambient °C
1939e624-399e-5e9b-97c5-c9c212b28fdc | textbox | Heater Plate °C
f242c3fd-4dfd-58a2-a89b-8b2853ecfaf9 | textbox | Drag Pressure
6f2dd8ff-5afe-5ec8-84fe-4130a87f67cf | textbox | Bead Up: P1 (Kpa/Bar)
e056bfe7-34a2-5589-9f4f-4f2cedae39bf | textbox | Bead Up: t1 (Evidence)
a427faec-f5e0-5d3a-89c9-45837b42fadb | textbox | Heat Soak: P2 (Kpa/Bar)
2e070011-7df1-569d-bbeb-1e951d10fec9 | textbox | Heat Soak: t2 (Seconds)
ebe72cce-2d71-5206-ba90-b84e64573966 | textbox | Change Over: t3 (Seconds)
06a76c79-8d04-5c99-8555-3944a1bb37c3 | textbox | Pressure Up: t4* (Seconds)
081acbe9-6157-5df4-b991-838ed87522ba | note | *t4 not applicable for SHP situations
3e803c08-8cde-570c-87c1-2f8c64db9207 | textbox | Weld and Cool: P3 (Kpa/Bar)
2ca472bb-c59a-5cb7-ad4a-661f29515cfd | textbox | Weld and Cool: t5 (h:m)
aa910808-dc4e-53a6-9c81-800a784e8adf | textbox | Rough Handling: t6 (h:m)
f175024a-1a19-5db8-a0d9-7cdcb89ac717 | textbox | Bead Size: Min
43293fb7-36f0-5f03-8d64-a6220f77ae9c | textbox | Bead Size: Max
667bb8a7-38ed-5223-8b0a-7828939aa55e | textbox | Comments
fa477787-4749-4a5c-a9b7-3e9fa4927a74 | signoff | Add Operator Signature
c664f31b-a383-4f76-a2bb-f521c2d4b7af | checkpoint | 8
cffce91b-06f8-570e-adfd-855052f0f9d7 | textbox | Time
ba83d04d-71b4-510c-bdc9-76f0e0ce5fb8 | textbox | Ambient °C
a3efcac4-16ba-5651-b104-f8cf48ac19da | textbox | Heater Plate °C
bcde68c3-8cb0-58ea-bb03-8387d35d297a | textbox | Drag Pressure
746e00be-1e8e-5a6f-86aa-659ee4d9bbd7 | textbox | Bead Up: P1 (Kpa/Bar)
52b2ea25-d2c0-58da-9877-cab72f637f78 | textbox | Bead Up: t1 (Evidence)
0ddde356-382b-5591-8225-40e29cb678f9 | textbox | Heat Soak: P2 (Kpa/Bar)
ad88e12c-6fb4-50e4-822d-3b2c2f9271be | textbox | Heat Soak: t2 (Seconds)
8d958bdd-6fd0-5888-a863-960e8a566079 | textbox | Change Over: t3 (Seconds)
cdec7d12-ca7c-54cb-848d-3eb39c253212 | textbox | Pressure Up: t4* (Seconds)
8fa48dd4-1e64-5b09-8977-922226d11b19 | note | *t4 not applicable for SHP situations
93352852-155f-53a0-8756-6c8a77151685 | textbox | Weld and Cool: P3 (Kpa/Bar)
1d7d4a33-9ba2-51c5-89ae-f13975be6be7 | textbox | Weld and Cool: t5 (h:m)
6aa72222-d729-5a0e-a9f6-be3f885ea2a8 | textbox | Rough Handling: t6 (h:m)
96712186-514e-5eca-9822-7274456f5617 | textbox | Bead Size: Min
cb109a4f-ee97-566e-84b5-047147a5eec7 | textbox | Bead Size: Max
cebbfbb3-5c85-5a42-9f7e-e082176c1009 | textbox | Comments
17dfbec2-a7b7-4cc4-b35f-f2f648b64357 | signoff | Add Operator Signature
542229ce-f3aa-415a-83ea-64db0f979b69 | checkpoint | 9
6d0c4034-ad08-536b-aab2-f9c1deda9067 | textbox | Time
00913794-64a8-5458-8d12-97342169662d | textbox | Ambient °C
93a1c7b1-451b-5539-8ac3-314173519f18 | textbox | Heater Plate °C
e9ad2dfe-a16e-52b3-8ace-5a0f9b8e24ea | textbox | Drag Pressure
efc5c50f-a271-5a21-abcd-0d0fa0b22bd6 | textbox | Bead Up: P1 (Kpa/Bar)
cb5ad200-2389-50cc-99ec-3d0aec4c9685 | textbox | Bead Up: t1 (Evidence)
dd65ef4c-f7cc-5a00-8abe-0e3eabcb3af4 | textbox | Heat Soak: P2 (Kpa/Bar)
aceb9d94-b173-53f0-9cbb-7065f34eb2eb | textbox | Heat Soak: t2 (Seconds)
b770c9a4-68a2-5efb-a81b-207a765a1bdf | textbox | Change Over: t3 (Seconds)
6b198f3d-3e30-5066-a0d9-7a1185e25be9 | textbox | Pressure Up: t4* (Seconds)
f86e0fbe-4a21-5fbb-9247-9b9f7b0ba67c | note | *t4 not applicable for SHP situations
7829904a-0f6f-5f82-aa71-778093e86661 | textbox | Weld and Cool: P3 (Kpa/Bar)
bc63a418-263e-5d46-b7cf-1654819b0228 | textbox | Weld and Cool: t5 (h:m)
0bd72aac-168d-52f2-9d5f-cf2537425b51 | textbox | Rough Handling: t6 (h:m)
0b25c50b-46b9-5e54-9990-0750a150b8b2 | textbox | Bead Size: Min
538a00c9-5a5a-5eee-8af0-cb752b519daf | textbox | Bead Size: Max
43221f13-0010-5247-bff3-7e9c15aaf19f | textbox | Comments
3d327ed6-b7ab-4030-8d41-16a24cdb1d79 | signoff | Add Operator Signature
ab365fb3-5a45-47d9-b48e-20fa7f8c96db | checkpoint | 10
989d37f7-1dca-53d1-868f-ce5a179f7cdc | textbox | Time
6a76c0d6-5dab-50e2-acf9-2d647c9e34cb | textbox | Ambient °C
b37d606b-ee07-5479-ba28-893437a41b7e | textbox | Heater Plate °C
6364897a-8aff-51b7-8eb2-b52998a25815 | textbox | Drag Pressure
a7418b25-ff41-521b-9093-1aea5b773a9d | textbox | Bead Up: P1 (Kpa/Bar)
37cc1590-1127-516d-adf7-92f86376d50f | textbox | Bead Up: t1 (Evidence)
d856c2df-9510-5eb9-8717-7b55c74c4017 | textbox | Heat Soak: P2 (Kpa/Bar)
b405f91d-35e5-5196-8492-9d5b2659da8a | textbox | Heat Soak: t2 (Seconds)
589a2be7-95ba-598c-9e8e-b7bc87e719cc | textbox | Change Over: t3 (Seconds)
f97ec113-1f00-5897-bb55-593c98280302 | textbox | Pressure Up: t4* (Seconds)
6ea30aaf-9505-569b-a8e3-6896f33f64b6 | note | *t4 not applicable for SHP situations
c58ed856-88bc-5cd6-a455-aa9930f17d7b | textbox | Weld and Cool: P3 (Kpa/Bar)
5a5ce15c-91b7-518d-97f1-cbe83430a942 | textbox | Weld and Cool: t5 (h:m)
dca0ef3d-8571-5895-ba4d-e645dc6d9516 | textbox | Rough Handling: t6 (h:m)
2a0d7df7-cfd5-53e4-8dad-19b2da98fdcb | textbox | Bead Size: Min
b143b932-3c6a-5453-89cc-0559d31648ad | textbox | Bead Size: Max
7afd6e24-6ab7-52e0-96ea-af7290c781da | textbox | Comments
63e4df0c-6c38-4483-a95f-5b45b5bfa079 | signoff | Add Operator Signature
6a0161f5-213d-4aaf-a527-9d98ef4e4390 | checkpoint | 11
3d7ead7d-8b74-5474-9e69-b1659ac14bda | textbox | Time
3b9edc93-1a3c-5833-b9e7-86c972e5604c | textbox | Ambient °C
082ffb5f-7f62-5a00-9489-3ffd9dc48eac | textbox | Heater Plate °C
cbd7b7bf-c825-52e8-a237-63339d534def | textbox | Drag Pressure
5ded405c-a2a7-5201-a3e5-8e62d4e43e1a | textbox | Bead Up: P1 (Kpa/Bar)
3d1a7e0a-37a5-5f17-9d96-83e1bc1edfcd | textbox | Bead Up: t1 (Evidence)
3972680b-511a-5e0c-9cbc-42854419f2c3 | textbox | Heat Soak: P2 (Kpa/Bar)
a6a15810-7640-5059-b8b6-7b6b70bde327 | textbox | Heat Soak: t2 (Seconds)
aacb3675-30b6-545c-af0e-ab085c97bbc0 | textbox | Change Over: t3 (Seconds)
9d348b1f-0dff-5764-a5e5-a03dc18a42ff | textbox | Pressure Up: t4* (Seconds)
194639c2-19d6-5c7d-9699-75de13501daa | note | *t4 not applicable for SHP situations
cfcb0059-5ed0-5815-b4eb-d4562dbbf774 | textbox | Weld and Cool: P3 (Kpa/Bar)
ad598669-db2a-5f88-9b4b-0de5ec3ea375 | textbox | Weld and Cool: t5 (h:m)
3cf0206f-7a8a-5b55-b772-5a320675853f | textbox | Rough Handling: t6 (h:m)
2510eb3e-86e7-5e6a-927f-1572bca20c5b | textbox | Bead Size: Min
83e73824-7960-5a27-820d-4b65e3f12340 | textbox | Bead Size: Max
ef08e390-37ba-5a63-b946-3299cca36f11 | textbox | Comments
100e6379-ed12-4278-b152-e4843f8d8e02 | signoff | Add Operator Signature
6f3d33be-a4b2-4640-b9e1-691a8d6de10a | checkpoint | 12
b1477e2f-90da-5aa1-a9f4-d6d4b80a9841 | textbox | Time
60f154b1-ee40-5a2a-9f95-366a93df6ee8 | textbox | Ambient °C
30242c58-f01e-5f44-91d0-20b9d16947df | textbox | Heater Plate °C
e4517505-1738-5743-ab48-5724f43eebe6 | textbox | Drag Pressure
623d21d4-502e-50f1-92b5-ae71ff31eec7 | textbox | Bead Up: P1 (Kpa/Bar)
1a6ea388-ed0f-5db8-bf2f-5c2e26e51407 | textbox | Bead Up: t1 (Evidence)
8177d62e-5c3b-517c-850c-b6f4d5e55bef | textbox | Heat Soak: P2 (Kpa/Bar)
9628e1ad-a815-56ed-ac19-6bfad2bfb20b | textbox | Heat Soak: t2 (Seconds)
8dfe4d09-ec75-53a2-ba3a-18d7a2375ff3 | textbox | Change Over: t3 (Seconds)
6d741cf1-2b6f-5c4c-b803-f6d697173a64 | textbox | Pressure Up: t4* (Seconds)
9508d90c-7c92-54df-bfce-f642607fc6af | note | *t4 not applicable for SHP situations
6b18621c-26bf-5b46-9fd3-da7872256f8d | textbox | Weld and Cool: P3 (Kpa/Bar)
4c7f986d-da36-505f-af3c-199f5f7d7e46 | textbox | Weld and Cool: t5 (h:m)
738c99c3-1a51-5a34-95a0-db8cafd2b594 | textbox | Rough Handling: t6 (h:m)
6cef81af-4ead-57e7-be96-7b3b482bc193 | textbox | Bead Size: Min
cdce2bdf-789c-5930-9d5d-3eb0d8d15d56 | textbox | Bead Size: Max
d5daf69d-4e7a-5563-b777-a8666d4155d9 | textbox | Comments
50beb9d7-950e-49be-911f-364cffc12cca | signoff | Add Operator Signature
6efcc9ae-4f38-4779-9fe4-7e2651a47ac7 | checkpoint | 13
7f22aad9-4cec-55c7-9ebf-3d4b18cbf3cf | textbox | Time
3ccd84ac-a7fc-53a7-96bc-8c6f5abf442b | textbox | Ambient °C
13f64288-e5ec-5191-ae79-5c0feca1c2fb | textbox | Heater Plate °C
893fa059-1fb2-5e45-a481-f9c8b77a9497 | textbox | Drag Pressure
681e672e-28d3-5ddc-b4b6-fa498779a37d | textbox | Bead Up: P1 (Kpa/Bar)
0ee0fa1f-f61c-55ab-a252-785aca88de36 | textbox | Bead Up: t1 (Evidence)
7cd8ecb1-da47-5b2f-ba63-b76b2f1d2d29 | textbox | Heat Soak: P2 (Kpa/Bar)
533434a7-5dd5-5587-892e-17f753aa743f | textbox | Heat Soak: t2 (Seconds)
fb8638e1-7647-5bef-9b67-3dde564da37d | textbox | Change Over: t3 (Seconds)
26e28dee-181e-5446-b4e6-1c131d333b5b | textbox | Pressure Up: t4* (Seconds)
54fd114e-f905-53d9-a922-7fddbf26ea61 | note | *t4 not applicable for SHP situations
b877fd11-1d69-5696-893a-c22d80654c2a | textbox | Weld and Cool: P3 (Kpa/Bar)
81f0a526-826c-51e5-9605-0b4b2adb2a0d | textbox | Weld and Cool: t5 (h:m)
165b1273-0c2c-53be-bfb6-e3f743f19f14 | textbox | Rough Handling: t6 (h:m)
0448c423-04e3-53cd-bba7-d954809de1b8 | textbox | Bead Size: Min
0cd0bb17-28a8-563f-9a1e-393080078117 | textbox | Bead Size: Max
76480249-2b8b-5a82-82c0-d6afbb4d24c2 | textbox | Comments
4c4c0234-a250-47b7-89af-5c2915fdd498 | signoff | Add Operator Signature
17424204-8d15-4360-b2dc-5a1b23ed1573 | checkpoint | 14
25a50c9c-f990-5896-80fc-dbb6069b30de | textbox | Time
058d6fc1-fbf2-5002-ae81-a7e782813e11 | textbox | Ambient °C
a007c929-67c1-5265-ba96-0d5b8c680619 | textbox | Heater Plate °C
cffb182a-b779-54f5-bb9d-d29c0b387a34 | textbox | Drag Pressure
00b27f12-3168-597d-a462-252e836188ab | textbox | Bead Up: P1 (Kpa/Bar)
2e237248-e882-59ae-a35d-0043c0ad51ae | textbox | Bead Up: t1 (Evidence)
5e45aa72-2f2e-5da0-b337-39da966c7ca3 | textbox | Heat Soak: P2 (Kpa/Bar)
41d80900-0578-5cc0-aa81-e1e20408d566 | textbox | Heat Soak: t2 (Seconds)
c669d1c8-276c-5bdc-90f8-350c69012369 | textbox | Change Over: t3 (Seconds)
717bb71d-3d85-5da8-9679-c1e34cd0e2b3 | textbox | Pressure Up: t4* (Seconds)
d8b417a3-d554-51d1-9f4b-7910fe230fde | note | *t4 not applicable for SHP situations
383ff3bf-c94b-5f67-92e3-6dc2e0b9533b | textbox | Weld and Cool: P3 (Kpa/Bar)
81658527-4f85-5bd4-8c82-7d097176c816 | textbox | Weld and Cool: t5 (h:m)
26089edc-57dc-5c2c-a0c0-b539b6da16fc | textbox | Rough Handling: t6 (h:m)
a9010052-7084-5fe4-a1e7-13d978af3521 | textbox | Bead Size: Min
9f00144b-cf88-5cf9-a315-e538cdb9189b | textbox | Bead Size: Max
866e0448-2e58-54fb-8d77-d34dca9f1bcd | textbox | Comments
e86cf32e-06d7-48fc-a576-4beb55ef035e | signoff | Add Operator Signature
4bb1d362-f5a8-4f96-a0fa-abaf05286685 | checkpoint | 15
8706635d-8618-591b-b6a7-11165403e34a | textbox | Time
b2885511-fefe-5ea8-9783-067dfba876f1 | textbox | Ambient °C
a9a9780f-64e0-5125-bb2a-f78c218ec3a7 | textbox | Heater Plate °C
14b402bc-7ce4-56f3-b75e-a2cf5686fe7c | textbox | Drag Pressure
541adbff-b1c1-5baf-a56d-82b4c458f21b | textbox | Bead Up: P1 (Kpa/Bar)
139de3fd-4682-5fcf-b1ab-ab6336a51a1f | textbox | Bead Up: t1 (Evidence)
498f9cda-6904-5cff-8844-f9f167a08046 | textbox | Heat Soak: P2 (Kpa/Bar)
a13fa3e8-3887-532e-961e-3be96b1464f2 | textbox | Heat Soak: t2 (Seconds)
8a7c73da-dce1-507e-9539-20e0a4b26f92 | textbox | Change Over: t3 (Seconds)
ec1b0e9c-d6bc-504f-a8b5-f4f82066aa3a | textbox | Pressure Up: t4* (Seconds)
e1370374-6e25-584b-b366-0dde65045053 | note | *t4 not applicable for SHP situations
6c60040c-d3c6-5333-a89a-56c7f714cc8e | textbox | Weld and Cool: P3 (Kpa/Bar)
e365b60d-172e-5baf-924b-acd7f602a684 | textbox | Weld and Cool: t5 (h:m)
095027bd-023d-5e04-b1ad-034d2daeea97 | textbox | Rough Handling: t6 (h:m)
f16b5e3a-dbce-5973-9195-3199dee6be1b | textbox | Bead Size: Min
23907499-e1a6-59c0-9c2a-08296860988c | textbox | Bead Size: Max
bfe3db3f-b35b-5802-b91c-e63341c59e04 | textbox | Comments
7bbde2b6-59a3-4fce-af42-674bfff325fe | signoff | Add Operator Signature
207a155a-6db7-4ee1-b64c-c3261f7b6cab | checkpoint | 16
1afa5649-4800-5cf6-8fda-38842f7897e4 | textbox | Time
6d3dbcc3-a5fe-5de5-ab60-d12e46ba8a59 | textbox | Ambient °C
17f0ea56-14dd-5a80-b47c-c9c715e37885 | textbox | Heater Plate °C
892c87a2-4c1b-5138-bdc0-a6a7778335bf | textbox | Drag Pressure
96b5e1c9-080c-59b4-bc94-dbe6d128db52 | textbox | Bead Up: P1 (Kpa/Bar)
34ef3245-d368-5aca-8aa5-78cd9fd21cda | textbox | Bead Up: t1 (Evidence)
92414874-bd56-51df-adf7-4cb5cd7dfed7 | textbox | Heat Soak: P2 (Kpa/Bar)
244967b2-d331-5ea2-bd19-3a6525c566ad | textbox | Heat Soak: t2 (Seconds)
68b7beac-85fb-51b7-9d8e-f234f3dc80a3 | textbox | Change Over: t3 (Seconds)
b92d9ce7-6dbb-5f84-89e1-80da8cc446a7 | textbox | Pressure Up: t4* (Seconds)
790fefce-3fd5-556e-9d1c-b156c987e7bb | note | *t4 not applicable for SHP situations
e980baad-6f3b-59b5-818f-0770ffd2e711 | textbox | Weld and Cool: P3 (Kpa/Bar)
c77b44ec-48bc-5df7-ac38-c155b2b9aadb | textbox | Weld and Cool: t5 (h:m)
0ffb31f4-b25e-50ac-9df6-d4379f932855 | textbox | Rough Handling: t6 (h:m)
a69df316-24a2-5778-bca2-c40cf4113c12 | textbox | Bead Size: Min
e46a1c1d-7821-50fb-811c-24f01d58e509 | textbox | Bead Size: Max
ca635c07-8980-5184-b0e5-570747e50709 | textbox | Comments
f40e2a6f-f619-426b-8530-32824a592de9 | signoff | Add Operator Signature
c90a5a90-6eed-458a-9039-f8e5cb76194a | checklist | Commissioning Test Report |  | Commissioning Test Report
77918e25-24fc-4773-bdbe-88dd29779994 | checkpoint | Commissioning Test Report:
fb603f87-8400-532d-8a03-7e8af838a3ae | textbox | Zone/Grid:
5dcd0216-927e-5c27-85f0-797486a2d311 | textbox | Drawing No.:
57f7fd10-6df5-503e-b55e-508917c59ff2 | textbox | Rev.:
aea210d6-0150-4bf3-860c-364870ca8c88 | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
6e104c68-2729-5d2a-a69a-fcbf983fc0a4 | note | Test:
93253996-c4d6-5048-93fe-920aebac7667 | note | Performance Test CL 2.20
e2c41440-c87b-5385-a96a-fcb9567aed69 | note | Fill fixture with water remove plug
5288688e-128f-5259-8a3d-c17373ebbf06 | note | Test for:
ceabfb2b-1a92-58b6-8fb1-307891385617 | note | Leaks
baf820f4-06da-53bd-a22b-b5ba67365bd5 | note | Loss of water
408d2dfa-0112-5f14-a067-1ec846fdae21 | note | Seal in Trap
40dc79e9-be89-5817-a628-8694f1e80ab7 | note | Induce siphonage in trap of adjacent fixture
394911d8-04f2-588b-aa71-31bd15ca6a17 | note | Complete draining of fixture
777b6ba2-e95a-5b09-bc4f-850f971d9eb2 | textbox | OK:
145cfcf2-aa6d-5de1-b456-581ba5979974 | textbox | Not OK:
d01405d0-da58-499f-87e1-326a873917fe | checkpoint | Item: Water Supply
da6b3b2b-4c53-5a70-9cac-1c36e7e04bbd | note | Test:
f1dd65c7-fb31-5bd8-8687-894e3181fba6 | note | Performance Test CL 2.20
c59984d5-4b0c-5d3c-a0ed-c4ad73c13971 | note | Check for adequate water volume.
2ff0b406-ca43-588b-a7dc-68330ae209e8 | note | Flush out pipework
44ca171b-be76-59fc-a80d-fe2cc1d73731 | note | Clean aerator
d0069198-665b-5472-8fef-8d0c219f84d8 | note | Water hammer
4b5980de-d5e0-54d9-923a-b79b9765aff4 | textbox | OK:
7e40697c-2db3-5c67-93ce-de3ca9b638dd | textbox | Not OK:
060e2032-3b22-49e3-b3f6-c287cf97ec54 | checkpoint | Item: Flush Performance
4e005935-756c-52dd-84dd-85d010854fb2 | note | Test:
72b744af-a43a-5871-a594-21386598b78d | note | Performance Test
1adfa283-7aab-586e-9f51-7b9e99ee9761 | note | Check for:
fd415f18-c2cd-56d7-b834-6b3cf34c6477 | note | Water Volume
41595a59-b437-5cbc-804c-0f32b2ea7f0e | note | Duration of flush
f2bb3a53-cad2-5a12-bea3-783330578860 | note | Flush out pipework
e1976303-a3df-5a54-98c2-efe870dd195f | note | Water hammer
13e73590-9526-5074-8c9b-024f14c449fa | textbox | OK:
92e790ea-52a5-524c-aa4e-934b598f8cf8 | textbox | Not OK:
3c6dbe14-f415-4ce3-90e9-87077e49c01d | checkpoint | Other
1003df4a-c23a-4e99-acd2-e392410050bc | checklist | Equipment Calibration Register |  | Equipment Calibration Register
dfc8c895-07b7-482a-a78c-b390dcd827b4 | checkpoint | 1
95a97b3c-10bb-528b-a109-55efc5d1a54c | textbox | Equipment Type:
f747e589-6d81-51de-bc3d-c17964ccc637 | textbox | Manufacturer:
cf53e070-5431-5ffb-b8d3-99524f96c1d4 | textbox | Model and Type:
4688502b-e6f2-5edf-bfb4-8136455d8357 | textbox | Serial No.:
1d3b540c-65d6-5904-87a7-783b234f76f7 | textbox | Next Service Due:
9e5ec280-1c92-4106-ac6e-731c5cbed2b0 | checkpoint | 2
0bb13184-cf3b-52b4-a34f-95fca2f7d7ab | textbox | Equipment Type:
104a2c6a-0650-5b95-829c-bde39fd1e347 | textbox | Manufacturer:
440fde14-f9fe-5600-a633-9e618b0a295a | textbox | Model and Type:
300c2c3a-ffc5-5530-b436-4c876f9cfcf3 | textbox | Serial No.:
db13d696-9791-5959-a090-a95a13fc097a | textbox | Next Service Due:
eebf6cc9-8b76-47d2-8661-de1a1f4bc84e | checkpoint | 3
6b5c0dc1-320d-5084-ab19-e24963ff59a9 | textbox | Equipment Type:
db74e51d-dbae-5df3-ab9e-459abaa38f58 | textbox | Manufacturer:
f0ae120d-d621-5079-bb69-fc4c7b39ddc7 | textbox | Model and Type:
2ad1c866-d4f6-5153-a2be-712c46efd296 | textbox | Serial No.:
adc33d11-7e73-5321-a833-d94833bd063f | textbox | Next Service Due:
9b041a0c-8553-484b-ba1e-61c136e25165 | checkpoint | 4
765c23e7-5f52-5b5c-98a6-315d5b103e63 | textbox | Equipment Type:
c5ca64df-1226-5804-be61-27bc6030ea34 | textbox | Manufacturer:
bce16dd6-4807-57bb-86f3-ba872afbbc9c | textbox | Model and Type:
627fa33c-118e-5517-99f2-528534108866 | textbox | Serial No.:
8c842c16-ac52-5f5f-a2e6-57ee78e5578c | textbox | Next Service Due:
8c8ba827-9050-4847-b639-0bf748ec5980 | checkpoint | 5
400038bc-6156-52a2-a8ef-d54a3b3249b9 | textbox | Equipment Type:
e22f6196-4531-5c34-b18c-4e8dddcfe5c6 | textbox | Manufacturer:
374ae095-1f12-565a-ba26-1c2f6722474c | textbox | Model and Type:
7285b791-39a9-5a7b-a800-19dde482b4fb | textbox | Serial No.:
291fb44b-e090-52c3-9efe-8d4e1cc9f933 | textbox | Next Service Due:
3f10603d-32c7-47bb-8e31-6f85bfda66ee | checkpoint | 6
66a789c9-c410-54e0-9014-2ff60577e62d | textbox | Equipment Type:
e7ff2d58-aca0-5d2f-bfed-2609fe38a805 | textbox | Manufacturer:
db17d73b-40f1-541a-8ecd-96ae08abeee4 | textbox | Model and Type:
dc55ea66-8991-50ba-8bed-02c4560f3ffd | textbox | Serial No.:
e83e2e56-4939-53f0-b94c-469b31375b71 | textbox | Next Service Due:
1ac92075-1b93-410f-8176-f06dfae32e12 | checkpoint | 7
52926a0b-bde0-52d0-bbe5-09c384081456 | textbox | Equipment Type:
87903024-a697-574c-9826-fcdf51eb5718 | textbox | Manufacturer:
aedd310c-0dbc-5158-8f82-ddb8afa18254 | textbox | Model and Type:
17b432cd-8ad7-55f0-946a-053bb34c08ab | textbox | Serial No.:
0271ccfc-227d-58b5-88b6-c68c178dc08f | textbox | Next Service Due:
2f8228c6-90c6-4f47-80c4-b51426e9be04 | checkpoint | 8
02272211-defc-5767-81be-0ade96467197 | textbox | Equipment Type:
612ac1dc-548d-5077-8628-3ba86817e54c | textbox | Manufacturer:
45e5d31f-a574-50d3-8f40-2303e4dd2d68 | textbox | Model and Type:
1a8d4f17-2229-524f-9696-547804feed30 | textbox | Serial No.:
155d99da-a733-56cf-a04e-aa7ad957c78d | textbox | Next Service Due:
5427ca2e-8cc0-4dde-a130-8b05fc7fa1c2 | checkpoint | 9
7c017f97-4081-5ab3-824d-a2b62da800bc | textbox | Equipment Type:
7e4da34d-f6e9-57fb-8f48-9d14a55271e6 | textbox | Manufacturer:
92d56ef0-2e0f-57bb-959c-85f5d405d4ae | textbox | Model and Type:
c87aa5ea-3453-59e3-9ae3-160c8b931d26 | textbox | Serial No.:
eeb0b373-c297-5df6-a1e3-89136703f46a | textbox | Next Service Due:
a5663853-4c6d-463f-aa4e-11b43ce3e780 | checkpoint | 10
17675471-a401-5640-9812-9a9d6646b6fd | textbox | Equipment Type:
d0b04450-91ef-559e-a2a2-03159b1a62fb | textbox | Manufacturer:
350af108-e711-57b4-b885-9de4052a3686 | textbox | Model and Type:
317f071a-1d3a-5876-a9bb-a3fdca9f202a | textbox | Serial No.:
12838320-1066-5d93-9f9f-ed95a47f2ab3 | textbox | Next Service Due:
f536cfbf-76c0-483a-80aa-43b6e2e6cf33 | checklist | Fire Hose Reel (FHR) Test Report |  | Fire Hose Reel (FHR) Test Report
af571ae0-2266-4767-bbc8-10b996b66284 | checkpoint | Fire Hose Reel (FHR) Test Report:
25ee78da-2390-58ae-8a47-95f69258a483 | textbox | Location of FHR:
249a901c-8ab2-5a4f-9391-67eda7f17101 | textbox | ID Number of FHR (If applicable):
d477c313-f0dc-58ff-9952-3e052cfaf667 | textbox | Manufacturer:
d2152ac7-1731-5790-93dd-ec1dec62bfc4 | textbox | Model:
39678427-ebf7-52db-9834-f2ef0f9ce8a6 | textbox | Size:
e8f21c49-9659-5110-8e7d-f57937689b16 | note | Aust. Standard Flow Rate: 0.33 LPS @ 210-230 KPA
303a5770-9a07-5170-8c0d-cff189e6f18a | button | Measurement Apparatus: | Bucket
5488b7aa-8005-5942-84e4-6918a9a3bfd7 | textbox | Bucket Size:
b417157a-239c-5d94-b9f1-47f47d4fd060 | note | Measurement Method:
22d218e6-5ec2-53b3-8baa-a703bb93c1cd | note | 1. Connect pressure gauge and outlet to end of hose
1ca350f5-0e01-5165-af1f-13c5462e4ec8 | note | 2. Note static pressure reading on gauge
3e35ad81-1856-54a6-8d20-9e59834d49c1 | note | 3. Place bucket at outlet of FHR and fill
70b31d73-308d-4251-b8e2-b1639a8e3e77 | checkpoint | Reading
3f4f254e-3a3a-5584-a3be-621d4c62d1ca | note | 3.3L
45689d11-49ea-545a-94fd-b0d1919950b2 | textbox | TIME (sec)
eee7cb9b-b7aa-5106-a6cc-ab66874e5c9f | textbox | Flow Pressure:
1060af9e-d6bf-5014-8612-dcd2812b015b | note | 6.6L
ee403f6b-924d-5a55-8a74-9c958caae3b3 | textbox | TIME (sec)
911ccb37-702f-5fb1-a5c4-6fdfa289f020 | textbox | Flow Pressure:
a7cd4e87-9268-5932-9a9b-331e383ce5dd | note | 9.9L
5d9980bb-9f7c-50ae-a7b3-b82fc02c4dcf | textbox | TIME (sec)
b13be254-434e-56a9-a275-f35fe2f9e687 | textbox | Flow Pressure:
571d5fad-a6c1-4ff7-89be-e51c650dd69c | checkpoint | Completion
62fa29c4-f154-55f2-999e-5d5c6c482502 | textbox | Geschke Pty Ltd. Representative:
9d3445d6-999b-5367-b0aa-71511bd50a48 | textbox | Others Present:
963c99a4-30c3-5c80-a6a0-f9ae1106318c | textbox | Date of Completion of Satisfactory Test:
ed71f571-7dae-4edc-8600-39ca063f4121 | checklist | Fire Penetration: |  | Fire Penetration:
2cdaadda-40c1-4a22-b4d2-6bf5bf07cd9e | checkpoint | Treatment Type
86f76dbb-9b32-573a-a543-b5d03e323c7d | dropdown | Treatment Type: | A1,A2,B,C,D,E,F,G,H1,H2,H3,J,K,M,N1,N2,O,P,Q,R,S,T,V
0e18de40-f130-4fa1-95b6-b64e23817d88 | checkpoint | Photo of penetration and sticker must be taken
be32c288-e780-5161-ad17-677f2a2d87cc | textbox | Installed by:
80bb7f9e-cae3-584d-83c3-e1ed4d531615 | textbox | Comments / Reasons why cannot complete:
0fa57b38-6575-47a7-931b-4126f1564e47 | checklist | Fixture/Hydraulic Installation |  | Fixture/Hydraulic Installation
cea02c3a-7ff2-4d93-8625-27c3de78df33 | checkpoint | What is being installed?
9cdb200b-53bc-4ae4-8eaa-61532532fb1c | checkpoint | Where is this fixture being installed?
006417e9-fd08-4aa7-a90c-70c9a6d3ceac | checkpoint | Have all parts been connected/completed and tested? If no, please detail why?
7daf3e9c-9b9c-47b0-8795-cc7485caf9d9 | checkpoint | Has photos of installation been taken and uploaded?
d9ae631b-06b9-43f7-bc3e-d5eda12516b3 | checklist | Grease Trap Checklist |  | Grease Trap Checklist
513a3e3b-3e75-4f85-80f0-cd3a484c73ac | checkpoint | Set out of pits.
68ddab24-09ef-4271-8128-b3d338d210fa | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
049a4728-d002-43f0-8d91-9e079115af0c | checkpoint | Bedding placement and compaction and material meets specification.
0233611e-32dd-4b00-9df1-578e8f2dbce9 | checkpoint | Laying and jointing of pipes R.Ls and falls
d2113b4c-cf29-4abc-b793-5a2dab38f8c4 | checkpoint | Connections to pits.
0530915a-5b90-460d-86c3-10e81b2c1e03 | checkpoint | Baffle is in place.
7c1bd4e9-cf4f-4e44-8f10-7bc8e2f9d0a9 | checkpoint | Penetrations are patched and made watertight.
2ced00dd-bc44-4526-b247-50d8404e2f59 | checkpoint | Suction line is installed as per spec.
caf26051-8b14-453f-9494-0e86daa3ea27 | checkpoint | Outlet pipework is installed as per spec.
e6d4c735-7d5e-4336-90c6-1a998d99c987 | checkpoint | Vents are connected and terminated to comply with Authority and Specification.
cf579929-738d-4fad-804b-4d4ada920ad9 | checkpoint | As built information updated onto drawings
4c684dce-7967-4a3d-a54c-ad7ebd66c333 | checklist | Hot Water Service Maintenance Log |  | Hot Water Service Maintenance Log
ddd445ee-589f-48a4-b4a2-a232dc0dd9c8 | checkpoint | Hot Water Service Unit Details
3fbbba82-1523-5024-ae66-6b6a2e6074b1 | textbox | Purchased from:
bcadaec5-f231-56c7-9f62-95fbef300605 | textbox | Make:
06bed521-7fc1-5777-843e-a3b4b98a59f0 | textbox | Model No.:
132d9a24-b3a8-510d-b13c-aa24a9c318fa | textbox | Location:
354fcb19-79bf-5c65-a366-c2a3911680a3 | textbox | Room Designation:
03f6cb10-d9f1-5aa8-b8c6-d5d3d2d8fe82 | textbox | Installed by:
0a840f0c-92ea-5182-a729-47534e23e68f | textbox | Installation Date:
d2c92b1d-3289-531b-8636-4f6ce3db5d27 | textbox | Number of units in series:
f7b19503-3727-5d58-9e4a-b0c48c5d8c18 | textbox | Prescribed temperature set on unit or combined package:
e6fed176-d140-4433-ac96-768d9e15bea0 | checkpoint | Does installation comply with manufacturers instructions
cf7f1085-ae86-4eef-9464-9af27aba0152 | checkpoint | Does installation comply with current requirements of the local water supply authority
ff149d20-7d51-43e9-bcee-53cd6b949783 | checkpoint | Clean Pump Strainers
fc0ccb99-e6f3-46ca-af4a-d0d01e286fd7 | checkpoint | Clean Hot Water inlet Strainer
266172d0-102c-456a-b13c-0169f7eb85ee | checkpoint | Clean Hot Water Return Strainer
5b216ec4-bd0d-4b5a-9bd0-68bed914a8a2 | checkpoint | Confirm all Valve Isolation reinstatement
fa9ca881-b062-4d5f-8add-dd14f2713ce5 | checkpoint | Confirm Unit is Operational
d1d086e8-ac9d-46ab-91cd-f4921e8ef3be | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
ebc82330-aa11-4693-9c49-c3d66a4971e1 | checkpoint | Commissioned By:
917226a6-d44d-570a-b72e-1ff72cddc1bd | textbox | Name:
08ee3200-ae53-5eb5-93f9-040d9673cef8 | textbox | Date:
fe4e7975-21c4-4721-bab8-050c9826328d | checklist | Hot Water Service Maintenance Log |  | Hot Water Service Maintenance Log
eb81c975-d653-41af-be40-538e74a73b7a | checkpoint | Hot Water Service Unit Details
81a91478-f462-5705-b1a4-c02b9b272c40 | textbox | Purchased from:
4a9002fb-0650-5fbf-9fc5-e7e21cb04b50 | textbox | Make:
e76f7b06-9385-5ee8-9097-ece512831a85 | textbox | Model No.:
430977f0-80ec-5f76-9110-f6dff69eca24 | textbox | Location:
4cb31f1d-30fa-53f6-b1dd-f2dbfe823d83 | textbox | Room Designation:
1730f07b-40a5-56af-b39b-840713d7fa75 | textbox | Installed by:
13fd8a92-f698-54b1-9bfa-b0ead1728022 | textbox | Installation Date:
3a12bf65-578d-51b9-ae9f-713e56e817fa | textbox | Number of units in series:
3cfdd7de-7093-583a-8fa0-8ab22b87b675 | textbox | Prescribed temperature set on unit or combined package:
c15bf349-49e2-4c4f-a626-7c2bfabf11a9 | checkpoint | Does installation comply with manufacturers instructions
79a349e6-2c85-4650-8e41-511ad84790df | checkpoint | Does installation comply with current requirements of the local water supply authority
82c8946c-3a96-4e2a-939c-249af200ae16 | checkpoint | Clean Pump Strainers
ff226fe2-cf40-42be-afef-ea4292b67041 | checkpoint | Clean Hot Water inlet Strainer
77ee47bb-990f-4ac9-9d07-5f84ae7c27f9 | checkpoint | Clean Hot Water Return Strainer
2e8cd8b3-d49b-47c6-a6cf-5ffbcf70a888 | checkpoint | Confirm all Valve Isolation reinstatement
72d2dfdf-aa69-4cd7-a67e-88dcdace6a7e | checkpoint | Confirm Unit is Operational
f77a7c53-8429-4d36-a8cb-7c41e9bdb7ce | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
a39850d6-9485-4dee-aa33-6b902b8767db | checkpoint | Commissioned By:
6244881b-b851-523a-bbe9-cbecd542fbef | textbox | Name:
6f9b9e6d-6ae9-5b89-afb4-ca51edeede3b | textbox | Date:
3de8a7b4-d685-41c1-aa56-afb51f330e1d | checklist | Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  | Installation Test Sheet (Cold Water, Hot Water & Flusher Line)
b82ec3c9-377b-4862-be5e-a269a91a6d36 | checkpoint | Installation Test Sheet:
42af2465-7b7d-593f-8b13-bd4bf78c5f77 | textbox | Drawing No.:
8e4f357c-0dff-51f0-8f9a-fbb1b6a54bd9 | textbox | Rev.:
013c7921-cb5d-463d-81bb-c7b5c33b0dc9 | checkpoint | PIPE CLIP HANGERS
9d24662b-a8e6-5188-9bdb-270f3f757e2f | textbox | Details:
3ac53b72-410e-54e3-9538-cb927c73581c | textbox | Tester:
9d6c3b68-8a3e-5488-80de-f45544c098e9 | textbox | Date:
936b091c-8235-5f54-b1d4-7aae12ed7760 | textbox | Notes:
02f0aa02-f775-4d6a-baeb-df91215fb2d2 | checkpoint | MATERIAL AND SIZE
e7ded8e5-05d3-55c4-8cc4-9a195c9f2610 | textbox | Details:
b2fafe64-40e2-55f7-af11-bb16baf2e7a4 | textbox | Tester:
cd66ad1b-e257-5602-a8b5-fd613bdca04f | textbox | Date:
0e780fad-1d54-5428-aef7-4ffa00edc541 | textbox | Notes:
0e223e97-9729-4268-9419-e34d7cce6608 | checkpoint | ALIGNMENT
d19be680-6546-5a68-898e-46ef9517cd00 | textbox | Details:
0883bef4-23d8-5e63-84e7-f5072afdae35 | textbox | Tester:
2920d5f5-502a-5ff4-b82c-c9690f936087 | textbox | Date:
ba4eebcf-2e39-5c6e-bb99-df00efaaf30e | textbox | Notes:
d3773ff9-4efd-4759-98d2-323c4941c16a | checkpoint | noteLING AND IDENTIFICATION
cae0968c-e9c9-583b-9137-d31e8d5cc4a0 | textbox | Details:
b232e9e0-9bcd-5325-b60e-2cead80d5531 | textbox | Tester:
63c6b5f2-10a7-541a-b657-f8f434947224 | textbox | Date:
05b959a7-7278-5cd4-bef4-94bbeb75f7c6 | textbox | Notes:
6fa06788-02b2-4754-97b5-9e924449c3a9 | checkpoint | JOINTING
6a314c39-bffe-55ac-af34-f4c19af71dde | textbox | Details:
2034ccf5-28c2-5161-b037-4ddea736e7a5 | textbox | Tester:
9af2994e-b2bd-5cc3-80fc-cb67a6f5d8ab | textbox | Date:
56fe9ea7-272e-51fa-be3a-733af1c7d810 | textbox | Notes:
c70122c1-eaa0-471f-b2de-1ff5cde3b9cd | checkpoint | PENETRATION SEALING
90fce85d-e03d-5c0f-8dc5-c0741f7b58f3 | textbox | Details:
561d3c72-d624-5353-9c43-5f8f82c1d619 | textbox | Tester:
7ed8e1a5-9f31-5217-8318-ae19c6af1f06 | textbox | Date:
bb570cd9-ac7c-5286-91fa-fcce4b5f5af6 | textbox | Notes:
cb191b37-ac79-479f-9039-719820d88df2 | checkpoint | FIRE STOP COLLARS
a27ec393-c6d7-5d9c-a548-27340fd60dcb | textbox | Details:
6a62d00f-9fab-5c14-8073-48cc2e392c95 | textbox | Tester:
7665d589-17fe-5051-ac10-ad835c83bf77 | textbox | Date:
09283b69-61e0-5424-9c85-ee97ce99c875 | textbox | Notes:
ca01ba49-ab8d-4f33-b8b5-f4b0dd8acd64 | checkpoint | PRESSURE TESTING COMPLTED (QA6)
2c4a5c71-954c-5fbb-b241-2cba1c253e46 | textbox | Details:
39ed3e2e-bd3f-5b21-bc36-1ff0f319f376 | textbox | Tester:
64a19637-b8f5-557b-80d0-d2519319be47 | textbox | Date:
e924eb87-9bad-5df0-a754-b4ea7fc899ff | textbox | Notes:
f2568cbd-06d9-4892-bd31-bcc65f680e32 | checkpoint | AUTHORITY INSPECTION (if applicable)
b33cbea6-f56b-5281-991a-f9c2285ddcb9 | textbox | Details:
53f0ae96-9ade-5b24-8a05-27484b80d622 | textbox | Tester:
39f5abba-34b6-5607-827c-8f639955067e | textbox | Date:
37ced103-b09b-5f9f-bba9-84046c09e0bc | textbox | Notes:
773861c6-cea3-4318-9293-8f7316ce48b5 | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
b6666443-02ad-5707-972f-8909a792e644 | textbox | Details:
e937e35e-c453-5413-b684-fd7ea43fa1ca | textbox | Tester:
c8cfc522-2024-5882-8f4c-dca809e2185f | textbox | Date:
71b5167b-2ce1-59ad-a353-7bf08e43fac2 | textbox | Notes:
f1d088bb-8af7-4a85-964f-d9744bd39f7c | checklist | Installation Test Sheet (Waste, Vent, Downpipes etc) |  | Installation Test Sheet (Waste, Vent, Downpipes etc)
68597297-49ba-4802-afb5-0d7e0679f85c | checkpoint | Installation Test Sheet:
8fa94797-9258-50f5-a974-f142580070dd | textbox | Drawing No.:
d2802873-5d2e-585b-97a8-5f37ab591150 | textbox | Rev.:
16e67d90-d591-4546-a82c-666b04bffdab | checkpoint | PIPE CLIP HANGERS
8e8691d9-94c3-53f7-a1fb-157f600adfc7 | textbox | Details:
02ee017d-0638-524d-b290-0c04d203c7f9 | textbox | Tester:
6ace4e12-96eb-51f5-a359-d25034327a60 | textbox | Date:
af62e49d-3702-576b-a1fc-cb2191101c1b | textbox | Notes:
e40e361f-217f-47ce-a008-23c961fc1e72 | checkpoint | MATERIAL AND SIZE
d84a52d1-01fc-54f6-9f5d-41aa9017063e | textbox | Details:
f0b3bfb9-8d8e-5448-8906-83d3cc4a2b1c | textbox | Tester:
c72ae317-e574-567c-9a88-6e5ec4d0cf70 | textbox | Date:
7058c0dd-2614-5d2a-a813-31c9760a6a04 | textbox | Notes:
207eccc5-bacf-471a-8dc5-66792c066bd4 | checkpoint | ALIGNMENT
26dbcd11-9066-5405-baff-5ecfa4436240 | textbox | Details:
c11b716a-3048-5ebd-9357-311bc1e66b7b | textbox | Tester:
27db4d09-3213-548e-a2e3-4c4370499e77 | textbox | Date:
31f47b3d-9f1a-5727-a1de-3aa9ae377114 | textbox | Notes:
40203f79-362d-4f5d-a768-067318722dab | checkpoint | noteLING AND IDENTIFICATION
3baf2ad1-3705-551f-b78c-fad294a345f6 | textbox | Details:
eaabd7f6-2971-5e65-a8dd-0b4216a43514 | textbox | Tester:
6ac35f60-1c38-5245-8d65-2ec89d7ab056 | textbox | Date:
36740728-600c-50dd-865e-d9ab0af6c680 | textbox | Notes:
16ee9016-d7a4-404d-bba6-02fc08b95e41 | checkpoint | JOINTING
75f332cf-37fc-5c92-9d86-788025e06470 | textbox | Details:
44ed2fc6-ad13-58e2-a454-921da87c07a6 | textbox | Tester:
636aedc2-abcd-5b83-a052-8eeb4f635af2 | textbox | Date:
e92e0f97-9867-50d1-9d39-9d40bb8c49c2 | textbox | Notes:
c556391a-6fa1-47db-9a58-5c7e19f366c9 | checkpoint | PENETRATION SEALING
c25b6951-86e4-5831-8c05-a4d4f82b9beb | textbox | Details:
e15aa1cc-7a76-5970-96a7-78c4a8df5786 | textbox | Tester:
c105a3f9-6903-5772-b554-3c4755ca3849 | textbox | Date:
2f758fa9-5589-5ee1-a50a-09dc05245e0b | textbox | Notes:
4c4a72a0-f6ac-4825-9346-726729788e1a | checkpoint | FIRE STOP COLLARS
72a48495-c706-5c86-8aee-91452d3f0601 | textbox | Details:
f96f38cc-e1d5-5acc-99eb-44ab1dd2585b | textbox | Tester:
61857b77-3b58-580d-b09f-67eb1ced34ae | textbox | Date:
5089f0b0-4c4b-52e7-908a-2c9e16766668 | textbox | Notes:
99e09d4f-bb99-4f1c-91bd-cb6c5fcc4885 | checkpoint | TESTING
0369aae2-b3fd-5f8e-973b-399fd3ba85c4 | textbox | Details:
48093629-1c34-5f20-b0a9-2b3d0fbe1eed | textbox | Tester:
6745b7fe-1abe-5912-af60-6f03ef31387d | textbox | Date:
8b9021e0-1875-5e82-93a2-276179bb08d0 | textbox | Notes:
ad4116fb-30cd-4022-8d1f-eba84d1fb683 | checkpoint | AUTHORITY INSPECTION (if applicable)
02d1e541-5a75-5f95-ae48-00c471e9fb7f | textbox | Details:
5544ec11-0173-55eb-a8b1-9bb200be095c | textbox | Tester:
05f484bc-ff64-578c-9757-74d4c3dc9d9b | textbox | Date:
01cf8df0-ea75-5bb0-84f6-4a1e851fb008 | textbox | Notes:
7dbfd0e7-6a69-4245-832e-0364157c59db | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
936c04fe-7c40-5571-8a07-13babda46a6a | textbox | Details:
42b53080-a73e-5d81-b85a-b14f27c83bd7 | textbox | Tester:
57cd608b-4d09-53ad-820f-28c39bb673ce | textbox | Date:
a7b6db15-cdcb-548d-b2a5-467b0b049fa1 | textbox | Notes:
c7af3fc3-ace6-44ea-a309-cb35a8bb8261 | checklist | ITP - Fire Sample Excl. Backfill ACOR Review |  | ITP - Fire Sample Excl. Backfill ACOR Review
2b3391be-c724-422a-9669-b43e74b6424d | checkpoint | 1. Approve specialist subcontractor
f49b2b34-a638-5247-9d9a-27740013ee1f | note | STAGE / FREQUENCY: Prior to awarding subcontract
9a33bd14-7a88-5f31-981c-20959c293312 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
70d947a1-80f9-53ff-982c-54ec83fc2ab1 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
59d9e110-9d5b-5796-b978-8f20071a49f8 | note | INSPECTION / TEST PROC: Document
f8c70e05-b918-5c97-be23-f443f1958921 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
d9e9fc4a-5c9b-5edd-aa27-4f6d5f71fa20 | note | HOLD OR WITNESS POINT: Hold Point
f48246d3-4289-48a2-b9a5-ee55218ad4e8 | signoff | hold point
ac13c8d6-d422-42f5-9991-5a84f48d4018 | checkpoint | 2. Approve Samples
8b637bde-339f-5132-9920-a51780ee2b0b | note | STAGE / FREQUENCY: Prior to ordering materials
1ac7b1fc-c3b7-5572-943a-02625824e132 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
817bb6ee-99e1-5327-8109-496b1f52dbce | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
a6482dfb-f3ce-562d-8147-31b8379eb2d6 | note | INSPECTION / TEST PROC: Document and Review
edd1a4da-6d3d-5fb0-be6b-c4b401cc6a54 | note | INSPECTOR / APPROVER: Engineer. Geschke
402f894f-2405-5b0c-9e7f-eb2d0764f167 | note | HOLD OR WITNESS POINT: Witness Point
defdd583-18f2-42d6-b86f-6f9b399abb44 | checkpoint | 3. Approve technical details
9b8689c6-7d1c-579c-bea3-c808c82e2f99 | note | STAGE / FREQUENCY: Prior to ordering equipment
ddfb516d-b232-5f32-9421-67a178d79f3b | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
f8733e71-6156-5241-8e64-9c46642163b9 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
98299bf7-264b-5d78-a546-cdff1ea76bde | note | INSPECTION / TEST PROC: Document and Review
9d3325cd-c717-51d0-877b-0020a8f6668c | note | INSPECTOR / APPROVER: Engineer. Geschke
40dec951-256a-5c85-8379-d6e1a72184c2 | note | HOLD OR WITNESS POINT: Witness Point
1e5719f5-d22c-49bc-b24c-60d1406c6570 | checkpoint | 4. Approve shop drawings
fc72dc16-4a6a-5119-a8ad-1aece3ba1566 | note | STAGE / FREQUENCY: Prior to commencement
65800562-eec2-5441-bbab-14aee608f8eb | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
478fa7b4-5238-5076-bb80-d3fee71614b5 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
af68b4b6-3009-5cdd-9275-54b369aa37b6 | note | INSPECTION / TEST PROC: Document and Review
e3ac4a56-d570-5ce6-beee-ec1da4c4757a | note | INSPECTOR / APPROVER: Engineer. Geschke
2c92b3bd-9b26-5cc7-b143-429fe6977fc0 | note | HOLD OR WITNESS POINT: Witness Point
a5fb7e08-ada3-417f-98d1-bbccbea4b742 | checkpoint | 5.01. Check set out of excavations
5d98a7a8-89c1-53db-a6ee-4f4b7e659e2d | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
aa4435b9-da86-5655-b307-ba94fc7f49b5 | note | RECORDS: 'Before' Photographs
9e785d31-6459-5144-b202-751644187b24 | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
8f414181-f827-5c4b-a118-6fb0cffc62fc | note | Minimum falls
adc38049-42d1-5d32-ba5a-4b8e5b2d2166 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
29d43408-a104-5b13-ae4b-3ffb36905e6c | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
91c9b317-cfab-5421-b70e-0f741384fde8 | note | INSPECTION / TEST PROC: Visual Inspection and Document
3fb1833c-ba9a-52bf-900c-b88e72f088d5 | note | INSPECTOR / APPROVER: Foreman. LLB
61fe52dc-9e51-5775-966f-388acc71d66d | note | HOLD OR WITNESS POINT: Witness Point
1126fc3c-d65c-418a-b647-311e31908250 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
cb9168cc-bd15-5527-aee9-f913a51af217 | note | STAGE / FREQUENCY: Each delivery
a7a1d18f-15e3-5e3f-9bd2-debca1c456bb | note | RECORDS: Delivery dockets name, signed and dated by Geschke
b35b2a5d-e434-53e2-9943-c32f5510980c | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
6de66979-439b-5c37-89dd-1127c184076a | note | Grade or class matches design
35a73442-5a03-54c2-ac13-ca27f1e2579d | note | Size and thickness matches design
9bd0d2a7-dadd-5c13-bf98-56867798da83 | note | Supplied items are free of defect
97be18ef-fcf9-5ecc-b8c3-857655a8435a | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
90800da0-2730-580a-aed1-6b3e51d5b2f3 | note | INSPECTION / TEST PROC: Visual Inspection and Document
e91943c7-e6dd-5fdf-bce7-ee642aebbd4d | note | INSPECTOR / APPROVER: Foreman. Geschke
8c1459be-e456-5234-a6eb-d73595c38664 | note | HOLD OR WITNESS POINT: Witness Point
45f103a7-27d7-4a90-8603-7e33edc12322 | checkpoint | 6. Check deliveries of materials
637df08b-ae57-5dca-8167-9f0509690c39 | note | STAGE / FREQUENCY: Each delivery
b6cbafd3-2740-53e9-9ae1-e5bfaecb5ff1 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
03fedd25-941b-5619-96e1-3a74bbeb3f30 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
a0cf2128-dc43-5796-8431-bb7e804c5fc7 | note | Grade or class matches design
a414c8cd-590e-5b0a-bd70-4f4b1dafaec2 | note | Size and thickness matches design
bf29827d-9b69-51fa-bf04-f0e060933e97 | note | Supplied items are free of defect
77a9ddab-55b9-569c-b07d-2707a2311e43 | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
1778a07b-5558-57c1-bf50-59c62d13565c | note | INSPECTION / TEST PROC: Visual Inspection and Document
52c2e273-eced-5178-84c8-e25f824d59e9 | note | INSPECTOR / APPROVER: Foreman. Geschke
cc064496-f7a0-5336-88d1-b581a5ceebaa | note | HOLD OR WITNESS POINT: Witness Point
2892d7b1-f9a3-41c2-a99b-12820fa7c777 | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
fe567b77-5f70-5c9c-a22a-cecd2d2e3c9c | tickbox | Standard Bead Profile Test
4f29db72-11eb-503a-9a54-c2b4d953fd69 | tickbox | Standard Destructive Tensile Test
af72a80b-c7bc-5e54-b634-d8292a9be605 | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
1dc894b8-7432-57b8-a41e-13ef0cadfeeb | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
97bfc990-bf92-55d8-b518-eb21187c5ba9 | tickbox | Gasketing Record
69a5af3f-e9a6-565e-b5e0-305f1558be89 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
7d89702b-db41-5f3f-8141-c32a7de19105 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
71c1f060-4d68-58f8-b659-16ad50fa9d88 | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
262d7169-9450-5446-bc17-e81b0bc93243 | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
a8320bb8-d9a8-5882-9b34-98bc8ca035e9 | note | Bead size to be uniform, symmetrical and free of contamination and air.
fd25836f-ecb2-55ff-90a1-f7d8a8736b5a | note | Bolt tightening to be completed using the correct sequence
d9202c5f-1f58-549f-b7a0-20fa5642586d | note | Final torque on bolts shall not exceed manufacture specification.
30c38c1c-7a1c-5266-ac29-d7b5e7f86710 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
db076274-b4d9-57ce-bf72-8f9079704083 | note | INSPECTION / TEST PROC: Document and Review
a838a81d-a2ce-57a4-9bc9-53a81c228b9d | note | INSPECTOR / APPROVER: Engineer. Geschke
9c49a8b3-9319-5af7-9650-fb098a7e1abc | note | HOLD OR WITNESS POINT: Witness Point
5e3d00d4-c87a-4e31-8e45-f27e3975a44e | checkpoint | 7.02. Check below ground pipework - pipes and fittings
ddeebaea-e620-54d7-8201-ef4601699486 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
9fef6850-1e60-5a8e-991b-1c5f970e8771 | note | RECORDS: 'During' Photographs & As-built Survey
7cbcc52b-e4db-5fc6-869d-cd72a1ac595e | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
a4851642-d2bc-56b0-a014-ece26c67baa8 | note | ACCEPTANCE CRITERIA: Service type clearly noteled with dimension & colour stripe
2ad78320-4cb3-5901-92f0-c892f31b6323 | note | Joints, fittings and connections match design
a11bbdac-1ff1-596b-bc5c-afead65bcbf8 | note | Alignment and position are as drawn
f3f04f6e-58d9-5ae9-9fda-700def06be8c | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
ee5d422c-7206-5d82-88c8-270f26c86a2b | note | INSPECTOR / APPROVER: Foreman. Geschke
ec8eaf13-8217-560f-810f-f655b7928ef8 | note | HOLD OR WITNESS POINT: Hold Point
575c72f7-ce70-467e-8429-5276ee769e1d | signoff | hold point
bfad3285-0750-4b0a-9efb-770685c1df01 | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
7e5147e5-32cf-5dbb-9cea-cb0c5279310e | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling.
93eb6271-0a23-504d-afd0-3f15f2c46047 | note | RECORDS: Standard Pressure Test Certificate QA.6
6301b6ff-17e4-5be5-bf33-81bdcd4438a1 | note | SPECIFICATION / STANDARD: Clause 2.3 of WSA 03 1999 & Clause 18.3 of WSA 03 1999
4e32a7e5-277f-547a-acff-254c71999a7e | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,700kPa pressure for two hours
0dff03c1-aaa8-538b-8366-a48c917c7e97 | note | Pipeline is flushed free of all debris
0c8ff758-4450-55e7-8efb-67ba124b0d72 | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
968bae19-5d31-5e0d-8b48-d825ecc51ce9 | note | INSPECTION / TEST PROC: Document and Review
3e5981dc-6bf6-54ee-b1dd-78aa0a71d631 | note | INSPECTOR / APPROVER: Engineer. Geschke
9a61b02a-6a85-5f8d-8473-60008a07cd4e | note | HOLD OR WITNESS POINT: Witness Point
682141e8-e173-482b-be15-b677ae23ea41 | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
b23550f6-d3d7-5f3f-915e-bc6aa657ec65 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
398e7ebf-b969-5adf-b303-cb93c5f352e9 | note | RECORDS: Photograph
b7ca6c3f-a665-5975-b6b2-f7e0bc685fd8 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
e9c11434-8b39-5948-90b0-5906edd4b238 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
d0dca575-2d15-517b-90eb-7d321466c119 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
19383a1a-4109-59e4-b521-1519a937553b | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
cf3c5a6c-7623-5990-a9f1-613bcee6c4ed | note | INSPECTION / TEST PROC: Visual Inspection
59799f1c-5a8c-5479-954f-2417bbea8ed5 | note | INSPECTOR / APPROVER: Foreman. Geschke
b487b0b8-32cd-59cc-9500-77455c0aa657 | note | HOLD OR WITNESS POINT: Witness Point
8d34705a-7da6-4446-846f-dddfc5b49f78 | checkpoint | 9. Check Completed Surface - Make Good
1ded22c1-3c39-509c-9e0a-a192006099c3 | note | STAGE / FREQUENCY: Prior to practical completion
89df9ebc-40b6-58e1-8d14-1c4291d7fcaf | note | RECORDS: 'Upon completion' Photographs
08068007-8dd4-535f-b0a3-174918963eb3 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
9d3c1db9-a3da-5c4f-a2fe-c42521240244 | note | INSPECTION / TEST PROC: Visual Inspection and Document
aad5d1d7-2826-5b1f-a058-947ea78ba68b | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
f56353be-a776-5f95-9ac4-30bad1a8a7e6 | note | HOLD OR WITNESS POINT: Hold Point
d7ee043a-4b01-4568-b088-53ecc057377d | signoff | hold point
4b7870a0-7653-4dc7-b7a5-414947bbd97d | checkpoint | 10. Obtain as built documents
1311a9ab-dec4-56bb-bf09-fb4c159233e6 | note | STAGE / FREQUENCY: Prior to practical completion
6c75a17f-9e98-5522-b29a-1a60e99a61e0 | note | RECORDS: As built documents
9b99e68f-89b3-52ad-b97e-2afbaa63305b | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
fb4c991f-c1ae-5428-8bc5-901e902e018c | note | INSPECTION / TEST PROC: Document and Review
54a14f33-0d02-5f0f-8fa9-ef18ffc990f5 | note | INSPECTOR / APPROVER: Engineer. Geschke
10b76f32-221b-59a2-8d27-19db99cb6146 | note | HOLD OR WITNESS POINT: Witness Point
b9be315a-e0d6-49c0-ad60-936d4c11d16d | checkpoint | 11. Obtain operating and maintenance manuals
02386398-cd73-55ff-824a-84df8c8ab68f | note | STAGE / FREQUENCY: Prior to practical completion
d4e618ea-90b6-573a-b073-3cdb9861b035 | note | RECORDS: Manuals
3c8d3e94-eae8-50fc-bc6e-2c4dbf39d9c6 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
dfb0e90f-e85c-5233-a369-aa91466f6b73 | note | INSPECTION / TEST PROC: Document and Review
f902bd93-44a7-5fcb-8bde-befe2e00c9fe | note | INSPECTOR / APPROVER: Engineer. Geschke
e7e719ad-aa97-5ab8-912c-f34c60b1eece | note | HOLD OR WITNESS POINT: Witness Point
ad44bfbc-2082-469c-af24-dc0344409f1b | checkpoint | 12. Obtain guarantees
1b36e2d9-e16b-5ba6-a0bd-6245dc048cf2 | note | STAGE / FREQUENCY: Prior to practical completion
a56a6aa1-56a5-58dc-88fa-2634ef8aee13 | note | RECORDS: Final commissioning checklist
c66bf771-eb7f-523c-8db4-fde4b71c92c3 | note | INSPECTION / TEST PROC: Document and Review
42dd06db-f2a1-503a-9d8d-d25c58a71ebb | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
f1fdfe79-578c-5b34-84b7-033ff09a86aa | note | HOLD OR WITNESS POINT: Witness Point
3af23212-a8cc-49bf-8082-32cb9c3c2a8b | checkpoint | 13.01. Check above ground Hydrants - Signal and Flow Test. Standard Flow Test
94bc3843-92e1-5869-abe1-c6f55c15337a | note | STAGE / FREQUENCY: Upon installation / one test per hydrant
78ba6e0c-a733-5818-bf07-3a63921a5ed8 | note | RECORDS: Standard Flow T est Certificate QA 6E
69fa951d-322e-5982-8dfa-c64f4f312e7f | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
511c5ccf-0e46-5277-b769-ea5806ddf07f | note | ACCEPTANCE CRITERIA: Hydrant flows up to 30l/s
ad478455-d5f4-58c5-87d1-45a09f3722fe | note | Hydrant tagged and signed
c3e4b603-5a87-57cb-984a-54802ab9ba67 | note | Bollards installed
c9c8502f-88ee-5e5a-90b0-dbab31f52277 | note | Signal sent to Building Sub FIP
822189c6-2058-5859-888a-257d84f80b76 | note | INSPECTION / TEST PROC: Visual Inspection and Document
37802a26-2bad-5e7f-a18b-88aadbeb7d26 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
dd5d0e83-93ed-5646-9c92-ecff89113fa2 | note | HOLD OR WITNESS POINT: Hold Point
984ff11b-1d81-447b-81a9-6979879c3dac | checkpoint | 13.02. Final commissioning & inspection & independent report
b0733e32-06ab-513d-a451-41d2f3294b8b | note | STAGE / FREQUENCY: Prior to practical completion
ff9cbd79-cd0f-5819-b308-6c27a4565eb7 | note | RECORDS: Final commissioning checklist Independent Report
ee2a2cce-623b-59cc-9925-855b81dae58c | note | INSPECTION / TEST PROC: Document and Review
82013259-a59a-5d07-a8c9-4690908eb58b | note | INSPECTOR / APPROVER: Independent Engineer. Geschke
d61b9c12-cd13-5b0e-976b-111ef50d5461 | note | HOLD OR WITNESS POINT: Witness Point
0d19c5ee-67aa-4328-91cb-5f2fd90565a9 | checklist | ITP - Gas Sample Excl. Backfill ACOR Review |  | ITP - Gas Sample Excl. Backfill ACOR Review
6a8de6ca-e4f5-486f-8857-2a1865b06d99 | checkpoint | 1. Approve specialist subcontractor
582c8bd9-54d8-5535-924f-8a83269e7c9e | note | STAGE / FREQUENCY: Prior to awarding subcontract
57a7ece3-e973-573e-b092-33214319fb76 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
73a7d7a1-4ae5-522a-ba16-62f64c962de2 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
c37cc367-6d83-5942-89e7-7316f089c4ca | note | INSPECTION / TEST PROC: Document
5b03d59c-3b68-5ffb-9b06-0da75be7a1da | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
1b9d0c7b-041f-515e-8237-23521345eae2 | note | HOLD OR WITNESS POINT: Hold Point
9bbfbeee-0280-4af3-a8f4-0bc4d5187c15 | signoff | hold point
4d0fecbd-a670-4a8e-b887-dddadd0b9d1a | checkpoint | 2. Approve Samples
c1b62248-1348-516b-a389-0f7caad532dd | note | STAGE / FREQUENCY: Prior to ordering materials
763c51fd-9f12-556d-bf4b-2979b26a1434 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
4f7a65f4-4742-579e-a9c7-ed0eb4f1a97f | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
0828ac7b-8438-54c8-93d2-19725b5f0639 | note | INSPECTION / TEST PROC: Document and Review
efa8e912-c24f-5600-9bac-2effc803c267 | note | INSPECTOR / APPROVER: Engineer. Geschke
1f945784-0d24-53a7-a4c9-35641556d904 | note | HOLD OR WITNESS POINT: Witness Point
15c462f7-b15a-4e24-9a73-236f5dcbe20b | checkpoint | 3. Approve technical details
6e2571d1-dad5-5d71-8807-c4e252492311 | note | STAGE / FREQUENCY: Prior to ordering equipment
918662e2-8ab0-52df-a42f-68e8da168faf | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
f25747a3-3ef8-5e1c-a97e-f2615e2e8439 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
6a8b2a4d-11ce-5886-8d6e-59682fd1a761 | note | INSPECTION / TEST PROC: Document and Review
9574420f-914d-5ff6-bc30-0b7ba7d414d2 | note | INSPECTOR / APPROVER: Engineer. Geschke
baad3268-4868-529c-a8e8-55fbeaf7ce43 | note | HOLD OR WITNESS POINT: Witness Point
91cc9eff-132c-472f-b580-105f48054be5 | checkpoint | 4. Approve shop drawings
102e8ef9-5d00-5819-9317-8e25a2e84af0 | note | STAGE / FREQUENCY: Prior to commencement
10ab87ce-6b12-5352-bfbc-0e4477cc62de | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
bc053cd2-5d40-559a-9d45-88a487c2abe0 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
ec691f6a-931f-539e-9cf3-a1806c346f48 | note | INSPECTION / TEST PROC: Document and Review
ba9ccafc-a988-50d7-8ccb-3db7b4c93319 | note | INSPECTOR / APPROVER: Engineer. Geschke
4d900bf8-635b-589f-8ab9-af70cc6613ed | note | HOLD OR WITNESS POINT: Witness Point
079a9746-3259-40ad-97ea-5da6f0cbd22f | checkpoint | 4.01. Approve shop drawings
ce83f0a8-8c57-5661-9717-016155b650d2 | note | STAGE / FREQUENCY: Prior to commencement
c6985732-c75f-552a-80b1-eee5f5c446f4 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
84883510-cec9-559d-9161-cf23475fbcdd | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
175d58b0-cb2a-5295-b196-9a7d6be35696 | note | INSPECTION / TEST PROC: Document and Review
71ae6b6d-6e62-5270-9f21-f8ea7c6bbcd2 | note | INSPECTOR / APPROVER: Engineer. Geschke
93ac2ecd-78cc-55c1-828c-173ea6cf5f23 | note | HOLD OR WITNESS POINT: Witness Point
5648dda1-bb18-4b3a-a6a5-28b4595741fd | checkpoint | 4.02. Approve Method of Work Plan
9aa0213d-b1f7-594f-b487-e1057ddc9e7c | note | STAGE / FREQUENCY: Prior to commencement
497aaa9d-3b43-50c3-9ce3-34194cee74f6 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.26.10
1b294e5f-393e-5547-9f9b-0e78f25aab47 | note | ACCEPTANCE CRITERIA: Construction staging plan to execute the works
6001fb28-1c1e-51d9-9956-324583f40b4c | note | Pipeline construction schedule
33d6ceed-2e6c-593c-8990-94288d8a9d4f | note | Nominate temporary supply
28e94d65-abb0-5079-ad79-3d378b6cd9a5 | note | Nominate safe work measures
15ffe744-205b-52da-9cec-2323bd417abc | note | Nominate notification procedures
383fd1e6-8a65-5bd8-8a1b-36e6ec342511 | note | INSPECTION / TEST PROC: Document and Review
1edbf24d-e369-5258-b8e6-9958e22b5c66 | note | INSPECTOR / APPROVER: Engineer. Geschke
8ce6893b-c07b-5b5f-806f-cba498297d56 | note | HOLD OR WITNESS POINT: Witness Point
b68d78f2-835e-4710-919e-1c3445110d8a | checkpoint | 5.01. Check set out of excavations
2a67f57d-b20f-5664-8c78-fce2996843fe | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
ac1d0510-5c42-51bb-b324-63a46dd58d58 | note | RECORDS: 'Before' Photographs
1ad48627-f2da-5d79-ad1f-0328ad6bb6dc | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
c2232a65-30c4-50d7-8c05-395abc1b7ae5 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
055a3507-e81f-56d7-bf8c-c4ed7f2caad8 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
847dfcf5-b29f-5295-b2dc-8f68c9ac3c91 | note | INSPECTION / TEST PROC: Visual Inspection and Document
f8a741c5-ea57-55c5-8b75-0e301c117ebe | note | INSPECTOR / APPROVER: Foreman. LLB
44b5938c-be7e-51c3-abf1-80d957f3e9e9 | note | HOLD OR WITNESS POINT: Witness Point
f3c17c6c-f16e-4655-85f9-46864831c5a7 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
6f81fbe4-597a-5100-a5a7-abab3f3165ff | note | STAGE / FREQUENCY: Prior to commencement / each TMP
395e4ac4-e3f4-5dfd-8278-47fb9d7076fc | note | RECORDS: Copy of Consent and Traffic Management Plan
7b5bf04e-8ead-524c-a5bb-84e128f44e68 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
896cf5b7-5908-5bd7-ae55-a5091468622f | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
bf937f4f-4d9a-5464-954b-dab53bd1e3a7 | note | INSPECTION / TEST PROC: Document and Review
fa36c507-307a-59bd-b337-110aa599ef02 | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
65fe6fd9-1212-5d67-ba47-386d7aea5974 | note | HOLD OR WITNESS POINT: Hold Point
49c01dfa-d1a8-4975-b45a-5048bdd2b719 | signoff | hold point
b527abf8-d856-4344-b80d-7931b147b39d | checkpoint | 6. Check deliveries of materials
84241270-fa13-5c82-b5fd-f2a4d86583d8 | note | STAGE / FREQUENCY: Each delivery
ca7a7172-2537-59dc-9247-a03347de61fe | note | RECORDS: Delivery dockets name, signed and dated by Geschke
f9b14a6e-c619-5eb2-bbe6-2a1be74aac8f | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
0d3b4b6b-5354-54d1-945d-934ee67bf2b9 | note | Grade or class matches design
b697baba-386b-583b-898b-27b9f5cf2978 | note | Size and thickness matches design
ffdc6c27-bd22-5a90-bd20-6e747e571417 | note | Supplied items are free of defect
47f180cd-d32a-5d84-b672-32ccef31ac81 | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
b61417aa-1c3b-5233-8af9-be3e9d770802 | note | INSPECTION / TEST PROC: Visual Inspection and Document
bc70d237-e719-540f-8e8e-dadef8313549 | note | INSPECTOR / APPROVER: Foreman. Geschke
437e2a88-02c2-5169-af55-37ee019f3b4a | note | HOLD OR WITNESS POINT: Witness Point
64db8973-8146-4cc7-b1e8-6827b957a566 | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
607f0a59-eab8-5545-a4ef-62446a7c2db7 | tickbox | Standard Bead Profile Test
865631de-7f0f-5561-b17d-7d1a3d041467 | tickbox | Standard Destructive Tensile Test
0860cd18-c753-538b-b477-24b3dc9d096c | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
002413e2-929d-5dbd-b174-43bc144c2dfe | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
748a5a6a-1ccc-5163-88e4-ed34f60091c3 | tickbox | Gasketing Record
242d6ee7-78a0-554f-b464-1965a073d30b | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
a27e49d4-0cfd-5817-bf07-f2a8167fc3f7 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
832af922-adc4-5522-9b6b-e6929971cd7b | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
78bc270f-ff81-52b0-8ff1-5ac50b09e8cf | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
0bdc5207-8175-587b-85ba-12365ce3c67b | note | Bead size to be uniform, symmetrical and free of contamination and air.
69a3716a-673e-54d3-a754-2fbc15ff8afd | note | Bolt tightening to be completed using the correct sequence
b55e5578-262a-53a7-ac74-2ee6d0b778f4 | note | Final torque on bolts shall not exceed manufacture specification.
9d10029b-3177-50c2-8b7b-6095dabf69d1 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
b343a55f-940f-53d7-9fa5-8994142bca70 | note | INSPECTION / TEST PROC: Document and Review
1f85d8d8-c801-5000-bbe5-410ac0deefc8 | note | INSPECTOR / APPROVER: Engineer. Geschke
6a15a59f-bb22-576b-9529-0fabcb19a815 | note | HOLD OR WITNESS POINT: Witness Point
651d1782-b12f-4139-b291-e1c1548e9504 | checkpoint | 7.02. Check below ground pipework - pipes and fittings
e4a97931-a35a-57cb-9ecd-ff8166362c15 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
5ff6dc96-aa1d-581f-a163-6bb937bd03cf | note | RECORDS: 'During' Photographs & As-built Survey
62a6d3eb-18d0-53d8-9fa8-36b3c5acb355 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
36e34890-3031-5408-9478-7192a7712595 | note | ACCEPTANCE CRITERIA: Service type clearly noteled with dimension & colour stripe
a1d2822e-1b42-593f-a0f1-07971da08d7b | note | Joints, fittings and connections match design
8c3d959a-8918-5953-a1a5-0e5a2f5500a5 | note | Alignment and position are as drawn
4f4c562f-b7c3-5409-bda6-741e439d889c | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
4e0c7592-80be-52d7-89be-cdadf9a9bede | note | INSPECTOR / APPROVER: Foreman. Geschke
23eb0b9c-4bf8-5249-bdf7-76a5376fdef5 | note | HOLD OR WITNESS POINT: Hold Point
100bb959-3472-4b83-abad-6d17c2a3d304 | signoff | hold point
f87e5fce-e062-46d8-93a6-c4e183b3b10d | checkpoint | 7.03. Check below ground pipework - Air pressure testing & swabbing. Standard Air Pressure T est
77056855-d0a8-5f4e-b807-a24dec5dc640 | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling / one test every 750 lm each pipeline
52272c28-7b95-51e3-98ff-5cca0f28313b | note | RECORDS: Standard Pressure T est Certificate QA.6
b2be56ba-731f-5143-8a6e-50518659d18d | note | SPECIFICATION / STANDARD: AS 5601 ACOR Consultants Civil Specification Section 6.26.8
3c1e7644-2052-5be1-9415-a981d677be6a | note | ACCEPTANCE CRITERIA: Pipeline and joints are airtight under the greater of 7 kPa pressure or 1.5 times the working pressure for 5 mins
ed5fe3b4-1cc5-5f86-9593-96c1eb882998 | note | Pipeline is flushed free of all debris
f8ea7f5d-c660-5003-b901-213db84ddd42 | note | INSPECTION / TEST PROC: Document and Review
2cfeb517-a9a1-5e9d-968f-b726ff5144a3 | note | INSPECTOR / APPROVER: Engineer. Geschke
3d36dfc9-3252-5df8-afb1-ac72e8b75df1 | note | HOLD OR WITNESS POINT: Witness Point
622bdc4a-e21d-4df4-aa6e-be4591b9b9a1 | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
fb3cc2a3-412a-59b9-a978-6891e804c763 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
63e6d205-4146-5dcc-b6a7-fab8e0a70140 | note | RECORDS: Photograph
29a19bcf-3368-50f6-8896-b079acc5ed7f | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
9af017fa-8662-5846-83c5-e422f5d365e3 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
b138f356-57a7-59f4-a30a-d166d0d2e1cf | note | Thickness of surrounding aggregate shall meet or exceed specified depth
71732125-8026-52ce-b148-9b38df978725 | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
9458c738-6a86-50a2-b01a-356e50523244 | note | INSPECTION / TEST PROC: Visual Inspection
6f96de05-4864-564e-ab35-09b10be5d0f6 | note | INSPECTOR / APPROVER: Foreman. Geschke
0480f5cb-9e1f-588c-b9db-4b578e365f60 | note | HOLD OR WITNESS POINT: Witness Point
0c8ca000-2b4f-460e-badc-e39db6d8d3c1 | checkpoint | 9. Check Completed Surface - Make Good
dcf14f4d-2472-5685-8c4d-ca7311a5041b | note | STAGE / FREQUENCY: Prior to practical completion
6f57775b-4c30-59b3-8aa1-a5da6a635905 | note | RECORDS: 'Upon completion' Photographs
4c9b865a-9aab-5723-a25a-33657ecea387 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
9d1cc5ca-b87a-55cf-a3ab-75a0e0e0f55e | note | INSPECTION / TEST PROC: Visual Inspection and Document
3a574589-c684-5e14-8389-82d061859e59 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
c27b90e0-5b6f-5c15-9e7c-f3b9f948e346 | note | HOLD OR WITNESS POINT: Hold Point
cc92bc84-d5b4-4dd1-91dc-9035c7da93d4 | signoff | hold point
ecf06600-3a65-48d5-8e63-359513d21d8c | checkpoint | 10. Obtain as built documents
82d36261-e1db-5184-97f6-cd2c9b8ca8d1 | note | STAGE / FREQUENCY: Prior to practical completion
d9ad6836-801b-5f4c-a637-a5a60846e943 | note | RECORDS: As built documents
a4b0d005-497e-592f-86b9-33dbe8613c9e | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
0232008c-ec42-5def-af9a-7a2bd89f3eda | note | INSPECTION / TEST PROC: Document and Review
622b2b01-89fc-59d9-a836-e7aa7fa36c4c | note | INSPECTOR / APPROVER: Engineer. Geschke
b1c6dfcc-02d5-5ba3-893e-ee87ee778664 | note | HOLD OR WITNESS POINT: Witness Point
8a9b3a60-ad20-4a21-9531-e05f88ea718d | checkpoint | 11. Obtain Regulatory Authorities certificates and approvals
86127c5c-0048-5106-b213-6c2800eb8d0f | note | STAGE / FREQUENCY: Prior to practical completion
ff7c0b5c-538c-5d35-8d31-d3e3fd24e5b4 | note | RECORDS: Certificates; Written approvals
fbc9f03f-8b9d-5040-a4b5-b8becb81bc97 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
2a231050-3126-5f03-a049-f7be9623de40 | note | INSPECTION / TEST PROC: Document and Review
526a8715-93e3-5dae-8211-8bf075a400fa | note | INSPECTOR / APPROVER: Independent Authority. LLB
c38491ef-e5aa-515a-a211-79b605927aa9 | note | HOLD OR WITNESS POINT: Hold Point
29809ef8-ea13-42e0-a72e-d896149c2914 | signoff | hold point
6984b13f-fa2e-4a89-bfa2-4391a12d0d48 | checkpoint | 12. Obtain operating and maintenance manuals
08e1251b-537b-5ec4-b452-79b8c4807994 | note | STAGE / FREQUENCY: Prior to practical completion
fb65ad16-ae3e-5b79-83af-0f0e7479206e | note | RECORDS: Manuals
8937254d-2b21-59be-861c-096518a706a2 | note | INSPECTION / TEST PROC: Document and Review
8e3391fe-4005-5648-b5e2-141174e8bcaf | note | INSPECTOR / APPROVER: Engineer. Geschke
4d1800b7-c384-53ee-9df1-ff2d33cb936f | note | HOLD OR WITNESS POINT: Witness Point
8f1f1ba8-98de-4e84-9d0f-1391f6403f89 | checkpoint | 13. Obtain guarantees
986f7165-56fd-50e0-9243-884aa4450797 | note | STAGE / FREQUENCY: Prior to practical completion
67c37cd9-e408-5b87-82e0-4d73ee98a841 | note | RECORDS: Final commissioning checklist
3c0ea951-3d2b-5a88-a778-da84ce07e50c | note | INSPECTION / TEST PROC: Document and Review
68ae247b-24df-500f-9c15-177688d72495 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
fec90823-f956-5ac3-97ca-0b0c2df83320 | note | HOLD OR WITNESS POINT: Witness Point
59869a37-9247-40a8-bc84-e34bd13b8576 | checkpoint | 14. Final commissioning & inspection
c8661b7e-2e24-5e32-b711-a277e6c656bc | note | STAGE / FREQUENCY: Prior to practical completion
bd48c732-5a67-5fa0-89dc-698799ddff1e | note | RECORDS: Final commissioning checklist
1b66a935-a38e-529d-9e3d-6d1c9e91c796 | note | INSPECTION / TEST PROC: Document and Review
3dc67594-12b0-5865-b65c-dbfc5204262c | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
8ac757ce-8341-531f-a3f9-20931b119755 | note | HOLD OR WITNESS POINT: Witness Point
8d58ab83-cc84-4c18-b385-6319b7c3a360 | checklist | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review |  | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review
ff0a6efa-555c-4abf-8a21-a65c3db922d9 | checkpoint | 1. Approve specialist subcontractor
7f8da416-0f26-5d3b-99b2-16c951363f10 | note | STAGE / FREQUENCY: Prior to awarding subcontract
2a00375f-0a3c-5e26-8a83-93e36b5d67d7 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
f9395f07-4f28-5844-97ea-b5d5a586bca3 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
bfb32cab-7cbe-569b-b0c8-fe40e3246d4e | note | INSPECTION / TEST PROC: Document
69662e54-aa84-5dd9-a80c-ace6d80ae8ec | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
d5a81958-f124-58d8-b3bb-aee3cf9f1c38 | note | HOLD OR WITNESS POINT: Hold Point
87e000e0-625c-4f6f-8b83-02d035392611 | signoff | hold point
92e91fbf-2fc4-482b-aa4b-88654a0e88d7 | checkpoint | 2. Approve Samples
46aa3013-c22a-53fb-93f6-100115772d7d | note | STAGE / FREQUENCY: Prior to ordering materials
13ec8825-e6d9-54c3-8092-c5a7ddc4a991 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
869962e4-841d-53cb-9bc0-7aa6b0b04dd2 | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
64f9699c-9cb6-547d-8b6e-ac7e5a1f0b8b | note | INSPECTION / TEST PROC: Document and Review
b7f6992a-eea9-577a-8449-a511d33bc840 | note | INSPECTOR / APPROVER: Engineer. Geschke
ff059f24-3eca-5fcb-b3f6-455f2c13c6a8 | note | HOLD OR WITNESS POINT: Witness Point
71e7e8cb-4bd3-4edf-b40a-abc84d5d572f | checkpoint | 3. Approve technical details
b4bfb9d4-16fe-503e-8507-9445bd746f53 | note | STAGE / FREQUENCY: Prior to ordering equipment
62a2fa40-a706-5123-87f5-a2440a83348d | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
0a8bdc25-0f5e-5bcb-ba61-e525deaa5fa5 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
2615c5fd-79c5-5eff-be41-0ab08e068387 | note | INSPECTION / TEST PROC: Document and Review
63597746-483a-5f55-9325-5e1b9395a700 | note | INSPECTOR / APPROVER: Engineer. Geschke
af82714a-f11e-5ed0-969d-2b3cffad2cc5 | note | HOLD OR WITNESS POINT: Witness Point
7d3d88df-e431-4fa0-b8f8-0e4c9502b84b | checkpoint | 4. Approve shop drawings
f9a32580-242e-5abe-8b33-272ee071a6a5 | note | STAGE / FREQUENCY: Prior to commencement
dc42d10c-ebcd-50ed-90fe-e0d3eb009f70 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
5540521f-2e23-5cf0-a686-cc1714778a4c | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
49b59ecc-4390-54f8-831c-893bac092db8 | note | INSPECTION / TEST PROC: Document and Review
19be7b74-d077-5567-8427-b941e6874029 | note | INSPECTOR / APPROVER: Engineer. Geschke
84d08887-061b-568e-b5e7-e58c76e32731 | note | HOLD OR WITNESS POINT: Witness Point
60e56446-e8e4-4112-b647-2c93b069d042 | checkpoint | 5.01. Check set out of excavations
8e7e58b5-24f9-5c49-a5a1-0bec04bcd235 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
90f85230-161f-58bf-9856-df875397ea4d | note | RECORDS: 'Before' Photographs
0ef9056b-a5e5-55bf-80e3-417835ec3e71 | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
df0e960a-c096-5fc9-8aae-b18a019471ef | note | Minimum falls
30db4470-ff5f-5389-93bb-eaaed7aaaab6 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
a25f46e8-0bef-5661-a04d-85a19aae1051 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
6a2c7661-4ab4-55d8-b6dd-d80d6b227e28 | note | INSPECTION / TEST PROC: Visual Inspection and Document
3fae3fe9-7619-58fc-8959-f09f626d6533 | note | INSPECTOR / APPROVER: Foreman. LLB
34a68ae2-6580-5e54-b656-622b73ffa382 | note | HOLD OR WITNESS POINT: Witness Point
322f838c-bd87-4da7-9480-31745e01d421 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
e67875ad-b3da-573d-aa72-e786b573c627 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
35a7fd49-e142-583a-b59d-8b3fdadd2ab3 | note | RECORDS: Copy of Consent and Traffic Management Plan
785b5f0b-5de5-5f52-83d7-5c8de9537cdf | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
d8d4c15f-aaf8-5a9e-9239-eba1426ec8fd | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
e4da6318-8d9e-5e4b-a578-3046271d3d51 | note | INSPECTION / TEST PROC: Document and Review
237ca6a0-b563-5f0e-ad94-b682b2b804ea | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
773e53c5-d83e-5ae0-9dda-6f3146106013 | note | HOLD OR WITNESS POINT: Hold Point
aeeb7936-fa9a-4950-a8b8-734b117700b1 | signoff | hold point
13fc3ecc-7dbc-42f8-b9ba-98ffb93f7f3b | checkpoint | 6. Check deliveries of materials
276bf23c-2fb9-5004-8f41-f4b1e952df80 | note | STAGE / FREQUENCY: Each delivery
8ed01d3a-3d49-5526-9fa7-09a50ba68740 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
452c48d9-1ee6-59cc-835f-b7cfa6c8987c | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
f040b8f7-447d-504e-ba95-87624749f880 | note | Grade or class matches design
141d82c6-eace-55c5-8bfe-f3d9926b7abd | note | Size and thickness matches design
f027a82f-0ed4-5858-8926-b5b13c5c7797 | note | Supplied items are free of defect
6e3cf3d6-46bc-5567-b72a-31eebf4cc455 | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
755d2ad7-8d86-5c03-b3d0-12d84b33e8cc | note | INSPECTION / TEST PROC: Visual Inspection and Document
aed30d27-fc58-5d70-b8bf-c0ad4c93d3d0 | note | INSPECTOR / APPROVER: Foreman. Geschke
5d760f62-696a-5ccb-8d57-81a26bb016c3 | note | HOLD OR WITNESS POINT: Witness Point
d236527e-05b3-405d-8ab1-e1516c0a02d6 | checkpoint | 7.01. Check below ground pipework - pipe welds. Standard Bead Profile Test Standard Destructive Tensile Test Standard Ovality Test
3cabaff6-77b1-578a-902a-16c275a2b7be | note | STAGE / FREQUENCY: Upon installation but prior to backfilling 1 test per 50 pipeline welds approx.1000 l.m
e2f4f5f9-ccee-5816-8a55-033a3f85c4a2 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Standard Ovality Certificate Standard Bead Profile T est Certificate Standard Destructive Tensile Test Certificate
e87f13cf-aa1c-5cba-8da3-bfd29c52f4b0 | note | SPECIFICATION / STANDARD: ISO 13953 ASTM F2620- 20 ASTM F2928 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
9a50f317-35f2-5f7b-bd59-e7d94cd1b15e | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
2c4d13af-83ce-566b-9668-71b22224f07a | note | Bead size to be uniform, symmetrical and free of contamination and air.
d3b519c5-a4db-53e5-8cd7-4902ba29cc85 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
dcab9b94-a361-50e8-962f-11409b066ce1 | note | INSPECTION / TEST PROC: Document and Review
4c32b94a-6f10-5b61-8c8b-95e18125312d | note | INSPECTOR / APPROVER: Engineer. Geschke
05169298-38ee-52ae-8519-266c136e2bd4 | note | HOLD OR WITNESS POINT: Witness Point
bfe14ecf-17d9-439d-9627-f4afb3596bf1 | checkpoint | 7.02. Check below ground pipework - pipes and fittings
c36abac8-339d-54e7-a60a-930cfe306b31 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
ecaed5ef-f4cb-5479-9446-4680e8e8b70c | note | RECORDS: 'During' Photographs & As-built Survey
751445ad-d8e1-579a-bccb-efeb9c473852 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
24e3b7d6-7ad3-5591-b48c-30033862961b | note | ACCEPTANCE CRITERIA: Service type clearly noteled with dimension & colour stripe
42834314-e921-55ef-b74d-46459c759d51 | note | Joints, fittings and connections match design
925f457c-a428-5edb-b116-6f4f34ec1461 | note | Alignment and position are as drawn
c03cea82-8a22-5c75-9e38-46a5740f884c | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
aac0f9fc-5052-528b-b910-04c2fdc88db6 | note | INSPECTOR / APPROVER: Foreman. Geschke
0afdcd89-e70d-5bae-a032-c850de47b0c0 | note | HOLD OR WITNESS POINT: Hold Point
1e9675c9-d989-4f2e-97f0-4688cc311ae0 | signoff | hold point
da468a2f-85f6-4601-909e-01591bca050d | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
72da2334-c90a-58ba-a553-04c96eb54e61 | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling
f913f361-9434-5e54-8700-0b77a30f165b | note | RECORDS: Standard Pressure T est Certificate QA.6
7b7a425b-02fe-534e-8253-388591a846ac | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,500kPa pressure for two hours
d0bd1c4c-d7d9-5449-8a1d-d2c1b537a3ef | note | Pipeline is flushed free of all debris
fb238201-7268-52fa-b355-ed60da0c0cda | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
57c08f19-3bdf-5421-808d-6a17bf796656 | note | INSPECTION / TEST PROC: Document and Review
18ed41b1-6ac3-59b0-82d7-eec95beb7389 | note | INSPECTOR / APPROVER: Engineer. Geschke
c807ba72-df44-5634-9153-f8ec58cb9b86 | note | HOLD OR WITNESS POINT: Witness Point
8f77abae-cc13-45a2-9cb8-0cd3da906340 | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
d7672592-0e27-5175-9e41-872fedc32444 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
77482223-59b7-507e-aa1c-37ccfba3958d | note | RECORDS: Photograph
70b9d865-0e32-5add-85ab-cd82c367416e | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
42470844-4ca9-5702-9c37-b57adc5c1b9b | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
372b404d-db62-5cdb-aad9-80103441f34a | note | Thickness of surrounding aggregate shall meet or exceed specified depth
465e81db-9347-5398-8ef1-c9ae09a0e5d3 | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
60ed9eb8-d163-5004-b747-811356f19375 | note | INSPECTION / TEST PROC: Visual Inspection
978288d0-dea9-5929-a11a-cc66f3e24b86 | note | INSPECTOR / APPROVER: Foreman. Geschke
91dee2dc-09f9-58db-8b64-0dce9088c395 | note | HOLD OR WITNESS POINT: Witness Point
81d6ecd9-0b77-4898-b8a8-1804faa63733 | checkpoint | 9. Check Completed Surface - Make Good
dbbda4b1-d634-5a8a-94d5-513ee46f56b5 | note | STAGE / FREQUENCY: Prior to practical completion
2ac18627-a0b7-53bd-b485-9b25a6c731b8 | note | RECORDS: 'Upon completion' Photographs
449521d9-0a90-524c-b143-4c5f2427bb57 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
f6b5a35b-9ea4-587c-ab2f-51355abbf4fa | note | INSPECTION / TEST PROC: Visual Inspection and Document
7689ecbb-1ec2-5f44-9b4f-7d3271364efd | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
c571f609-8bd2-5bb9-9b37-9081d1ac1c79 | note | HOLD OR WITNESS POINT: Hold Point
ff159489-f765-4a82-89cc-4e859eb43c5d | signoff | hold point
30a06265-d270-488f-b877-1a88831c7530 | checkpoint | 10. Obtain as built documents
7b43c6d7-e3c3-59d4-b808-895382626938 | note | STAGE / FREQUENCY: Prior to practical completion
da1837e8-70fd-518e-b59b-ef39b0782a6e | note | RECORDS: As built documents
3acd500a-a2f6-5fc9-9871-793f02e78e04 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
1cc8fb36-a46b-5fce-959d-77c0d2a7343c | note | INSPECTION / TEST PROC: Document and Review
78197737-f4c6-5935-98cc-f29b89e1ed75 | note | INSPECTOR / APPROVER: Engineer. Geschke
9ebc8207-f43c-5c33-87c3-8e166a5fbc3f | note | HOLD OR WITNESS POINT: Witness Point
c8866ec5-5b03-49ea-b8e1-23756d12e31c | checkpoint | 11. Obtain Regulatory Authorities certificates and approvals
26bbe107-904e-5906-b8ca-7aa2182ecf50 | note | STAGE / FREQUENCY: Prior to practical completion
35651a87-a416-5841-ac61-360f1557570e | note | RECORDS: Certificates; Written approvals
b13f1ace-9dfc-5c99-89a4-a86ea409f290 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
be0f5ab0-d22b-5395-b6fa-497711ea062e | note | INSPECTION / TEST PROC: Document and Review
7eb7af23-15ec-5542-99dc-d0a072d54c89 | note | INSPECTOR / APPROVER: Independent Authority. LLB
e43750e9-3b95-5895-bcd6-d5a8b86e27f1 | note | HOLD OR WITNESS POINT: Hold Point
4abf5cda-63f5-4a4c-8a97-838a934a758d | signoff | hold point
ba8dd1a6-4a31-413c-a114-e1a6815e1d5f | checkpoint | 12. Obtain operating and maintenance manuals
a3d93b52-bb6d-52a7-a8d8-f2d1868b4ccf | note | STAGE / FREQUENCY: Prior to practical completion
b6fafade-2c64-5255-bf69-a14211445520 | note | RECORDS: Manuals
ae4034c9-e0b2-59aa-a94c-a15cd9773809 | note | INSPECTION / TEST PROC: Document and Review
0378d2ec-cd89-570d-9c94-8a2e49b49292 | note | INSPECTOR / APPROVER: Engineer. Geschke
7451d322-835c-5127-8407-0a6528356ebe | note | HOLD OR WITNESS POINT: Witness Point
2dd3df2f-ba5c-4948-9d71-209018270cef | checkpoint | 13. Obtain guarantees
b8d4af24-6be0-5668-a057-f7336e3cd9bb | note | STAGE / FREQUENCY: Prior to practical completion
df61d6e1-23a2-51e0-8767-041af5b7a28d | note | RECORDS: Final commissioning checklist
f5aee836-4d23-574c-b00b-520903eb0ba1 | note | INSPECTION / TEST PROC: Document and Review
e74e84d1-5725-5ef5-96ca-adbd80583fc3 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
0f733363-b2aa-556a-94c3-cc627cfc4389 | note | HOLD OR WITNESS POINT: Witness Point
bc2b3207-1b01-49a4-8e3a-f49d614c1546 | checkpoint | 14. Final commissioning & inspection
4a887076-691e-574d-9409-bac769400067 | note | STAGE / FREQUENCY: Prior to practical completion
197b5497-b8e5-5342-b90b-91eb137110b4 | note | RECORDS: Final commissioning checklist
a5fdebb4-abfc-5636-919f-09d29bba97c6 | note | INSPECTION / TEST PROC: Document and Review
b9aca811-f73a-5823-ab89-0a27d0aee55a | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
18e95a2a-b3ca-528f-8703-6b5b13ef8f19 | note | HOLD OR WITNESS POINT: Witness Point
5c659fe9-12d3-47b3-9b01-c190c1cca0b0 | checklist | ITP - Storm Water Sample Excl. Backfill |  | ITP - Storm Water Sample Excl. Backfill
b4e95aaa-fe50-474f-993b-321215cd9e1c | checkpoint | 1. Approve specialist subcontractor
d08c55c2-2281-5ee4-8a2c-f9d5081744f8 | note | STAGE / FREQUENCY: Prior to awarding subcontract
6d57bc85-fe86-5b3e-948b-772914662241 | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
51c360ba-c6ca-56c1-b30b-19d2c3b0dacf | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
3cda3c8c-5395-5128-ac0e-8cd3ff9e7a5b | note | INSPECTION / TEST PROC: Document
46e9461c-4226-5735-bee5-97275b90f937 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
bd3182a0-d968-5911-8068-7e9ced2b6562 | note | HOLD OR WITNESS POINT: Hold Point
1c68adf9-ffd1-4ec1-873e-06851c77793c | signoff | hold point
e069c81e-303a-453a-9064-88a36cb8d793 | checkpoint | 2. Approve Samples
ff088368-b45b-5dfa-97c0-16a6e9b77b67 | note | STAGE / FREQUENCY: Prior to ordering materials
1f2cd547-3be4-516e-9bc7-a39330375ed8 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
13f7ae05-0bcc-59c6-aaab-68e6bfa0474b | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
62df83dc-75b9-5329-9633-c011a000941f | note | INSPECTION / TEST PROC: Document and Review
2c83e5bf-3e25-5373-8e11-52eddd8a3b23 | note | INSPECTOR / APPROVER: Engineer. Geschke
f8c67a54-991a-5ded-acc2-9f920dbcab1d | note | HOLD OR WITNESS POINT: Witness Point
37e31463-a214-48eb-b1b1-69c4df78e59f | checkpoint | 3. Approve technical details
b81282fc-6c9c-5517-ac2d-51e242f59629 | note | STAGE / FREQUENCY: Prior to ordering equipment
4f7f9372-206b-5f87-94b8-9d75318278b7 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
0acfcb8c-7e21-5122-8735-269676c309f9 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
a00f4423-2a9c-50c3-84a9-a20df1b03768 | note | INSPECTION / TEST PROC: Document and Review
665dac7f-7d2b-5321-b24a-1e9328303d24 | note | INSPECTOR / APPROVER: Engineer. Geschke
ec7e2ce5-1d5d-5318-b7ff-87590d497b17 | note | HOLD OR WITNESS POINT: Witness Point
066bb5a8-eb46-430f-af60-c5610469a54e | checkpoint | 4. Approve shop drawings
5275f4a0-a8a6-53c7-922e-198e420cf347 | note | STAGE / FREQUENCY: Prior to commencement
c31d7cd4-788f-56f9-b5ab-9d871faff830 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
c476e1c5-bbd8-5eb4-9edd-19a61d4a7ad1 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
6f00824f-a982-51ac-b3e0-e2ad7faa4bf3 | note | INSPECTION / TEST PROC: Document and Review
28a993fa-a9bf-5087-93f8-6209101de09c | note | INSPECTOR / APPROVER: Engineer. Geschke
0018addc-5faa-5d65-9e11-a46edfd4a478 | note | HOLD OR WITNESS POINT: Witness Point
2d71b319-29ad-47a4-a885-d39ee50e1284 | checkpoint | 5.01 . Check set out. By Delta
92b0c45a-fb29-530d-a5e8-be2d4dcfdf36 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
f0877561-9330-51be-a885-359779a35243 | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
4ca26de9-4003-5389-93cf-6d8497f20983 | note | Height control point is marked within 40m of works area.
05642f63-d05b-54e4-befc-48f5424958f4 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
22f30997-1151-57ca-8ebb-2eac718a6d42 | note | INSPECTION / TEST PROC: Visual Inspection and Document
b5260a09-a277-5db6-967e-dfed66a461ca | note | INSPECTOR / APPROVER: Foreman. Delta
af06d731-2286-5b5c-ac36-af592023dd7b | note | HOLD OR WITNESS POINT: Witness Point
d7291ad5-68f3-47ae-a194-32c860cd6d85 | checkpoint | 5.02. Check excavations
5c676ad2-6a92-5aef-a6fd-de915c78e0de | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
cc405134-1caa-5e36-8c5d-40b243c3ddcd | note | RECORDS: 'Before' Photographs
d75787d9-f750-5e06-82c6-144a39c1a503 | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
85c5fa02-4c40-5cb1-ab6c-94f1f58eab39 | note | Minimum falls
92d5d946-ba22-5fdc-9560-d2ed7c8d4a6f | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
912cbeb4-9695-5bef-853b-8e04d075988e | note | INSPECTION / TEST PROC: Visual Inspection and Document
415ba818-4c20-541a-bd19-9d2657f44252 | note | INSPECTOR / APPROVER: Foreman. LLB
eeccaa51-a872-5a35-89f6-7e70b32c6ba8 | note | HOLD OR WITNESS POINT: Witness Point
a253fe7d-087e-472d-8c3a-f27639e26373 | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
59f98b64-13aa-5098-ba34-8cfa5b278556 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
e38b96fb-dce2-52da-b7d9-213b00284385 | note | RECORDS: Copy of Consent and Traffic Management Plan
5690e8c8-3b16-5055-964a-0060bbb461cc | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
906a5612-47ed-54c6-86d0-626710b6679f | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
4813bcbe-0c19-5bed-a322-9915c95c043d | note | INSPECTION / TEST PROC: Document and Review
9244b37d-18d7-5775-a149-e204886c4b6b | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
6c201f37-9483-51e9-aedc-a85c4fc4f487 | note | HOLD OR WITNESS POINT: Hold Point
b5c00e68-9831-42e0-b059-0349ea944eb1 | signoff | hold point
e464cb8c-9c81-428b-a5da-1c91e64e8234 | checkpoint | 6. Check deliveries of materials
8c6fa7e1-8703-57ed-a2c5-e11805d10bb3 | note | STAGE / FREQUENCY: Each delivery
510c5e5a-1645-54d0-b5b5-d91939c73312 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
bbea6e1a-3478-5540-a1b2-9f316cb45a0d | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
f05fcf0c-87f4-533c-ba93-b1c76259cdc2 | note | Grade or class matches design
0cfafd74-5b25-5312-a61b-a71f4daac770 | note | Size and thickness matches design
46f7a62c-3a01-56f6-be74-4c9b520e6e48 | note | Supplied items are free of defect
f467b2f2-45e3-57ac-bd9c-3b2432d3906b | note | Marking, packaging and preservation is fit for storage / construction
e996730c-d614-58b1-83d7-a2a5ee4ef0ac | note | INSPECTION / TEST PROC: Visual Inspection and Document
84215ffe-8bad-5ab9-a3f7-158667c98647 | note | INSPECTOR / APPROVER: Foreman. Geschke
f2574d9e-6b93-5751-94ab-c1a00c0cff67 | note | HOLD OR WITNESS POINT: Witness Point
9f7f6f45-3d64-42d7-9e07-b97f1ad73859 | checkpoint | 7.01. Check below ground pipework - rubber ring joints
11402ed3-e7fc-5831-972d-ef9fd2a040de | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / one test each grid
96a51a04-5656-5ad3-9139-13c991ff5e02 | note | ACCEPTANCE CRITERIA: Joints are secure and flexible
eab8cc6d-0a99-556d-8dcd-380778d2d9a0 | note | INSPECTION / TEST PROC: Visual Inspection
1b4e3f7e-0367-52d6-ba21-6092c46236e3 | note | INSPECTOR / APPROVER: Foreman. Geschke
b6a12e83-28e3-552d-b665-315852a6c787 | note | HOLD OR WITNESS POINT: Witness Point
90da98f8-e023-47ad-a5de-b911ec84a7b9 | checkpoint | 7.02. Check below ground pipework - pipes and fittings. By Delta
e5b1e15d-fcfe-5424-b6b6-2f5f6ed1481f | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / once per grid
024b9df5-254a-5f72-b3e8-7e71450a8621 | note | RECORDS: 'During' Photographs by Delta & As- built Survey by Delta
80e84622-1609-54a7-9660-0546b8df2ba5 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
4ce4f9a4-c7cf-5eca-9ed4-eadd1eb64e56 | note | ACCEPTANCE CRITERIA: Service type clearly noteled with dimension & colour stripe
6c6f4f36-e215-5c39-8763-e8ecbec96943 | note | Joints, fittings and connections match design
fc62c27f-97cb-5937-b2d6-2e471d53586a | note | Alignment and position are as drawn
c99e4f24-6997-586b-b707-82c49b66b394 | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
233b4650-548a-586b-8c71-ddb2b2989b9a | note | INSPECTOR / APPROVER: Foreman. Delta
8301edd5-2e90-5258-bdd9-025920727976 | note | HOLD OR WITNESS POINT: Hold Point
e99fa220-9a8b-411a-b8e9-604e6d1e7605 | signoff | Hold Point
a9b72a9b-fa40-40a3-90b8-4f09876d96f5 | checkpoint | 7.03. Check below ground pipework - bedding, haunching, surrounding and encasing
06fd23ab-6d19-5856-b419-a9df98e1563c | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
fe731fcc-5bed-5811-aa6c-fdedcd46c7f3 | note | RECORDS: Photograph
f89708fd-4196-53e1-820c-07adb3df88db | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
a4ee8813-c0f4-5fe1-a253-169ee945b0e4 | note | ACCEPTANCE CRITERIA: Constructed using approved material
f62189a3-b5cc-54a9-ba5c-2abaff117de0 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
6e57679e-dc28-5cfb-bf03-20189f48db8a | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
84c9c00b-be13-5407-8e70-fe5bc6439d13 | note | INSPECTION / TEST PROC: Visual Inspection
f50d0c67-0e6a-5264-9e14-3d62a0a4b487 | note | INSPECTOR / APPROVER: Foreman. Geschke
8117b94f-f331-544c-84bc-89218f1808da | note | HOLD OR WITNESS POINT: Witness Point
0a431e07-93c8-4509-90ec-e977307349ce | checkpoint | 9. Check Finished Surface - Make Good. By Delta
af91f354-2591-5a1d-b5b8-abbb426683d9 | note | STAGE / FREQUENCY: Prior to practical completion
72a578e4-6dfd-5528-90de-7abbe3293bb4 | note | RECORDS: 'Upon completion' Photographs by Delta
6fb181cb-5218-58d7-b0f1-d7fc42f77555 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.18.5.12
0178fff6-8385-5731-8a0f-ab2c3b8d565d | note | ACCEPTANCE CRITERIA: If works are in existing roadways, paving or asphalt has been replaced.
2b173fd9-add4-567a-9511-71bcb180b598 | note | Finished surface is free of obstruction/debris and matches finis
e0662b31-e7ff-50d3-808b-936e4939b621 | note | INSPECTION / TEST PROC: Visual Inspection and Document
f6fd962d-198e-5070-a0a7-22d81d564d84 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Delta
9614139d-a40d-5e4a-a454-016acae7a510 | note | HOLD OR WITNESS POINT: Hold Point
39ecd226-5b73-494f-8e27-20cd6a71180c | signoff | hold point
c0a3a838-e9fb-41db-a1ce-b3c5ac0f7a42 | checkpoint | 10. Obtain as built documents. By Delta
b2fb8501-b87d-5dd6-a4ff-cedbc33710b7 | note | STAGE / FREQUENCY: Prior to practical completion
42e33232-4651-582a-a7d3-6d311849a486 | note | RECORDS: As built documents by Delta
74870c71-1581-5151-9082-622f75fae80d | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
f1ae501a-0218-547c-a454-ffe723fb30bb | note | INSPECTION / TEST PROC: Document and Review
e7e515e4-e02e-534f-95e6-db76f5dc97de | note | INSPECTOR / APPROVER: Engineer. Delta
16dd1412-26a2-5453-82c1-17a30b59a353 | note | HOLD OR WITNESS POINT: Witness Point
446fd25f-e6f5-49b1-ab11-baba2f0687de | checkpoint | 11. Obtain operating and maintenance manuals
4862a367-c365-5808-b879-1b27af08e3a3 | note | STAGE / FREQUENCY: Prior to practical completion
a668b95f-af64-5f5d-8ec4-5367f42552c3 | note | RECORDS: Manuals
546e967a-571c-5808-9887-83164b63255f | note | INSPECTION / TEST PROC: Document and Review
074d8ef7-651b-5e83-881b-2666f220e5a1 | note | INSPECTOR / APPROVER: Engineer. Geschke
6926b766-107d-5b5d-9d75-782a6cd1ea8d | note | HOLD OR WITNESS POINT: Witness Point
33593a7a-ed08-44ae-b113-999e7c13120b | checkpoint | 12. Obtain Guarantees
d4edb8f1-367d-5abc-9cb3-025acda83bc9 | note | STAGE / FREQUENCY: Prior to practical completion
1bdda352-a014-5afc-a39e-bdccc3afc80e | note | RECORDS: Written guarantees
41d76f58-5be9-57ae-a5ec-bab740932ff9 | note | INSPECTION / TEST PROC: Document and Review
c4dc0443-d1d0-524c-9f11-9e269b2994c0 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
403f28cd-3f1d-5325-b3a0-881e582200aa | note | HOLD OR WITNESS POINT: Witness Point
e647c56b-8a67-49d9-a073-d6b9591701ab | checkpoint | 13. Final commissioning & inspection
66012c4d-55d9-52e5-8d16-6a5529fd2b10 | note | STAGE / FREQUENCY: Prior to practical completion
f5d884a6-bcff-5a99-a427-ecf1701e89fb | note | RECORDS: Final commissioning checklist
f5e3eed4-0063-5edc-8394-b97e559569f9 | note | INSPECTION / TEST PROC: Document and Review
3ddd71d0-7614-5201-8ba8-9477e8a07581 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
e5c5e48e-d671-5839-947a-4b188e4f1b94 | note | HOLD OR WITNESS POINT: Witness Point
7bbb5f27-36ad-4e31-9258-a3cc21952973 | checklist | ITP - Subsoil Sample |  | ITP - Subsoil Sample
6f143ce1-e449-4108-bf48-23e55b9865f9 | checkpoint | 1. Approve specialist subcontractor
7f40d82c-3e40-54c4-8798-9cafa10d3293 | note | STAGE / FREQUENCY: Prior to awarding subcontract
2002115a-7fff-5d6d-959e-677eb4bbc6bd | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
142d6cbc-35be-5fd4-8681-72a221731d0c | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
137ac898-9f9d-5cb5-84b8-61357073b07e | note | INSPECTION / TEST PROC: Document
d3ae4c69-0828-516e-905e-3ca57749286a | note | INSPECTOR / APPROVER:Subcontractors Authorised Representative. Geschke
ddd9b49e-9949-50ef-8973-1499977a1db1 | note | HOLD OR WITNESS POINT: Hold Point
26d69a48-1fd3-425a-ba54-ec9093d1f84f | signoff | hold point
01e9eef2-ce6e-4d15-96ca-568fac853460 | checkpoint | 2. Approve Samples
1cf88905-8a35-5318-b0b5-50dcaba0109b | note | STAGE / FREQUENCY: Prior to ordering materials
fd7defde-f2c6-5609-bcaa-825f1fc6facc | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
82e186c6-50a3-5df6-863e-44ba9fe160e0 | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
03658fde-751b-5036-afa8-c6d77df907d7 | note | INSPECTION / TEST PROC: Document and Review
cd061f8f-5ccc-52ae-ad52-63fcaf3e8289 | note | INSPECTOR / APPROVER: Engineer. Geschke
0a1fd2ff-18d9-5428-b863-67d03571aae0 | note | HOLD OR WITNESS POINT: Witness Point
b8c02f08-bee6-4693-9da8-60b281d14a6f | checkpoint | 3. Approve technical details
924dbd2a-483b-59a7-85f1-c6acd4d1831f | note | STAGE / FREQUENCY: Prior to ordering equipment
d5e85c7b-4c5e-5e2a-8518-bd8655140b69 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
637ccbb0-d528-5b03-8f51-2e2b6f15fdb2 | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
137092cf-bc6c-55c1-880c-389c49d0b387 | note | INSPECTION / TEST PROC: Document and Review
760ebb23-654a-570a-ad4a-2ca89e991e16 | note | INSPECTOR / APPROVER: Engineer. Geschke
782b4440-f371-56b4-ad38-b7e11ca11f0c | note | HOLD OR WITNESS POINT: Witness Point
6954d1fa-7662-435c-95fb-0dd0b2a31ca1 | checkpoint | 4. Approve shop drawings
62abeaa1-d99d-5e26-b3db-b880855a5913 | note | STAGE / FREQUENCY: Prior to commencement
2cfe41de-8c5b-5e01-896c-9bf74fa590ac | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
c647786c-2234-555e-aabc-93faaacbe6b2 | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
d8211c3a-2865-55db-a0ff-8902a2245a34 | note | INSPECTION / TEST PROC: Document and Review
ec48c81b-48df-524b-addb-1148490424f2 | note | INSPECTOR / APPROVER: Engineer. Geschke
42b6375c-05a7-5096-8b65-46f0e0db4b9d | note | HOLD OR WITNESS POINT: Witness Point
a2e9b315-3b41-41fd-a8b9-30a00314b1de | checkpoint | 5.01. Check set out - Works by Delta
902346ac-b038-5f84-a82a-4436537afda7 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
7571184e-36c8-53ed-a6cc-239151f7d5af | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
bd0b1da2-cc91-5d9e-b8bd-f52dc01ca5f5 | note | Height control point is marked within 40m of works area.
decc4db0-a0ef-5332-af6e-5cfc5f014e6c | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
33d6ba44-14a7-59e2-8423-de95c1aa0ed9 | note | INSPECTION / TEST PROC: Visual Inspection and Document
cc9efad5-0a74-500d-a791-61fbfcc78b83 | note | INSPECTOR / APPROVER: Foreman. Delta
e18e5702-e810-5587-a563-536a816abe69 | note | HOLD OR WITNESS POINT: Witness Point
7568562f-b92c-41e9-a624-0ddad551fc5d | checkpoint | 5.02. Check excavations
703919e6-76d8-57ef-86ef-c52478e4bd6a | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
6f8b79a7-6329-58b9-8a55-20bb514dbaf2 | note | RECORDS: 'Before' Photographs
c837e861-9354-542c-9259-c7de886ab096 | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
d7e5eaf6-f3f5-5568-a71b-db82c5d856e9 | note | Minimum falls
88cc5094-634a-5e92-8793-799baeae7564 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
5a9799a0-16cf-518e-95da-b3b4c4797207 | note | INSPECTION / TEST PROC: Visual Inspection
c1b880de-6464-5372-abf6-ca3382fe72f2 | note | INSPECTOR / APPROVER: Foreman. LLB
c3345b7d-2f66-575d-9dfa-eb61d10a8e69 | note | HOLD OR WITNESS POINT: Witness Point
c1ea06c9-bb1f-4325-9cdf-26d7766e554b | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
2a80b81c-374d-59e9-87c2-9e2dd6bac592 | note | STAGE / FREQUENCY: Prior to commencement / Each TMP
b3027f66-8e6e-56fc-b57c-2985b12413d1 | note | RECORDS: Copy of Consent and Traffic Management Plan
b4e86f85-4df7-5d12-a052-016a47d91269 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
f1167f4b-0dc8-5df9-b4bd-200db9deb3a0 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
ac7c8abd-d1b2-5c13-a6a5-15a456a3d787 | note | INSPECTION / TEST PROC: Document and Review
f99835cc-981f-5141-994d-ddabe9fce19c | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
9d4a284b-4371-5ccd-9abe-5a39837e68aa | note | HOLD OR WITNESS POINT: Hold Point
55636ef9-71bf-4883-9def-073c2578f9be | signoff | hold point
67a57ec4-efcc-4347-bc0e-7fb0dadd391f | checkpoint | 6. Check deliveries of materials
0f68b220-d7cb-56af-a343-843ade690aa9 | note | STAGE / FREQUENCY: Each delivery
ded67dd3-2527-5ed2-a111-ddbbae72e88c | note | RECORDS: Delivery dockets name, signed and dated by Geschke
d898eb69-b9b0-5d4c-b194-d0ed0360c9a7 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
bcacc7d4-391a-5859-8a8d-7ebe4146bddf | note | Grade or class matches design
5b120a19-f087-549b-913d-016b856e9743 | note | Size and thickness matches design
c3780468-4cfe-5259-ac34-26be69af7b8d | note | Supplied items are free of defect
86ad1eb3-0ad8-563a-89da-2da84f4890a1 | note | Marking, packaging and preservation is fit for storage / construction.
0e7eb905-f741-5199-b6e0-2581c119cd10 | note | INSPECTION / TEST PROC: Visual Inspection and Document
489b58b8-cfa7-5862-83fa-2dc52f4a7b90 | note | INSPECTOR / APPROVER: Foreman. Geschke
ba953d4c-033d-5ab8-85a9-1b0c0aed0dc2 | note | HOLD OR WITNESS POINT: Witness Point
f475ef05-f997-49bd-8d7c-a1f1bae910d1 | checkpoint | 7.01. Check below ground pipework - pipes and fittings
b967fec6-c0f8-56da-b1ab-7518e10d315c | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
cec6f855-26b4-5f92-b523-7aa26738eca6 | note | RECORDS: 'During' Photographs & As-built Survey by Delta
0082cd80-955d-517e-ad72-402df914b4c5 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
cd5d01f8-b9e5-527a-ae6d-54ef3a12417e | note | ACCEPTANCE CRITERIA: Joints, fittings and connections match design
4b702fc3-c311-568d-8af7-a4e9ae9378ba | note | Alignment and position are as drawn
bef1e0aa-a804-5ec3-ac9b-a54de145201b | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
f65751fa-dce4-5bc0-a905-4e89aa6ec13f | note | INSPECTOR / APPROVER: Foreman. Geschke
4e61b6aa-2e86-5e27-b4a0-8bd774f67563 | note | HOLD OR WITNESS POINT: Hold Point
0e787bb3-d861-445c-a83d-f835d8a153ba | signoff | hold point
9e298bba-efa3-47d7-8d39-49def8ff4a70 | checkpoint | 7.02. Check below ground pipework - high ends and flushing points
7d51d3a6-ac2d-5eaf-b822-2e10b9587d00 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
6350429d-ce4f-5c79-8d43-5ec39729f8bd | note | ACCEPTANCE CRITERIA: Capped at surface level with hinged lid, cast iron box in concrete surround 300 x 300 x 150mm
76524131-8232-506c-bb68-29a264bb48df | note | INSPECTION / TEST PROC: Visual Inspection
3a059269-c3f5-5b15-bb38-18ee3f50920c | note | INSPECTOR / APPROVER: Foreman. Geschke
036efaa3-69dd-5d35-9fae-7bd27d9fafd4 | note | HOLD OR WITNESS POINT: Hold Point
49597f1a-a221-4bb0-9ab3-32ce0fe16ef6 | signoff | hold point
e2bf6507-abfc-4e36-b751-97853530e7a3 | checkpoint | 7.03. Check below ground pipework - haunching, surrounding and encasing
721afc9a-5438-5e21-99f6-cb7e3162f421 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
984de5ac-659e-5509-a756-1c88c473f284 | note | RECORDS: Photograph
fdeae07e-2d40-5d74-be76-9335ee21927a | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.19.3
21c44133-5489-5ab4-8944-c687acdfd127 | note | ACCEPTANCE CRITERIA: Free draining granular material
1567fb94-e405-51c3-98d9-c22ce47c09c4 | note | All faces of filter material in contact with topsoil or similar shall be covered in geotextile
a77851f0-6bf6-5732-ae80-2e8552addc3f | note | Material used is as specified and approved.
3edf6baf-7eb6-54f0-b091-e627d5eee55b | note | INSPECTION / TEST PROC: Visual Inspection
afab5c18-441f-59bf-a84d-db4b67972c76 | note | INSPECTOR / APPROVER: Foreman. Geschke
955a2e0a-cd70-51f1-a0a1-4bfa0f177369 | note | HOLD OR WITNESS POINT: Witness Point
c646b40d-0e12-4585-8569-f61de904781a | checkpoint | 8. Check Completed Surface - Make Good
22c2a77e-7e25-56a3-a451-b8b36fa6cffe | note | STAGE / FREQUENCY: Prior to practical completion
dfecab82-2ed6-53dd-8005-599c8aa9c5ae | note | RECORDS: 'Upon completion' Photographs
d2ef0827-babf-5750-9ab6-4db3936cfdc7 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework less depth of works by others
0377a4cd-21ac-5241-96c6-33ec1da10d5d | note | INSPECTION / TEST PROC: Visual Inspection and Document
ae496b77-adda-5afe-a622-2e79c31665fa | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
8f4916c1-bcf3-558f-a5d9-190c7eb719b9 | note | HOLD OR WITNESS POINT:
9f24d7f5-332d-5c56-ba65-5bb7e92ea2d4 | note | HOLD OR WITNESS POINT: Hold Point
6b604a93-eb4b-4101-a388-93eeba9c4474 | signoff | hold point
cc9a16fa-1e6e-4ab4-bbe7-7537c9fba268 | checkpoint | 9. Obtain 'as built' documents - Works by Delta
13d26541-7cff-57c8-bac5-6aa06c853446 | note | STAGE / FREQUENCY: Prior to practical completion
52362203-4f1d-5167-8a89-d74e009e1016 | note | RECORDS: As built documents by Delta
a254e23b-4e6b-56a4-b0bc-2b712f6f2599 | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
4fefd207-1e5f-531d-b5f1-c20e76a58923 | note | INSPECTION / TEST PROC: Document and Review
5634394e-360e-5c8c-abbc-79330ef5f3f2 | note | INSPECTOR / APPROVER: Engineer. Delta
c0c32f98-959d-5600-b354-2421a177a228 | note | HOLD OR WITNESS POINT: Witness Point
55b387b3-2cbe-4912-9125-5470dd1feca9 | checkpoint | 10. Obtain operating and maintenance manuals
0a459c7c-bc7f-512a-9ad3-85eb5578042a | note | STAGE / FREQUENCY: Prior to practical completion
5fdef146-f018-5304-bfef-a377b4321b90 | note | RECORDS: Manuals
c891ccec-f7e3-54f4-ad65-06151f9d7d43 | note | INSPECTION / TEST PROC: Document and Review
aca54e25-7028-505c-8138-ce1fe397cbf1 | note | INSPECTOR / APPROVER: Engineer. Geschke
7bcae0b8-3a01-54c9-a028-316a41f3b255 | note | HOLD OR WITNESS POINT: Witness Point
b6ce98b8-67b0-49ad-953f-7dab7b835155 | checkpoint | 11. Obtain Guarantees
565b061a-fbd4-518b-b696-ef69f97a73bc | note | STAGE / FREQUENCY: Prior to practical completion
01f721a3-0d02-542b-8808-fa97a9818038 | note | RECORDS: Written guarantees
a667f732-7287-51bd-80e3-d1414f71f75a | note | INSPECTION / TEST PROC: Document and Review
279fb788-6f8d-57e0-a31b-976d765c94f3 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
8efb056b-3703-5f3c-aa1a-a77600dd0050 | note | HOLD OR WITNESS POINT: Witness Point
01ce0825-0468-4895-acc9-6f67d07eb954 | checkpoint | 12. Final commissioning & inspection
215bf5c9-d20b-5433-8feb-15cc796e296e | note | STAGE / FREQUENCY: Prior to practical completion
7f1ad25e-a3a4-5e84-bab9-9bac495d5a21 | note | RECORDS: Final commissioning checklist
31c50d84-55ee-5f17-83fa-2a95b0fbdf04 | note | INSPECTION / TEST PROC: Document and Review
cbde2192-4ef3-55fd-be83-d2007f95c9ab | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
1de55b1c-3f28-54fc-8686-3681edfb9774 | note | HOLD OR WITNESS POINT: Witness Point
f11bfc53-1a04-425c-92bc-df747118bda1 | checklist | ITP Trench Compaction - Various Services |  | ITP Trench Compaction - Various Services
b7835681-6582-4f55-8421-87aaea2cd71f | checkpoint | 8.01 - To assist with the requirements of not only test results but ensure supervision to assess the competency of the construction methods a Level 1 GITA tester will be on hand to express an opinion on the compliance of the work practices. Geschke Plumbing are to compact in 150mm layers with Trench Pad Foot Roller.
36bd27f6-51dd-577c-8087-09cb1d685f86 | note | STAGE / FREQUENCY: During compaction
250a72e4-61fb-5d78-9753-73ec903eb03f | note | RECORDS: Written document by Level 1 GITA tester. Geschke mark-up of backfill type, test & observation location by grid
4b69c7ed-9068-5c4b-b287-eb84a85401ec | note | SPECIFICATION / STANDARD: AS 3798-2007
7b601018-d96f-5fa0-8886-add047341cd0 | note | ACCEPTANCE CRITERIA: Geschke are to compact in 150mm layers with Trench Pad Foot Roller
dd50edb2-6749-5cdf-af32-1f9fea6a96e8 | note | INSPECTION / TEST PROC: Audit Activity
d9f813a0-302b-5aee-8b9a-31bfa9296574 | note | INSPECTOR / APPROVER: Geotechnical Testing Authority. Geschke
18c7aa48-3aeb-5646-a5e4-ffd719cb6b17 | note | HOLD OR WITNESS POINT: Witness Point
b0e45574-4c74-4705-9d4a-7bfba763a240 | checkpoint | 8.02 - If Stab Sand is required for back fill this will be delivered 5% stab sand as per approved material. 5% stab sand on 100 slump poured straight from the shoot
30c68986-0cd6-52ca-b58d-c41ac3f09a47 | note | STAGE / FREQUENCY: Prior to installation / Each pour.
5f718c64-a900-52ef-b429-f6f012c12ff6 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
7bd7f5ee-c2f9-5f54-a1a5-bdeb6ef6faa7 | note | ACCEPTANCE CRITERIA: Stabilised sand mix meets 100 slump direct from concrete truck shoot
a3118061-738d-5795-9a62-1c5d33032d99 | note | INSPECTION / TEST PROC: Document and Review
f2ce388d-b94b-5d59-adff-0ca048ee6d0f | note | INSPECTOR / APPROVER: Foreman. Geschke.
f6b0f781-12ec-575e-ac39-bf66b9aa0172 | note | HOLD OR WITNESS POINT: Witness Point
9c21416b-f854-4faf-979f-6a455167d95a | checkpoint | 8.03 - Testing to be completed in backfilled zones with 1 test through 2 layers every 40 linear meters. We will test our trenching through 2 layers at finished height less topsoil depth. This test will be completed approx. every 40 linear meters.
657551e2-1d1f-5af2-8546-e6a8a45531b3 | note | STAGE / FREQUENCY: Prior to completion / one test every 40 linear meters
0861e73a-d0e0-5770-8f3f-b1969ad3b8de | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
35b7979b-1c72-541b-bc66-173db9972063 | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
3f34b15d-100a-5294-b186-a3f64b2b5402 | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivalent density of existing ground found adjacent to the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
c44287b0-2329-5678-935f-e01a31a86c21 | note | INSPECTION / TEST PROC: Test Activity
7a036e51-f36d-59b6-bada-ea94ad8b09c7 | note | INSPECTOR / APPROVER: Foreman. Geschke
3abad011-bf59-5c30-9410-1295a5ac71fd | note | HOLD OR WITNESS POINT: Witness Point
ffe286aa-fadb-46e4-9f0d-cc89ab133f58 | checkpoint | 8.04 - Testing to be completed adjacent to work zone as required by digging back top soil layer and testing in ground. One test in existing ground adjacent to work zone through 2 layers at finished height less topsoil depth.
6a4b6559-f58a-54d2-acb9-1bc050467d38 | note | STAGE / FREQUENCY: Prior to completion / one test as required
dc50c982-4004-5ffe-8e83-7bebfe863f39 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
6f7e1c18-db60-534c-aac1-b5eeef94057e | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
8c9ef382-b1b3-58ee-9819-3e8702fbaac1 | note | INSPECTION / TEST PROC: Test Activity
7ac044af-d0f6-53e4-b789-a9fcd58391b0 | note | INSPECTOR / APPROVER: Foreman. Geschke
63cb7be9-ca77-53a0-b68c-ec50ea39b9a4 | note | HOLD OR WITNESS POINT: Witness Point
f7863cf2-9ce8-4d94-94c9-18aea9cbaa89 | checkpoint | 8.05 - Compaction Test Results. Test Results as per above test plan.
c4556137-ee6b-52d4-b5e7-197cd2bef63a | note | STAGE / FREQUENCY: Testing as per above
6d1863c8-90e0-5a34-a0c0-6012ffddcb7b | note | RECORDS: Standard HILF Test Certificate
1e3a162b-d0d7-5fcc-a4bb-80a4af8f39ac | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
c4339aad-0133-55d1-a81a-d6fc2ccc71e5 | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivariant density of existing ground found in the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
7f8f64f9-58b2-57d7-8a46-cad70e60ab96 | note | INSPECTION / TEST PROC: Document and Review
f100c3f3-6bad-530e-8a97-6e4357709bca | note | INSPECTOR / APPROVER: Foreman. Geschke.
f2541b04-4269-53a3-afbd-c14972ead4ab | note | HOLD OR WITNESS POINT: Witness Point
21ed809a-2360-418a-a43b-727a1c843e7a | checklist | Maintenance Inspection Report - |  | Maintenance Inspection Report -
f389388c-9e31-4e06-b19a-9f83f56ab32c | section | Details
6f541aa0-7c81-4543-a6d6-633b2986db44 | checkpoint | Inspection Details - Pass once entered
486d53e7-ced0-53b4-96e5-9acfda3c1a65 | textbox | Site Name
7e46a03a-3352-5c4b-9c51-2527e049986b | textbox | Date
7ae41ded-c5b3-5aa6-814f-5a81a0c76bd5 | textbox | Site Address
407d5a05-c706-5ba6-ba1d-d88af63ce8ed | textbox | Contact
5053f0a2-7b23-5054-9f99-9c99b3834d38 | textbox | Contact Phone #
0b942f64-dd50-5141-a401-f68299ec1bf7 | textbox | Inspection Task Location
f80e146f-c912-5a66-b37d-10f6fba54abe | textbox | Item/Equipment to be Inspected
d05dabb7-8dfa-4a9a-877b-1137581eea28 | section | Inspection
de33641e-0eab-40f7-bf27-a26d3460e596 | checkpoint | Does installation comply with manufacturer's instructions
19b8c2b5-6a65-4e64-afae-0f926a91e869 | checkpoint | Does the item function as it was designed to
1e47c593-f14d-4e0e-9d15-b6a7ab52a23e | checkpoint | Is there any reports from the customer of the item not working or any issues
8785c0ca-c6e2-4b37-9acf-6fc41eb87811 | checkpoint | Is the item free from damage or future damage
1167f516-841b-4e98-8a77-141f4b4a4ac3 | checkpoint | Has all parts i.e strainers, sumps and pits been cleaned
948403e3-0306-4c23-a679-634a480f8337 | checkpoint | Is there further maintenance or parts required to complete inspection
a4b21a08-53b1-48da-8384-ec1240bc13fc | checkpoint | Photo taken and uploaded to report
1762a124-1ed9-421f-a282-866ce6256d98 | checkpoint | Item left in safe working order
f5a43908-589d-45da-8e10-d16b087201fb | checkpoint | Inspection Completed
00c23f87-1d9f-5e23-b9a8-12d10d15d6e6 | textbox | Additional Comments
df410ffe-36e1-40e6-a57e-ec688387d5c6 | signoff | Click to Add Inspector's Signature
ed8de06b-b05f-4da3-a413-0160cca403f1 | checklist | Non-Conformance and Rectification Report |  | Non-Conformance and Rectification Report
f295be5f-7c1a-4819-990c-69edfdea5eb4 | checkpoint | Non-Conformance and Rectification Report Details:
2253b833-b18b-5f29-a3c3-53f7ff90f401 | textbox | Drawing No./Rev:
4809fb23-56e9-5160-b8f8-2d89e4e3d83a | textbox | Zone or Grid:
db475a31-a044-5db2-93a5-6cded3383352 | textbox | Issued To:
4bc14b38-715e-5101-bf13-23c8645234c5 | textbox | Item Not Conforming
6a791f30-bba9-5ee8-b8d0-931840bd5d8a | textbox | Reason For Non-Conformance
36e73b89-57de-5ff0-a3f0-f073b16f557b | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
703c431b-75bf-56b4-b962-da0d2222f624 | textbox | Action Required:
3f386620-edcb-5178-9d39-2eebfa449c61 | textbox | Date:
92b5045c-f088-5b82-9753-0efbd8a89ae1 | textbox | Rectification:
4bf5e342-2567-5d51-80f1-490b9f66e0ca | textbox | Date:
f592bc2f-6058-5aad-a549-2e52c92ddbcf | note | Note: Non-conformance register to be updated
9930eba6-2284-46f5-9a29-ee7dfd496a61 | checklist | Pre Cast Slab Penetration Placement Checklist |  | Pre Cast Slab Penetration Placement Checklist
31a18b5c-f7aa-4743-8135-87638985154e | checkpoint | Pre Cast Slab Penetration Placement Details:
fdfbe6bc-9b91-5766-9079-ed51c449bc29 | textbox | Drawing No. / Rev:
a3fc80ca-3a42-52c5-b52f-31ffb37595dc | textbox | Slab No.
ded8586b-cc7d-57d2-81dd-fa6b0d71ab2b | textbox | Total: Sewer - waste penetrations
64d0322e-1490-5cb5-9675-f5ea9f4754b3 | textbox | Total: Stormwater penetrations
2e29a11b-fa1a-57c9-87a0-ea478644ef44 | textbox | Total: Water
ce91ea3e-fb84-59cc-9ca9-7c3bfcea3105 | textbox | Other:
d4a6546b-e900-4f01-9c3c-40f008d5f6da | checkpoint | Geschke Representative Sign Off
7e03412d-04b3-478c-96b4-3c19cce3ca94 | signoff | Request Sign Off
8f28ab2f-655f-4e2b-b52f-02993d778d9f | checkpoint | Construction Company Representative Sign Off
d00d6107-03f5-40af-bffe-a80413d917c6 | signoff | Request Sign Off
9ac0adc5-9958-464a-8caa-fc96050aa5da | checklist | Project Photos |  | Project Photos
a261bba8-6a88-4244-8905-07a19ff33feb | checkpoint | Attach Photos and Comments
d8559d11-be68-4223-870c-e3854680efaa | checklist | QA (ITC) 8.1E; ITP A1.8 - Installation of Electrical Conduits Checklist |  | QA (ITC) 8.1E; ITP A1.8 - Installation of Electrical Conduits Checklist
310dd865-503e-44ff-9a3b-fe5622a57b72 | checkpoint | Electrical Conduits Installation Report Details:
78f5c2cf-f0cd-504c-82e0-e3fe40893705 | textbox | Spec No.:
3faa2e11-5322-5c0c-b19a-aa0c28f159dd | textbox | Drawing & Revision no.:
5c2442ed-ae5c-50a5-b33a-be1bac98ecc1 | textbox | Shop Drawings no:
c6aaf269-f785-5322-8627-99d76a2ed2ab | textbox | Zone:
c5d471ca-9ba9-5551-b382-92891478df1e | textbox | Starting IL established:
717d6346-70e1-4c70-a2d1-f698a19a640c | checkpoint | Conduits Lines
0ba9b5a4-da36-5a4c-ada1-a50fa959ec61 | textbox | Date started:
f6e97786-48e6-5e02-86a4-4fc538283379 | textbox | Conduit Line Number:
167f035f-d3c9-5638-a358-f547a53085bd | button | Bedding and Haunching | Yes,No
08b893f0-be2c-4c59-878b-316abd4e3a7b | checkpoint | Bedding material, placement and compaction meets specification.
dd052aba-af73-51f3-a95e-cac2e8b591fe | note | Spec#: Electrical Specification
cd860570-d04c-5c3a-b78d-9b700123a3f4 | textbox | Material used:
a0375530-4d53-580b-857c-194bd20a9f78 | textbox | Docket #:
a787512e-5f1f-4215-aab0-353fb8d80368 | checkpoint | Conduit Instllation Checklist
cd46f729-9f2e-5c4b-8664-27c0e7f015e3 | button | STOWE Conduit Installation Checklist is filled in and attached | Yes,No
addf45a9-d7d7-479a-9e5f-983b55a64cad | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
4cc5637d-265b-5915-8589-89721ba0b56e | button | Stowe Group Signature Sign-Off added below | Yes,No
2b0114e9-73cc-55ab-879e-3de37660c7d6 | button | Geschke Group Signature Sign-Off added below | Yes,No
f8b3ad77-7f35-5140-a75f-713c4810a1f4 | button | BESIX Watpac Representative Sign-Off added below | Yes,No
91516720-9252-5461-ba86-f4a6fe145eec | button | Seqirus Representative Sign- Off added below | Yes,No
5e7467ed-136e-4adb-a28c-2655af3e4e2a | checkpoint | Backfill
dbe3bef6-7a2b-545d-b7dd-69035322d59b | note | Spec#: Electrical Specification
1e231aa1-b32d-5228-9a42-db6f656fbe1e | textbox | Material used:
c8f8df2c-a5b2-5471-a092-02203476da6c | textbox | Docket #:
a2c01ad2-f30a-4dee-af3b-811d92e96ab9 | checkpoint | Compaction Test Report
365bd576-6a3b-5eb4-a35a-c6af8dd17e97 | textbox | Compaction Test Report No.:
76a8af70-aae3-4bf3-8870-ca3654dc43ba | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
152decfb-5997-59ee-9eec-e267ad86c271 | button | Stowe Group Signature Sign-Off added below | Yes,No
1abaf46f-6cdb-5004-825f-87a98122296c | button | Geschke Group Signature Sign-Off added below | Yes,No
b031a046-8f4f-409c-9edb-d10b902fca6b | checklist | QA (ITC) 8.1F; ITP A1.7 - Installation of Electrical Pits Checklist |  | QA (ITC) 8.1F; ITP A1.7 - Installation of Electrical Pits Checklist
753445f0-1555-40ea-90be-6d54d2a7cb87 | checkpoint | Electrical Pit Installation Report Details:
03061e96-ec29-5149-8242-5873aee96492 | textbox | Pit number:
ec7c4316-42ec-57b5-b1bf-ac60338258f6 | textbox | Spec No.: Electrical Specification
0808fd9b-ed84-5d1a-ac49-067370edaedf | textbox | Drawing & Revision no.:
47c4eef9-4b16-57ab-8902-9fc487194f9b | textbox | Shop Drawings no:
14ef1db8-3969-52f3-a1df-35c0783083aa | textbox | Zone:
3c6c0f58-045d-5855-8cea-188bb8aa793f | textbox | RL of the bottom of the pit
8f0a745b-1b9f-46e2-87f4-04ad00505fab | checkpoint | Bedding material, placement and compaction meets specification.
a387a1d5-6e42-53f2-ba5a-0f58bc2e402d | note | Spec#: Electrical Specification
02950d3f-d016-5de6-afbb-9585e3d36256 | textbox | Material used:
3dcc97b5-683d-5a20-b7d4-7de91832ce64 | textbox | Docket #:
efb83c84-6daf-4894-a5f9-97d37cf7a265 | checkpoint | Pit installation
eab38fbd-ed29-5c22-887c-e51cb6e7807a | button | Placement of cover | Yes, No
81a85053-1b0b-518c-b50b-e56c4b968fa2 | button | Concreting of cover | Yes,No
73ec575c-0e8a-418e-94f4-907ca18b6fb0 | checkpoint | Pit Installation Checklist
86c85196-7c12-582a-9a86-c282e81b3159 | button | STOWE Pit Installation Checklist is filled in and attached | Yes,No
dcbf8c22-370e-4b91-80b6-ea73425ae48b | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
96aa923f-77dc-5b73-9e91-d5b196eee11d | button | Stowe Group Signature Sign-Off added below | Yes,No
f35d3adf-d4a2-5ca2-aa97-45143d9ec8bd | button | Geschke Group Signature Sign-Off added below | Yes,No
684d6c7b-65a3-5020-8ec5-ee8172e56ccf | button | BESIX Watpac Representative Sign-Off added below | Yes,No
d2a50c6d-60d4-561e-91bf-d43a1b2be055 | button | Seqirus Representative Sign- Off added below | Yes,No
37ec1fad-5483-40b5-9986-aa5ffd08fb5c | checkpoint | Backfill
bd148706-283f-58fe-bd8a-21b6500eaeae | note | Spec#: Electrical Specification
b4efa248-f407-58c7-86cd-66c9d9db0e56 | textbox | Material used:
689a8a1c-c2d0-516f-81df-c8f1e4c34023 | textbox | Docket #:
e4b8abe1-feaf-4459-a59e-94c9e7c3b3fa | checkpoint | Compaction Test Report
7a075677-714f-5bb5-ad2b-1ed68453bd06 | textbox | Compaction Test Report No.:
2262e74a-d87a-4312-866d-2ba4cef751d4 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
f3b409fd-f51f-5818-8768-5fe07ac72c03 | button | Stowe Group Signature Sign-Off added below | Yes,No
b6ce0544-2249-5298-900c-f00e039755b7 | button | Geschke Group Signature Sign-Off added below | Yes,No
b7e3744b-9a3b-4701-b15d-72b7693bdbf5 | checklist | QA 6 - Pressure Test # |  | QA 6 - Pressure Test #
17c87af6-dd9a-488d-8244-89c68312cb65 | checkpoint | Quality Control Pressure Test Report:
cca8e140-46ce-559a-ac79-889a4a62d9ff | textbox | Drawing No.:
3cc6f0d1-c9ba-5de5-bfab-abd3f2f38584 | textbox | Rev.:
1b15667e-75a6-5786-8c88-52aae01f4eb2 | button | Test: | Air, Water
cee3a142-3d6f-5a97-b6ec-cc6bb003d05f | textbox | Section
309c7507-6571-58b9-87e4-f0acdc0dd874 | textbox | From
69d1df3f-e4b7-5726-beaa-e37581b64a11 | textbox | To
6e4d8814-f1eb-531d-9a8e-16e50792d47b | note | Specified System Working (500 kPa)
da966caf-f674-4238-ad49-0d681f0e3fcf | checkpoint | Specified System Test:
c38b3195-d8c8-572e-acc5-e1644bf11697 | textbox | Pressure (1500 kPa)
37de6b90-39dd-5355-a23f-7544cedbf91d | textbox | Duration (2 HRS)
2062c742-f209-407f-8c0d-06be48b65912 | checkpoint | 1st Reading
a696e2d0-6975-58df-b32a-6e1de8a6cdd7 | textbox | Time
e9f2926a-3378-5ca9-83e3-305fcd1f645d | textbox | KPA
5db56989-9bc4-5199-a12d-4caf7b91f87c | textbox | Ambient Temp
2bf7e6e0-efa2-470a-a073-ee38a8db5a4c | checkpoint | 2nd Reading
efd649a4-24a9-5c82-9788-681ad4fedeb5 | textbox | Time
9fafa55f-2018-51c5-b103-71c0a271019e | textbox | KPA
f7823a27-8e88-53f3-bf86-cfb65a1926b3 | textbox | Ambient Temp
c3d8eb49-faf3-4e8e-968e-e864b4219bc1 | checkpoint | Test Result - Passed?
2e4418b4-da72-5c20-bd22-b0331211fe14 | textbox | Repeat
a40a828e-fea8-5ca4-8fff-7ba3d5010eb3 | note | Company: Geschke Group
bef16e96-48c5-52ad-9be4-2f0a4ccb0f6e | note | Phone: 03 9798 1619
9271dcbe-0a57-5f4c-8417-56159d07cf1f | note | Address: 45 Pacific Drive, Keysborough
21e23b6f-a14f-5abe-945c-354a025e169f | note | Project: Centre for National Resilience Project - Melbourne
a54a29a6-9160-595b-84b3-e95a576b9479 | note | Principal: Multiplex Constructions
f3b47968-533c-4547-a182-88bac472a973 | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
97097755-2bea-5e98-ad82-b511c6d87b49 | button | Geschke Group Signature Sign-Off added below | Yes, No
0e8e1d2b-dc38-5ad3-bca4-dac7192a8f8a | button | Principal Contractor Representative Sign-Off added below | Yes, No
cf19f557-e8a8-4e7b-91c2-bd1422472def | checklist | QA 6D - Quality Control Gas Regulation Test Report |  | QA 6D - Quality Control Gas Regulation Test Report
857331f2-9143-4220-9cf2-831df7bb3567 | checkpoint | Quality Control Gas Regulation Test Report:
2a49b025-5413-55c9-8e85-74288b55657e | textbox | Drawing No.
b511dd52-30b3-5611-a341-8bb3724e74f3 | textbox | Rev:
31590836-d29c-49e3-885b-419e76a35d5f | checkpoint | Test - Flowing inlet pressure to project
8959a93d-ab7d-521a-9718-96b828e210f0 | textbox | Inlet Pipe and Size:
04daccbd-10bf-5f50-b83a-68d5527afe19 | textbox | Spring range:
222f5197-306b-5432-b4a6-66422aa55aca | textbox | Orifice Size:
05b5e148-34db-5239-a798-1bb4efeaa659 | textbox | Model:
cd69efb2-d02d-4918-8e9f-2600040bb2ec | checkpoint | Section
f0e7a549-d782-5885-883a-dca4fb083070 | textbox | Section:
8696843c-415f-5e44-af7f-9e99151d81af | textbox | Pressure (KPA)
3e69dc05-2e24-4d13-a4f1-ef9d9ee4b5f2 | checkpoint | Test upstream inlet pressure to regulation
de2547cf-d709-5a18-a38a-b69055835e03 | textbox | Pressure (KPA)
74c7193b-0469-4106-b4e9-795ea31b19ba | checkpoint | Test downstream out pressure to regulation
d6ac7654-3240-53ef-a609-ea8d42de629a | textbox | Pressure (KPA)
580a6c4c-49a6-51ce-9779-f93c569f5b3b | textbox | Duration (hrs)
b075288f-1073-4326-afb5-6840a90a159f | checkpoint | Adjust out pressure KPA as stated on GPL shop drawings
0f696c9d-f27d-5d05-8cdb-8b14069b7efb | textbox | Reading (KPA)
8a42b5e7-abf3-4d3c-b25d-1d4612471ba1 | checkpoint | Confirm outlet KPA does not fluctuate more than 0.8KPA
9ef90474-4d23-5cf8-9deb-b4ed9042bd15 | textbox | Repeat:
b7fb9781-7fdc-4251-88cb-28682d6ffcb1 | checkpoint | Sign Off
8183a425-a561-5c29-9812-e0d47a25e21f | textbox | Geschke Pty Ltd. Representative:
814fc43c-b43c-5aab-ad78-16ac43f1f29e | textbox | Others Present:
5b6d46f7-47e5-5e5a-b50f-d21ad5f72656 | textbox | Date of Satisfactory Completion:
c21d7437-a0b0-411c-b88e-750ee3c44702 | checklist | QA 8 - BGS00# |  | QA 8 - BGS00#
911731f1-af4f-4833-a65f-4c8a44e417c6 | checkpoint | Principal Contractor Permits Issued
1cf5952f-91bf-461d-86c8-2c4d70714b8a | checkpoint | Set out pits trench depths and runs.
b05458d4-c61b-5308-868d-9b8ee3873daf | textbox | Drawing & Revision # (or Attach photo below)
b073564b-e9ca-58c9-be7d-45c222611e51 | textbox | Survey setout completed by:
30e903de-02c8-5f2f-9abf-772b6981f87b | textbox | Manhole Coordinates - enter Eastings & Northings
dbe3067b-9f14-527a-a63f-d020d5dc6414 | textbox | Starting IL established - enter IL
19b1c3b1-b495-5cc9-836f-a15a1bddcd0e | button | Survey confirmed drain started at correct IL | Yes, No
d4b9a0d3-80a9-5637-94cc-28a2ad13597b | button | Drawings attached | Yes, No
82f3c7f3-66df-4920-b228-af1258846419 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
7ea5510e-23ca-5c94-b847-c28002c33857 | note | Spec#: AS3500
9d9c4ff3-7fa3-576b-9ae5-d231e5025154 | textbox | Materials used:
b9593f27-9461-50f4-81ca-8fc8969bb93e | button | Approved by Principal | Yes, No
1eeedd48-629b-45b6-b5c4-0edff6f29266 | checkpoint | Bedding material, placement and compaction meets specification.
4998a97c-babb-5e88-881d-1bcb83ef0355 | note | Spec#: AS3500
8ff4fc74-187e-54b4-ab9a-be9656e90c97 | note | 7mm Q-Minus Bedding
698729a8-5d23-42a8-a79f-15f341db1160 | checkpoint | Laying and jointing of pipes - RL and fall
8666265a-3f40-5531-8e78-47ff5fa2fb52 | button | PVC pipe with Rubber push fit jointing | Yes, No
6699f42e-2218-5571-927a-0a4aba767b48 | button | Fall achieved (1:200 required) | Yes, No
16f14cf1-2e84-4ebf-b477-7de7e7f922ce | checkpoint | Connections to pits and existing services as per spec and Australian Standards
f24ff48e-830b-4f1b-a5b3-eee554e66eb3 | checkpoint | Hydrostatic tests are carried out as required.
769b62c9-573f-51c0-90a8-e878a94d7c03 | button | Air or Water? | Water, Air
5641c8d5-f3b2-5498-adea-4148fdbffd7d | note | Inspected and recorded by Independent Certifier or PIC
27a05d1c-85ed-4887-9dc3-dffd290df8c8 | checkpoint | Mirror tests completed
69c8df13-4ae5-58c0-af92-6d45b5565061 | textbox | Independent testing company:
da1e85ef-6a49-5aa9-808e-bb5983183d37 | button | Inspection report attached | Yes, No
51cd1e15-9b02-4f51-8051-f0242dce8b8e | checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
927be1f1-dd6f-59c8-8fff-1ae589602b2e | tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
2941b78f-7319-5f84-b66e-5ee136a46436 | tickbox | 5% Stabilised Sand
40c00e76-948a-5bab-a8e9-6f1d2796f7ca | textbox | Compaction testing completed by:
ac9314a8-6fdc-557a-af2d-4be45b7b165c | button | Compaction report attached | Yes, No
732d27c4-db0a-4978-84d8-b743f41cb877 | checkpoint | Temporary cover provided to open drain.
6848947f-a0a5-4489-8731-487672d0a0b2 | checkpoint | PVC/ Plastic caps to open ends
85597613-94ea-4881-8445-acff6e5328ae | checkpoint | As built information updated onto drawings
8446662c-1739-5820-aa0e-d60c4ca6fe06 | button | Drain installed as per nominated drawing | Yes, No
4da05414-dcc6-5a2b-bd1c-cd650b6dcc80 | button | Invert levels checked by independent surveyor | Yes, No
c7280496-f30b-5472-ab55-900c26729391 | note | As Built drawings to be updated as required
39e5b030-3b05-41e2-b487-fdf5dc48ac3e | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
8686d9bf-1f23-5380-b00d-349cd0e69b9a | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
54b88402-a625-5cb7-84f7-472782dcf25a | note | Company: Geschke Group
1583520d-822e-5705-9e61-943447b65ef5 | note | Phone: 03 9798 1619
234c79ef-4ddd-5862-a41a-5ff45741e6f3 | note | Address: 45 Pacific Drive, Keysborough
13faeca9-ee17-5401-99c2-3787e5206faa | note | Project: Centre for National Resilience Project - Melbourne
67b2a6b3-db1a-52b9-afe7-ad7b271dde4d | note | Principal: Multiplex Constructions
515c42d5-4ac9-4d47-9b34-3f2f40f4694c | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
d2b78ad2-27a3-517d-a651-2c82da9f56f7 | button | Geschke Group Signature Sign-Off added below | Yes, No
273fb211-37d3-581d-81c5-56945dba6cdf | button | Principal Contractor Representative Sign-Off added below | Yes, No
39eb05f4-a199-4181-9311-9821c5246996 | checklist | QA 8 - W/RW/F-00# |  | QA 8 - W/RW/F-00#
caa07c3f-d355-49a6-a44f-c13e93699b53 | checkpoint | Principal Contractor Permits Issued
2c3441e5-f56a-4940-ad1d-a1e9a0f7baa3 | checkpoint | Set out of trench depths and runs
92d04ee6-046e-5726-9e9a-2eccc30971a1 | textbox | Drawing & Revision # (or Attach photo below)
27a1ddf6-b37e-5e0b-8efe-f38a44aacf14 | textbox | Survey setout completed by
e3159bcc-973a-5aef-bb18-e0e72b6b491c | button | Drawings attached | Yes, No
8e051956-bc0e-4668-94ed-325ce71bff56 | checkpoint | Pipes and fittings comply with relevant Authority and Specification
acee7c65-acb9-58cb-a8ba-112200a3e60e | note | Spec#: AS3500
9b4cf1f1-11f4-5b70-a90d-ef76ab407e5a | textbox | Materials used
61dbd32e-30be-5ac8-88ac-8346ebc30d40 | button | Approved by Principal | Yes, No
d5c14ed8-7c7e-47d9-926e-03a0af27118c | checkpoint | Bedding placement and compaction and material meets specification
1bb22774-6e9b-5924-9483-821101d77a98 | note | Spec#: AS3500
c1361355-a534-5f1f-9dc9-71f6c3256074 | note | Packing sand encased pipe
b0e28fc5-5cf5-45b1-ae9d-49435f11e205 | checkpoint | Jointing of pipes
7a5928fb-113b-551f-8e00-1bb1f6cae660 | note | If either of below are selected, please reference the ITP/Attach below - As applicable
c67b3618-dcfe-5773-a397-40fe99ea6c2c | tickbox | Electrofusion GPL QA 16 form
612ba819-99f4-5420-b282-6b3bd13f4d3b | tickbox | Butt Welds GPL QA 25 form
50863db0-4a43-413b-9a95-d107a6cdbba5 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
7b2c1578-5344-4186-9e87-ad709f997cd2 | checkpoint | Testing of pipes are carried out as required
77c4b8cb-4de9-50c2-bcbe-50428b1eeb07 | note | If below is selected, please reference the ITP/Attach below - As applicable
51f6be1d-73a4-5379-b4f1-53e349e2f96b | tickbox | Water system hydrostatic test
b3692806-2ee7-55f1-916b-47bb35c010bf | tickbox | Fire system test completed by Independent tester
a9b856c1-dc31-445b-9141-54cc1371e368 | checkpoint | Additional service within trench
c7705b2a-c9b3-50ae-a77a-3309b8faa350 | button | Are there other services to be installed in this trench? | Yes, No
16fed4b9-68e2-5554-a8b0-9b45acea1551 | button | If Yes have these services been installed prior to backfill of trench? | Yes, No
507b2d0f-5db4-4c0d-af3c-563211b24390 | checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
09ffbb1c-cf1d-53ac-aeab-b5a3dfaec89e | tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
7e003771-8d41-5b32-8e78-53a8aa18987b | tickbox | 5% Stabilised Sand
4a31afa4-69fe-57ea-9065-be9e6f1d1603 | note | Detectable marker tape
7a86d34f-e72a-4a80-9ace-698f0ac6d061 | checkpoint | Temporary cover provided to open drain
d0b52ea1-f358-4205-b34b-9ea590f299e7 | checkpoint | PVC/ Plastic caps to open ends
0613de26-fb08-4bbf-a11c-8d0578d50854 | checkpoint | As built information updated onto drawings
abe9203e-9187-589b-a47a-6c57c3233ac3 | note | Ongoing
57261c75-3f54-560b-aac3-e55a9ab7fe41 | note | To be provided
dab6eaa7-6ba6-4be1-9bf8-be42a6d37d10 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
513bbd3f-8052-5abc-8a48-5b1fc6b8d57c | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
b0f9e3f0-5bc0-5153-8ecf-105cd0a4fa6a | note | Company: Geschke Group
01b4e8e8-95d7-5c8a-a723-42f0272c0bd3 | note | Phone: 03 9798 1619
d3769674-0295-5501-8871-3d94aaf68f34 | note | Address: 45 Pacific Drive, Keysborough
1706861a-98fd-5af9-92eb-4b07ff01a408 | note | Project: Centre for National Resilience Project - Melbourne
98194af0-8640-55d1-a216-c9e28f827749 | note | Principal: Multiplex Constructions
27329dc7-e043-4854-864c-570e5b7b3850 | checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
e04c261d-9b37-5ac3-9088-273b9f4fc736 | button | Geschke Group Supervisor Sign-Off added below | Yes, No
e39247f1-e9b5-582d-9e2e-8159dadb297f | button | Principal Contractor Representative Sign-Off added below | Yes, No
2ef517fb-c04f-4f2f-a50d-20ed7e133c0d | checklist | QA 16 - EF00# |  | QA 16 - EF00#
111dd940-a08d-4921-8a07-45fa0ab91aa1 | checkpoint | Operator Details
61123c71-c584-5a8e-acc5-817057741957 | textbox | Name
b253a4d3-7dd9-5624-82ca-9b5fd3ca90ec | textbox | ID No.
435a2765-0b30-5625-9df6-fc55e9d37c2f | textbox | Company
bce825f1-1434-5944-b93e-b93736b14651 | textbox | Address
a7ba54ac-3975-46a5-81da-1c62ca382535 | checkpoint | Welding Machine Details
fa4bff26-c90c-5e38-8266-c87b6feb1ed1 | textbox | Manufacturer
a2e5a9d9-8709-5194-8495-2bd571724d82 | textbox | Type/Model
9ab68d9a-90d6-5be7-9367-26b13bce3d6f | textbox | Serial Number
022b163d-dc77-5306-800a-a2fbb24ace5c | textbox | Year Built
87e9d867-9851-4b99-b54b-bff13787c5cf | checkpoint | Actual Pipe Size
94d04061-ea73-518a-9cca-d4a7ae8ba272 | textbox | Type
1c0ef925-6522-5abb-8817-b83d8964ff76 | textbox | Brand
0bc3f53a-72db-5161-bf68-d48aaaad8e6c | textbox | En
22103dd0-ee41-565a-878f-c1f1b0b599a6 | textbox | OD
ba725d6e-6465-5baa-9b91-1b76b2672e03 | textbox | Ovality %
5cc66dc8-7bfc-4529-8eb1-551f3d6436ee | checkpoint | Fitting Data
b8897994-9971-5651-9283-011d7d29f688 | textbox | Brand
cdde8692-b027-5570-9a07-68cc4a987a07 | textbox | Type (Coupling, Tee, Reducer etc.)
b5cc27e1-f55f-48e4-89e1-456dc8444c44 | checkpoint | Unit Setting
5f897c7a-8410-5ed0-89dc-d31bcd790b9c | textbox | Manual
92efd0f7-ad2a-5ea5-8952-c9ae49c78948 | textbox | Automatic
eb67b2b3-0d42-4f8b-9b0d-fa1793b21337 | checkpoint | Preparation
516a9c13-10fd-5b6e-b05d-6e0695f70f7a | textbox | Cleaned and Peeled
48343a1b-356d-5d44-b976-0699848579fc | textbox | Pipe/Fitting Clamped
97a4bbcc-9e6b-4bf8-872e-a746bbd74166 | checkpoint | Welding Times
28d4f15e-1171-53ba-b101-e2d025cb389c | textbox | Joining Seconds
dc06ad7e-041b-5832-a9cb-33384d3c5926 | textbox | Cooling Minutes
803fb626-0c1b-4fca-9533-e47cd90d0248 | checkpoint | Conditions
c545494a-158e-5b8e-8563-fc84420aa928 | textbox | Ambient Temp
3cf18c1c-e380-5000-8902-e1d332b421d3 | textbox | Weather
a32409d5-2001-54fd-89f0-30e0b93ebed3 | textbox | Preventive Measures
216ef4f2-b499-4ec4-aa7a-2e7c3dae574b | checkpoint | Power
caf2bd4b-eff0-5cc0-9c36-0777cf7e6306 | textbox | Mains
b0fe66e1-e808-5e9c-a55c-1f7a386fc6aa | textbox | Gen Set
281e484a-6b6a-4052-9b6a-569febca9fed | checkpoint | Operator Sign Off
eea6dc0c-ae7a-4783-b20e-789851d7aac0 | checklist | QA 16 - PE Electrofusion Welding - Field Operational Sheet |  | QA 16 - PE Electrofusion Welding - Field Operational Sheet
9787d313-9d65-4199-8e5f-2c58ef76bdcb | checkpoint | Operator Details
9af4f074-73c2-5501-b513-af3a441445f9 | textbox | Name
5ed40b1f-1f7a-5884-bfad-9d2cc5b50fb7 | textbox | ID No.
9b29ce19-dd37-547b-b8a2-62283d4c4610 | textbox | Company
c208260f-fe67-5f89-ae13-07a52ea9dcfc | textbox | Address
ea853ebc-483a-40b9-af0b-ef8fc2c1aa0d | checkpoint | Welding Machine Details
0c31befe-b71b-5fee-842c-397934a3900a | textbox | Manufacturer
9c93713e-bbaa-5d40-a9ad-0a9246ee43f4 | textbox | Type/Model
0006d0f7-08d0-5e85-b508-00cb79f2bb9c | textbox | Serial Number
b6eaa7e4-c2ea-5df9-bdf2-c0e9fa086128 | textbox | Year Built
fda28d5d-3a40-43b2-b0e1-cd628379e0b0 | checkpoint | Actual Pipe Size
67f35448-5b1d-5709-af75-716fa079dca8 | textbox | Type
cf0d9ebd-7818-56b9-a9c9-8a14e41214fd | textbox | Brand
d9b1190a-717f-5c25-8598-5d3b63bbf3da | textbox | En
04fea2c5-e300-56ca-b17b-493b1dc4aed2 | textbox | OD
df771e64-b0f8-5ba5-a475-a2ea2cef5cb7 | textbox | Ovality %
1d8a33c1-6e5b-40ce-8046-58c5ab432a3a | checkpoint | Fitting Data
d8e85233-8f47-57c3-9cce-6a53d834fea2 | textbox | Brand
5a6dbcff-b6da-5ba7-93d4-3c4c3c8f8f40 | textbox | Type (Coupling, Tee, Reducer etc.)
e9651ae7-927f-44d9-9e6d-902c390faeea | checkpoint | Unit Setting
1567dcf6-b746-5efe-b180-252ccd6bc897 | textbox | Manual
c0a22bec-7c3a-5a78-a7ae-8e6e8246e585 | textbox | Automatic
6c7e8941-a131-4eb6-b646-138da97feba2 | checkpoint | Preparation
15bed649-f288-5e68-9da9-4e36b553616e | textbox | Cleaned and Peeled
9d3c45f7-cf05-57ae-b60c-d4ae5a8706e5 | textbox | Pipe/Fitting Clamped
fe8e9c81-8333-4f20-b3d4-81cdf7b9109d | checkpoint | Welding Times
2a4ed29d-dde1-5d89-8cc9-7b405cac84a6 | textbox | Joining Seconds
508e408b-2cb1-5388-9e89-154cffaefed9 | textbox | Cooling Minutes
ca4aff4f-3556-4966-974d-ec1342c9fdc7 | checkpoint | Conditions
abc3d223-1400-53f8-a7fb-5c060864f305 | textbox | Ambient Temp
f3d04124-5d2f-5450-a3ae-3cc935e5f082 | textbox | Weather
5f3a3a01-54a4-5f03-bda1-d8d38dac240f | textbox | Preventive Measures
bc265ec4-07a9-4e9b-8e2c-98d6d419726a | checkpoint | Power
158a6e35-ba7f-5c36-b540-e9f2307f3b8b | textbox | Mains
5fd99706-72db-54ef-a028-9f5dce31c204 | textbox | Gen Set
7dcabd90-daae-454d-bfc5-2fd07daad64b | checkpoint | Operator Sign Off
f13b9df3-9eb1-4ce3-a500-a496484dd5e4 | checklist | QA 18 - Gasket Installation |  | QA 18 - Gasket Installation
0bf0cfa4-fa73-4ccf-9fae-4cff69107069 | checkpoint | Gasket Installtion:
3333e143-681e-5ad2-9ec3-d9f650816c0e | textbox | Location/Identification:
37c0dd33-e0eb-5997-acd9-cd0ef3d75788 | textbox | Nominal Bolt Size:
c4784bd0-1eaa-54e4-bd3d-db884fd1374f | textbox | Gasket Contact Surface Finish on Flange:
39f786bd-373c-52ad-8ddb-25006148c3a5 | textbox | Lubricant used:
a3d67965-27aa-5f89-a9c1-eac9777762b7 | note | 1. Galvanised nuts and bolts must use good quality lubricating oil on threads
dca54013-e76e-59f9-bfd7-abf8c2a690a0 | note | 2. Below Ground Galvanised nuts and bolts must denzo and plastic wrap full flange and cover bolts
b518d14d-e91d-5619-8a3d-1141f3fdf7b9 | note | 3. Stainless steel nuts and bolts must use anti seize / molybond on threads must return 24 hrs later to tighten in sequence and required torque
9ed7d247-569b-53d5-9a0b-ca393e286182 | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
008a0adf-9c63-5c43-8da0-ac61c84b6aec | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
731bf625-e259-5c89-811b-380281fc13ae | note | 6. Zinc bolts, nuts and washers rust when used externally use galvanised
db064acf-8bc0-4b76-8ba9-da36068a75ed | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
4feced83-b67c-4821-886d-da691a9329ad | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
06de08d9-ead5-4642-91f0-2f66c9beabd0 | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
7ca84d3a-5882-4733-88bd-0829927116df | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
49c4b6ae-972a-425d-838a-436834205644 | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier seek from GPL foreman
c28e539d-645b-4819-bd02-a6a7173f1b21 | checkpoint | Check gap for uniformity.
c398140e-72d3-45a9-8720-f1cd634d06be | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a Round)
4e2dbd95-4d94-433f-b808-6863a69b805b | checkpoint | Final Torque
7cadc442-a8d6-5506-b1f2-eb20c9487b45 | textbox | Final torque*:
57199db0-13cd-5b30-8a24-d03762277499 | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
dd2c6804-04e7-5f35-a77c-fd4f48b131ad | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
0c5aeb51-8609-5dbe-8f22-17c368183136 | textbox | Round 1 Tighten to:
69d33c7b-dd87-523e-9281-21874e557e39 | textbox | Round 2 Tighten to:
305eeff1-b0bd-59f3-b6c9-f9b611668739 | textbox | Round 3 Tighten to:
e95942ff-b571-5527-97dc-6f174091f2e9 | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
5577a61f-1d6e-58a5-afbb-9ed45f14539d | note | Final Rotational Round 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
8b69281a-368a-5434-bb16-4f24ef438d51 | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
9af4accb-e894-5ac6-883f-4e5b2c9c2d9f | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
7f28d7d9-c5a0-551b-8753-fba7a0b98ec4 | textbox | Other:
79685d05-ddeb-5a76-a3f4-9163e495b86a | textbox | Where was torque information provided from:
3c2eacec-c4a3-5d5f-bbe9-815e0b0a1251 | textbox | Joint Assembler Name:
0169ff28-45da-4730-b694-76a2beebf1f8 | signoff | Joint Assembler Signature
3c1fa4d3-4d53-41e5-9d9a-a0f8b379897a | checklist | QA 24 - Hose Reel Register |  | QA 24 - Hose Reel Register
92f1fafe-2ef8-4059-8249-030af223ac6f | checkpoint | Hose Reel Register
494f4370-ebbf-5e70-be09-b0c804124cd1 | textbox | Ref No:
33d5c3e1-af37-51cd-b06b-d92c24299202 | textbox | Building:
f52581a1-34d2-5b43-aab2-23613e9abf2c | textbox | Zone:
73a04817-7c63-5116-92bc-7a20d04f2ee5 | textbox | Level:
47c65c12-db99-516c-ba33-cc250fdd3e5f | textbox | Adjacent to:
a3833607-fece-59aa-a224-ec7b1d05d020 | textbox | Length:
a21af562-d243-5e58-986d-52ad386a5df0 | textbox | Date Tested:
95bc5eef-b360-5c49-8c8f-ba74fbed9581 | textbox | Flow Rate:
16ced4ec-49f3-5f43-9f88-78c813a59d27 | button | Obstructed Access | No,Yes
6a16f81c-a819-51f7-805c-46d22042335d | button | Operating instruction visible and legible | No,Yes
639389ba-1034-5692-b090-f52bad6c3f8a | button | No leaks throughout hose reel mechanism | No,Yes
2ff8f5f9-ff7b-513e-bbcf-af8dae376671 | button | Hose runs freely through guides | No,Yes
a1acb166-4846-50e9-a939-b1e1b3131b93 | button | No signs of corrosion | No,Yes
4c9d3bbc-d9c9-46ec-b127-7b17136fd5a4 | checkpoint | Result (Pass / Fail)
a3cc4dc6-0c82-4583-8517-d22afe9530d1 | checklist | QA 25 - BW00# |  | QA 25 - BW00#
107ac9c6-4169-420c-906f-6b4183abb25a | checkpoint | Operator Details - Pass once entered
7e864967-b151-5fa4-9dbc-9d35b74e92b6 | note | Supervisor sign off at completion of ITP after weld #16
ec64fe0f-412f-5492-a6c2-3be49298b3de | textbox | Name
5822afb4-30f1-54f9-8a12-1ce64b360675 | textbox | Certification Number
32e5c6c9-1df8-47ed-af45-c2a3f05a5333 | checkpoint | Welding Machine Details
48492597-fc64-5df3-95bd-92fbbb08e902 | textbox | Manufacturer
5bcff39e-37df-5e34-b447-d31066af3d2a | textbox | Type/Model
735b095a-8d45-5f4c-a536-2b7c574bb05e | textbox | Serial Number
83cc0863-e12a-5d7e-ba31-a68670b76173 | textbox | Year Built
ef31ac1c-b2ea-49f7-98b0-6396b3ee78da | checkpoint | Pipe / Material Details - Pass once entered
48f45a5d-2228-542c-a49d-47751d345bf8 | textbox | Dn (OD)
deabfd26-2459-54e9-9091-2ea5deab57b1 | textbox | SDR
061af90f-a6b2-5667-bcf7-b65dd0a78023 | textbox | En
5ee80cba-1095-53a3-b951-2a3b8f3e7002 | textbox | Type
0ebe3081-a1ee-5838-ace1-5ae2cb0c9375 | textbox | Parameter
4c65aa5c-41aa-56c4-b519-e16ebffa3c8e | textbox | SLP
5dc2e564-c906-5a90-ae23-28af77d0b9a1 | textbox | SHP
d52cf383-1ede-4318-afbb-99acd524668b | checkpoint | Weld #1
469f5e53-d959-551d-b020-ac574efd1d1f | textbox | Time
0e50e31e-e988-56a0-9d0c-fce1800f6051 | textbox | Ambient C
082b48a9-14f7-50b0-b490-fd59eb5f273c | textbox | Heater Plate °C
42cd5b66-e032-5044-b1cc-3107e2a95b40 | textbox | Drag Pressure
7d8bca1d-8b41-5b2e-888b-275627782974 | textbox | Bead Up: P1 (Kpa/Bar)
0a78d84f-6e5a-5ab6-85a2-34195e433342 | textbox | Bead Up: t1 (Evidence)
97a89d8a-fb60-506e-93ea-3e90f5c820cb | textbox | Heat Soak: P2 (Kpa/Bar)
948aeac9-6396-5075-9b5f-0c8f3696b506 | textbox | Heat Soak: t2 (Seconds)
241fb78b-6086-5ed2-97bc-d8fbcc51cfc9 | textbox | Change Over: t3 (Seconds)
97ffcf19-955d-5340-b84f-b3361c44898a | textbox | Pressure Up: t4* (Seconds)
652e4584-366d-5c00-bdb3-a97ba66e5f15 | note | *t4 not applicable for SHP situations
cf0004ef-f4d5-5bc3-9ce6-b93252367a68 | textbox | Weld and Cool: P3 (Kpa/Bar)
2f3c521f-7791-5e2a-84b4-7f1816795152 | textbox | Weld and Cool: t5 (h:m)
0a26fee2-4a4c-5ab0-9540-c4b4f79350e7 | textbox | Rough Handling: t6 (h:m)
b022dbda-49e2-5159-be62-96538470ac9d | textbox | Bead Size: Min
69d3d9f4-cbaa-58f9-a327-276972860766 | textbox | Bead Size: Max
8be924d9-c863-515d-a243-d1144e4f1b37 | textbox | Comments
b094aa03-74fd-4af6-af20-0668b6744854 | checkpoint | Weld #2
25084078-f75d-52d3-8044-5e7b536f7da3 | textbox | Time
44731c6a-c329-5f67-862b-3a784b022de6 | textbox | Ambient °C
ab7731c6-6899-5a9f-a512-aaf2fb7d7e28 | textbox | Heater Plate °C
50b36237-633a-5f1a-b43b-648899ab02ba | textbox | Drag Pressure
9addb222-5bba-5517-86bf-0bccbdd9ed01 | textbox | Bead Up: P1 (Kpa/Bar)
83fc6587-5798-539b-b7eb-59f2379ea3d2 | textbox | Bead Up: t1 (Evidence)
2cd7eea7-372a-5b50-92ee-b3683583be33 | textbox | Heat Soak: P2 (Kpa/Bar)
dcf84de6-f0f1-5d3a-b8be-86b5a2e01ad7 | textbox | Heat Soak: t2 (Seconds)
d1309e9f-3ffc-5840-ba49-37ed37223a6f | textbox | Change Over: t3 (Seconds)
16eb4e40-fb7f-5cae-9656-67b02fc600fb | textbox | Pressure Up: t4* (Seconds)
72783dd0-fe68-588d-9f22-293e480bfeab | note | *t4 not applicable for SHP situations
a756c887-ca10-5cb1-9c0d-0ceef1a0d162 | textbox | Weld and Cool: P3 (Kpa/Bar)
ecdf27b2-777f-53e4-9ec7-38845fa41705 | textbox | Weld and Cool: t5 (h:m)
5eb4f743-3ec0-5162-9969-e7872092aa68 | textbox | Rough Handling: t6 (h:m)
ec112f49-6dad-5ab3-a1bc-1a4d34634d1b | textbox | Bead Size: Min
22621b80-601e-571d-af82-decd02f08de3 | textbox | Bead Size: Max
35ec6889-6486-54c7-85ed-b13078f1867f | textbox | Comments
2386a8bd-fb94-480c-adaa-5f14863115cf | checkpoint | Weld #3
edacc9ee-e424-5f41-a607-6d4257eda6bc | textbox | Time
e6782191-1508-560b-81ae-d3800a6dde10 | textbox | Ambient °C
8f8243f4-d0b3-5609-9bec-2281edfb6387 | textbox | Heater Plate °C
fb10b458-1847-5278-b08d-65c3b21d4326 | textbox | Drag Pressure
c5e4feb3-954b-5aa0-8703-33e4adb89df0 | textbox | Bead Up: P1 (Kpa/Bar)
d5c1627a-300a-5041-8ee5-54eeb439a139 | textbox | Bead Up: t1 (Evidence)
76ecac7a-7585-59e3-95c7-4920a2277d26 | textbox | Heat Soak: P2 (Kpa/Bar)
dd4989ac-9630-5da3-908f-51bfa9a2c53f | textbox | Heat Soak: t2 (Seconds)
0abda261-24b9-55c2-ab9d-c1dbe4b5c31d | textbox | Change Over: t3 (Seconds)
3943afc5-4c7c-57e9-978c-6b7873562b75 | textbox | Pressure Up: t4* (Seconds)
269e131c-9da3-5c9b-a0a6-24a1a028d136 | note | *t4 not applicable for SHP situations
c3cfbf0d-cfca-56d7-a96d-74c253f65d81 | textbox | Weld and Cool: P3 (Kpa/Bar)
42333320-f570-5829-969e-a4eec206af8e | textbox | Weld and Cool: t5 (h:m)
0ef0e342-9144-55db-b5f5-52b532e560a8 | textbox | Rough Handling: t6 (h:m)
d627f573-acf4-5812-81b0-8d1bc5ebeac0 | textbox | Bead Size: Min
8e1f1a3b-a726-50f8-b79f-9849145c152f | textbox | Bead Size: Max
86eaef21-869b-52db-a9dc-c83da5e8ab1c | textbox | Comments
504ded67-b67d-4e3e-ac36-629843825c73 | checkpoint | Weld #4
db3f2830-2f7c-5b85-9702-0dc3348b9f2b | textbox | Time
1d6f6b77-0963-5ea7-93b2-a31da42e6e6a | textbox | Ambient °C
72b99a83-a2aa-5e78-81f4-6a1f67d2bb03 | textbox | Heater Plate °C
d1ea358e-1fdf-5064-a714-17ead9e5c57e | textbox | Drag Pressure
0de6bbab-03e1-5896-9d65-a4e5dade0b4c | textbox | Bead Up: P1 (Kpa/Bar)
f66d730c-d3ba-593b-aa60-a78296b34f9c | textbox | Bead Up: t1 (Evidence)
83764dff-d0de-5b82-8fcc-1c8e06079607 | textbox | Heat Soak: P2 (Kpa/Bar)
649f3cc5-8689-50fa-a1dc-5550ac30953a | textbox | Heat Soak: t2 (Seconds)
8177d02d-8da7-57bb-bc16-02433d172162 | textbox | Change Over: t3 (Seconds)
523fea3b-54a2-5872-8347-07b07651b3ac | textbox | Pressure Up: t4* (Seconds)
2557116d-b5ce-595a-af71-f76b6796ef60 | note | *t4 not applicable for SHP situations
33c9568b-0bf4-5795-920b-1cb020214a09 | textbox | Weld and Cool: P3 (Kpa/Bar)
061e6571-4c8c-5a82-9fc9-dcb1305c73e8 | textbox | Weld and Cool: t5 (h:m)
a52f2576-3db7-50ad-b3c4-a2bfe541bc26 | textbox | Rough Handling: t6 (h:m)
91435060-6cd1-584e-bc72-afa2818cf9e8 | textbox | Bead Size: Min
7c91dc68-e619-533c-8389-0422d285c3bf | textbox | Bead Size: Max
1d5ef320-95fb-5ac6-a7f5-c06b17a69e0c | textbox | Comments
ab346c56-eba1-4903-9cc2-db59cb0c7907 | checkpoint | Weld #5
2da708b0-e3da-5f8a-a1bf-4eb10d06911e | textbox | Time
ad01daa3-bb7e-5733-b706-3a16fae04d5b | textbox | Ambient °C
df742bab-5f4f-535a-8c85-2f1cc40b78d4 | textbox | Heater Plate °C
c216e45e-4e7c-5a06-81f6-889c339253c3 | textbox | Drag Pressure
35487985-bff5-5cc2-b776-a04066c8fc8b | textbox | Bead Up: P1 (Kpa/Bar)
d08422bd-6158-518c-9415-aa1f33580abf | textbox | Bead Up: t1 (Evidence)
0cb8f65f-38e4-5fe2-8bc9-6508f603b72b | textbox | Heat Soak: P2 (Kpa/Bar)
97bad0ca-1125-57b9-826c-8aa219bc7ad3 | textbox | Heat Soak: t2 (Seconds)
834a367b-0d4e-5359-9a1f-5a2a02b5e662 | textbox | Change Over: t3 (Seconds)
07a85ae1-ab8f-5b93-aaad-e1bc8663ee3a | textbox | Pressure Up: t4* (Seconds)
265c02a5-afba-5de0-b926-3aaa64d7a3d8 | note | *t4 not applicable for SHP situations
d96b046d-231e-5b31-bee6-d75cdac0eb7d | textbox | Weld and Cool: P3 (Kpa/Bar)
05555d42-12c4-5da4-86a6-c62e3fac114c | textbox | Weld and Cool: t5 (h:m)
e1d676fc-54ab-5213-9c6c-6725f614df13 | textbox | Rough Handling: t6 (h:m)
c5337f32-2a78-5dc4-b48a-6213b31fa229 | textbox | Bead Size: Min
e19a39aa-70a8-52bb-9036-f63df2c726c3 | textbox | Bead Size: Max
0efbc14e-afa9-5235-badc-e83671cfbf67 | textbox | Comments
970e73e8-2de8-454d-aa6f-86cc33c2bdbe | checkpoint | Weld #6
d12d45f4-f454-510e-a736-62691f9b879b | textbox | Time
6d1a4f35-14d4-5b03-b9be-8892f201c799 | textbox | Ambient °C
f916b142-2a13-5009-9ccf-244995cb866f | textbox | Heater Plate °C
675ec426-e32c-5a29-b953-00540ba91704 | textbox | Drag Pressure
f4aa4258-8881-5496-bb20-4900b4bb3625 | textbox | Bead Up: P1 (Kpa/Bar)
a35f6113-f9fc-5d60-8eaa-57000ccff1e8 | textbox | Bead Up: t1 (Evidence)
b6d00701-c3b6-57b3-a8bd-8d4139ef256e | textbox | Heat Soak: P2 (Kpa/Bar)
d6fad4e9-6b6c-54bd-81f8-9c5929e200ae | textbox | Heat Soak: t2 (Seconds)
d1cc71db-932f-5de4-a0c0-fc395a338433 | textbox | Change Over: t3 (Seconds)
81933ef5-3b95-5c6f-b175-fd1bdcb464d6 | textbox | Pressure Up: t4* (Seconds)
c15c15e7-f6ae-5046-afd1-0e6f8c88ba27 | note | *t4 not applicable for SHP situations
7705f704-bc80-5875-8b56-c21bfd81f3fe | textbox | Weld and Cool: P3 (Kpa/Bar)
9b08455d-db3a-57c3-b19d-3cd4d00326f5 | textbox | Weld and Cool: t5 (h:m)
3e27d7a6-ed76-5bf2-a12d-f3d4ddb296d5 | textbox | Rough Handling: t6 (h:m)
3f5bcd74-4504-5c1b-91e0-8f0e1b6cb7f1 | textbox | Bead Size: Min
587a3240-2824-5675-9b83-c0c92c5a885a | textbox | Bead Size: Max
80078b49-e0e9-5f53-b0b4-be8d08aa2196 | textbox | Comments
f9b43fa1-300d-4d00-8eee-fd3aebcfcae3 | checkpoint | Weld #7
c1731414-9aab-557b-a6e6-48ccb1352a97 | textbox | Time
c592b758-3cd6-54d5-9141-6197dd135b98 | textbox | Ambient °C
ce569232-3117-5709-9f60-39abe1fc62f0 | textbox | Heater Plate °C
e449623c-f9c0-5616-8f1c-f8fd9e656ff5 | textbox | Drag Pressure
f19d641b-601a-5794-ba68-b720c1409ec6 | textbox | Bead Up: P1 (Kpa/Bar)
6e67ccaf-4f1f-598c-b590-0af2572e6f98 | textbox | Bead Up: t1 (Evidence)
5cda27cf-a6eb-52b2-af06-90e9a6a4c886 | textbox | Heat Soak: P2 (Kpa/Bar)
c5a87544-5801-5fbf-ae2a-2efc89f31cf0 | textbox | Heat Soak: t2 (Seconds)
da7a7906-f573-5155-902d-016ed2cb9d08 | textbox | Change Over: t3 (Seconds)
045b1cc3-4cbc-5dfc-a955-beaf77e51e2c | textbox | Pressure Up: t4* (Seconds)
c1e001fe-e2f4-5339-9e79-46f521b5b574 | note | *t4 not applicable for SHP situations
71348539-3cfa-520f-862d-2543108eb601 | textbox | Weld and Cool: P3 (Kpa/Bar)
169fdbd1-46ed-515c-b041-f749ebac064f | textbox | Weld and Cool: t5 (h:m)
9d461614-1a06-5a86-ab0d-93a0db2c48e2 | textbox | Rough Handling: t6 (h:m)
94d35d42-252f-502c-8382-f109488b0842 | textbox | Bead Size: Min
3f40ff01-49f0-5dc5-9e48-29727625f6b8 | textbox | Bead Size: Max
629b0344-6b87-5c77-a543-659200443571 | textbox | Comments
f0068186-c234-42a4-b6f7-cb12708e7122 | checkpoint | Weld #8
8f597d97-b47f-5314-a0b6-3be2a84b15e9 | textbox | Time
38de1d43-26ce-5250-94fe-c40de96d79b9 | textbox | Ambient °C
f684cd91-b169-53f9-89c3-0352a8d3accb | textbox | Heater Plate °C
826b984c-7e85-5918-b11c-172e2f2c291d | textbox | Drag Pressure
ddcbae59-f267-5074-aa2a-a34c04d080b3 | textbox | Bead Up: P1 (Kpa/Bar)
5053ff17-c32f-530d-87d4-c8d1afaeb6c6 | textbox | Bead Up: t1 (Evidence)
60cbba25-f06b-5d93-90b2-31053f52ff66 | textbox | Heat Soak: P2 (Kpa/Bar)
5920d70b-fc49-5d47-a998-c02630a5022c | textbox | Heat Soak: t2 (Seconds)
b9f9be7a-93f6-5db7-b241-778154675269 | textbox | Change Over: t3 (Seconds)
fae94cbc-73a7-57a2-a29e-9b05d7e07225 | textbox | Pressure Up: t4* (Seconds)
17ddd88d-4eba-5967-a309-07628b0f66db | note | *t4 not applicable for SHP situations
3434a80d-32b5-5926-95c9-e4ec39a55f53 | textbox | Weld and Cool: P3 (Kpa/Bar)
1b36ef9b-effc-5324-9d06-da9224686d8c | textbox | Weld and Cool: t5 (h:m)
2d14a853-d5eb-5ee5-832a-939eba7aeb95 | textbox | Rough Handling: t6 (h:m)
025ffc83-77e1-538a-a217-66765fd36c26 | textbox | Bead Size: Min
88a399aa-cb36-5e7b-b149-da8c4478c107 | textbox | Bead Size: Max
e27a54a0-dccc-53d3-9bd4-0f575e4d8880 | textbox | Comments
c6ed36d0-a228-4351-bc04-7fed10ee9ee2 | checkpoint | Weld #9
152e4811-6e0a-56f3-a6e1-704b524b68bc | textbox | Time
0ac431f2-4b10-5e6a-a2f0-f025dfa445bd | textbox | Ambient °C
8fc61011-5519-59ab-8fb0-b85bc8a2d2e0 | textbox | Heater Plate °C
ea169f9e-eba1-5049-ba93-654694f45a38 | textbox | Drag Pressure
ccab0021-ec4e-56bc-94fa-2219ce8e51c7 | textbox | Bead Up: P1 (Kpa/Bar)
ccc70d40-aebc-57ef-a2fa-67925edf4019 | textbox | Bead Up: t1 (Evidence)
57fd1021-b11c-5cbd-9c8a-4408680695b9 | textbox | Heat Soak: P2 (Kpa/Bar)
457af086-420d-559c-b80a-4ae2f6c83514 | textbox | Heat Soak: t2 (Seconds)
57a03850-b8a8-5bf8-9d3f-73981faa4c0e | textbox | Change Over: t3 (Seconds)
6f85bcc6-2156-557f-8c1a-31676dfc9638 | textbox | Pressure Up: t4* (Seconds)
6b67f777-4dad-5329-897b-e182cd30bbe4 | note | *t4 not applicable for SHP situations
b106574f-463a-572b-ab89-e8ee729f76a1 | textbox | Weld and Cool: P3 (Kpa/Bar)
6e005382-e16b-514b-87be-c5bd2a6b8801 | textbox | Weld and Cool: t5 (h:m)
8121ba36-ce46-5e8a-8bf9-265942f31cbd | textbox | Rough Handling: t6 (h:m)
db2f43f2-d457-51be-936f-0d741f2af830 | textbox | Bead Size: Min
78e1af61-2da9-509d-9b7a-04558ec10481 | textbox | Bead Size: Max
e7237614-32e8-5801-a549-45f860542997 | textbox | Comments
7232acfa-b82d-41b5-8661-259568a02f51 | checkpoint | Weld #10
1742b2d5-2a9f-5470-98f6-4503b55dd0a7 | textbox | Time
f1a60a0a-99ca-570e-9622-0af431a60f7e | textbox | Ambient °C
1421e89f-3e0a-5fcf-939a-4d4a997f4f59 | textbox | Heater Plate °C
e6246011-7f26-5f67-95cd-cda8e030f2d9 | textbox | Drag Pressure
a6453aa2-c288-57de-8c00-f533b27fe4b0 | textbox | Bead Up: P1 (Kpa/Bar)
8f3aeb8b-3aaa-552e-b391-e53d19425cf0 | textbox | Bead Up: t1 (Evidence)
b0da2c23-5b84-5923-ac55-850cacd19b24 | textbox | Heat Soak: P2 (Kpa/Bar)
6bce50e7-eb5b-5014-b362-2338b6679a38 | textbox | Heat Soak: t2 (Seconds)
938e956f-24a5-5a8a-a6f0-2f826a696449 | textbox | Change Over: t3 (Seconds)
047c4b92-67ad-5eaa-a947-de6ebc21f6ef | textbox | Pressure Up: t4* (Seconds)
bc7eb3ab-6a22-5a0f-a794-f3be6eda061b | note | *t4 not applicable for SHP situations
2eea0dba-02b6-5653-8128-91d57ab936bf | textbox | Weld and Cool: P3 (Kpa/Bar)
82e98091-1c0b-5b94-af11-1053e20cd20a | textbox | Weld and Cool: t5 (h:m)
204c65d7-dd24-54ee-b47a-e4293b0b8d02 | textbox | Rough Handling: t6 (h:m)
ce2bdfdf-76eb-5034-ba86-98a7a3db5c45 | textbox | Bead Size: Min
5ecb4be9-d46f-55e7-a6a0-110f602a7998 | textbox | Bead Size: Max
3713f80f-af39-5f71-8fa0-b84bbfc560a0 | textbox | Comments
549c3ec5-1334-4d08-9980-69963540342b | checkpoint | Weld #11
9c806a28-8a65-5d35-8d1a-2614aa13cfa9 | textbox | Time
25747ced-a86a-54ab-89bf-c92f1c1f12e6 | textbox | Ambient °C
d338c258-5335-5662-b521-e83d03ce405a | textbox | Heater Plate °C
8230bff3-7ecc-5c20-9f73-1fd22fa2fe0c | textbox | Drag Pressure
ba864ca2-7bd1-5ac6-8e74-5049ae3537c7 | textbox | Bead Up: P1 (Kpa/Bar)
952cc56d-ffff-5e04-a978-d76d2de86639 | textbox | Bead Up: t1 (Evidence)
4496a925-81b2-513d-99cd-bd7338879e68 | textbox | Heat Soak: P2 (Kpa/Bar)
979f9945-4281-55fc-94b9-9232bf365441 | textbox | Heat Soak: t2 (Seconds)
215ab350-7dc1-519a-885b-958aa4edd071 | textbox | Change Over: t3 (Seconds)
bcf33a3c-01a3-57c0-9f2d-2e962e0edffe | textbox | Pressure Up: t4* (Seconds)
4c87d8dc-9ab9-59c5-9b01-7087dfea2dea | note | *t4 not applicable for SHP situations
e454629d-c89c-573b-80af-04c7a84f0fe4 | textbox | Weld and Cool: P3 (Kpa/Bar)
2fc97de0-d4cc-5780-93ea-49799dc84e2a | textbox | Weld and Cool: t5 (h:m)
694596c0-8665-5a89-b407-1b74fc2d3e0f | textbox | Rough Handling: t6 (h:m)
f7a83911-a37c-5dcb-9890-07675cba5e34 | textbox | Bead Size: Min
dfad453c-48ac-58c3-83f6-512393cc304e | textbox | Bead Size: Max
21551884-e067-58be-90b8-7e7c53351d83 | textbox | Comments
25dbf5e6-e85f-46ad-b932-ce9d9a5ce52b | checkpoint | Weld #12
1cf4880f-5692-5f9a-981b-2621e017b296 | textbox | Time
83172cc5-794b-5359-bc09-0fbabde5158a | textbox | Ambient °C
64774a28-dec8-5209-bde0-e3393d4460fe | textbox | Heater Plate °C
3b7538ab-10d5-5dad-b1fc-0dbe88d7da96 | textbox | Drag Pressure
38c4a80e-d84a-52ea-ac4e-7625af292b7e | textbox | Bead Up: P1 (Kpa/Bar)
9eed04b8-a7c7-590d-aae4-8f0402caa6ca | textbox | Bead Up: t1 (Evidence)
cfb32152-52f1-54c4-9e95-5195af43d3de | textbox | Heat Soak: P2 (Kpa/Bar)
e4399a36-3346-5647-8c2f-0466823837a9 | textbox | Heat Soak: t2 (Seconds)
12c2b5a4-4222-535e-a05b-2c56deea56bb | textbox | Change Over: t3 (Seconds)
2f6b94ea-da72-5343-b932-8fcdd429ca9c | textbox | Pressure Up: t4* (Seconds)
b0847eac-45ea-584b-b8cc-52248025dc56 | note | *t4 not applicable for SHP situations
889d2859-d3b6-5eca-90be-1bfff46cd1f3 | textbox | Weld and Cool: P3 (Kpa/Bar)
f5a07e27-9c68-5bbd-b6c0-d56c83f2585e | textbox | Weld and Cool: t5 (h:m)
a2e06ffb-c1b9-545c-ad34-0319bb68b78a | textbox | Rough Handling: t6 (h:m)
23cceab3-877e-532d-9c7c-2b0b8ef8124d | textbox | Bead Size: Min
2fd43bb1-13dc-5179-ba22-4e775be0a7b6 | textbox | Bead Size: Max
115adf1a-7cd9-5f0d-8a9a-30c5c77d2883 | textbox | Comments
8927f230-313b-426b-9475-99632361715b | checkpoint | Weld #13
d2cedd53-9db7-51f1-97c3-15c17ed614ca | textbox | Time
59aa2bcc-3696-558c-acb0-8eb86a22be41 | textbox | Ambient °C
e652e5e7-2b23-5700-b58d-6dd7b5600c98 | textbox | Heater Plate °C
bf1338cc-4229-582e-bc6c-178cd5dd6e82 | textbox | Drag Pressure
03c58d07-46ae-530e-bb2e-1294563f8adb | textbox | Bead Up: P1 (Kpa/Bar)
dc6fc6ca-1601-5aed-aeb5-e8d4fad7b757 | textbox | Bead Up: t1 (Evidence)
8002f1be-024b-566a-a3de-b7f7eb8000c1 | textbox | Heat Soak: P2 (Kpa/Bar)
85c872c4-6e22-516a-b1af-1eb808a4ce29 | textbox | Heat Soak: t2 (Seconds)
f575adb1-6540-5d44-8677-59feea9239f9 | textbox | Change Over: t3 (Seconds)
b6fca43e-c071-5108-857a-a1b0581085c5 | textbox | Pressure Up: t4* (Seconds)
9f3f7a44-40df-5762-9f3c-1b1c5218b73b | note | *t4 not applicable for SHP situations
c90821b5-c0a4-5265-835c-7f3464829088 | textbox | Weld and Cool: P3 (Kpa/Bar)
6c27193f-4b6e-5b53-8338-c2a12d2b09e1 | textbox | Weld and Cool: t5 (h:m)
a7726ba7-0b0e-56d7-a117-fb8e8d65b053 | textbox | Rough Handling: t6 (h:m)
a725ac9d-3de9-5676-b8a0-6601044107a3 | textbox | Bead Size: Min
a6f33be3-0873-5aa4-b79a-b55af729cfdb | textbox | Bead Size: Max
b9d915e1-f9c7-55b9-ab7d-7f5927c6396b | textbox | Comments
49a98601-c202-4551-8349-e403d87008df | checkpoint | Weld #14
27153778-332e-5897-a707-c6f3018f4063 | textbox | Time
2031aa5f-9fa2-522d-a78e-c536b567f5e3 | textbox | Ambient °C
5f1f4a02-9c57-55fb-a139-72acd4ec024b | textbox | Heater Plate °C
ec769f09-31d3-5c41-b0d5-2058734745b9 | textbox | Drag Pressure
7294c575-60e2-5dd2-9535-9359d2a6e021 | textbox | Bead Up: P1 (Kpa/Bar)
d284572a-cb42-52b1-8f20-6c692ad08eaf | textbox | Bead Up: t1 (Evidence)
34cbd2b0-3ea9-5ca8-b4dc-9b96cd4118d7 | textbox | Heat Soak: P2 (Kpa/Bar)
bd706829-a3ba-5e83-ad99-ef2827d37ffe | textbox | Heat Soak: t2 (Seconds)
df704de2-96dd-5c4e-ae08-3249d15a4ca5 | textbox | Change Over: t3 (Seconds)
22eea7c4-2419-5277-99f5-a6ecab19de9e | textbox | Pressure Up: t4* (Seconds)
d8279d85-a89e-5ada-8f81-20e884036289 | note | *t4 not applicable for SHP situations
a53166b7-e893-5357-b65d-69be607fece6 | textbox | Weld and Cool: P3 (Kpa/Bar)
782d975d-9e05-5726-9fad-f6d96c3939cb | textbox | Weld and Cool: t5 (h:m)
4c246af1-9cef-5697-9ba7-c9240ebab4be | textbox | Rough Handling: t6 (h:m)
3d4c1e4a-1ac3-574c-bdbe-3dd918f64829 | textbox | Bead Size: Min
00cd8269-21b5-5c1b-b1c3-081ebb42d8ee | textbox | Bead Size: Max
16cc2178-fe3c-5d67-a60d-96eeb59dfc0f | textbox | Comments
3464e6f1-dcbf-4fa4-bd9e-3dc735e64234 | checkpoint | Weld #15
0aef2956-aa7b-5fb4-88c4-3e6abea7aa1c | textbox | Time
e5d4acf0-72a7-57a8-a466-81aa7ec15010 | textbox | Ambient °C
1cb1addd-1e66-5e9e-b29a-c36af5f0cf12 | textbox | Heater Plate °C
784f5246-90fb-522f-bcb1-6ec11226380f | textbox | Drag Pressure
eeacbae9-b369-59a6-aa61-e6f6ba0ad341 | textbox | Bead Up: P1 (Kpa/Bar)
48000f39-7a2f-5476-bea6-3d9a6559f2d0 | textbox | Bead Up: t1 (Evidence)
22527124-2a0e-537e-b492-3c54eb54637f | textbox | Heat Soak: P2 (Kpa/Bar)
f335fa99-243e-5846-9451-420d7a1c8b60 | textbox | Heat Soak: t2 (Seconds)
427aa325-9acc-5481-85e0-6245e75bfd41 | textbox | Change Over: t3 (Seconds)
b9066c16-50fd-57d9-a759-c4e0e50fdaa4 | textbox | Pressure Up: t4* (Seconds)
cc6d5fe5-6c96-577a-b827-dde448cb0be9 | note | *t4 not applicable for SHP situations
ecca4f7c-0145-5620-a25e-8935e16575c6 | textbox | Weld and Cool: P3 (Kpa/Bar)
6e40b436-99f4-5d79-9719-e759ac9b49a3 | textbox | Weld and Cool: t5 (h:m)
5562b210-ee4f-54fc-bf4d-7e9ea96664bb | textbox | Rough Handling: t6 (h:m)
b6d0b32d-f7d2-53ce-bc23-2365ed871080 | textbox | Bead Size: Min
f6122c78-3fb8-555d-a2c5-e6cc21daf4eb | textbox | Bead Size: Max
336bdd5a-3dfa-554a-b08e-0ec8440db229 | textbox | Comments
0becacab-10bb-488a-b96c-ade87da15f57 | checkpoint | Weld #16
1083e63e-cd81-51ad-8ca1-833d04041e53 | textbox | Time
b600f02f-699b-5501-b0a3-56731489fc18 | textbox | Ambient °C
f265547e-f32e-5325-86ee-f535f5763302 | textbox | Heater Plate °C
718b9e91-6316-5f92-9b3c-e42285042b62 | textbox | Drag Pressure
306bf348-1a9a-5946-8357-95533f60a291 | textbox | Bead Up: P1 (Kpa/Bar)
851f133f-1f43-566f-8448-951bce2183ee | textbox | Bead Up: t1 (Evidence)
b5dd8b38-f830-5aef-a1ff-6afd935b139d | textbox | Heat Soak: P2 (Kpa/Bar)
0e6a38f2-d196-543c-baa6-35484efc5b29 | textbox | Heat Soak: t2 (Seconds)
884d014c-7dad-5dbd-adc8-75a88478311e | textbox | Change Over: t3 (Seconds)
6a66af10-1550-59fa-9645-8c6e8feb1bb4 | textbox | Pressure Up: t4* (Seconds)
fbd7ebf3-f375-5380-868d-d26be0ac530c | note | *t4 not applicable for SHP situations
76d25581-f9ba-58ef-89bd-a95e0358b104 | textbox | Weld and Cool: P3 (Kpa/Bar)
f6d8c17f-ec2c-5075-8b60-80bf24448c1d | textbox | Weld and Cool: t5 (h:m)
0bd412f5-5502-5152-96d2-5100d8848ee3 | textbox | Rough Handling: t6 (h:m)
ccd89919-161f-5269-b498-68dec2dd0658 | textbox | Bead Size: Min
261ae6a1-9ec1-5507-9038-09a7d300c1d9 | textbox | Bead Size: Max
2ad714ed-8778-5c04-a0dd-fbdba97e8cfe | textbox | Comments
3fbc8964-29c8-4888-a484-934b119d7f53 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
cbee3c11-daef-59a1-a30d-7b1ce13c2043 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
983ace80-7aa0-5d8d-9f5b-f1c8d2aefbb0 | note | Company: Geschke Group
864b7856-b05d-5eb4-a639-a8cec70f9a68 | note | Phone: 03 9798 1619
589176de-4282-51e3-884f-f4daf79dd666 | note | Address: 45 Pacific Drive, Keysborough
d0429fe7-f136-5aa8-95dd-b4d196b4095e | note | Project: Centre for National Resilience Project - Melbourne
c5a1c988-6490-53fa-b4b5-8f1c063b5b46 | note | Principal: Multiplex Constructions
b3c686d1-e6b6-49c5-8411-bcf768359511 | checkpoint | Foreman Sign-Offs completed - Click to Attach Signature(s) below
f2287b5a-546f-5fa0-ba56-8fc3e898e454 | note | Operator Sign-off added to each weld above as required
151ef55a-89a3-5421-9297-4990e93bd5c7 | button | Geschke Group Signature Sign-Off added below | Yes, No
550d6ba7-76c4-5851-8418-52d05c8c3be1 | button | Principal Contractor Representative Sign-Off added below | Yes, No
c355d426-82b3-4e47-bdf4-7842cde76772 | checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  | QA 29 Periodic Flushing / Copper Protection Test Sheet
3ed437d0-ddf4-4394-afd0-03857d3b02a0 | checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
7cc99b2c-a55f-5a48-8763-006e9c5ca75d | note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
d0637c9e-69a7-55e1-ab94-ad34bc1407e4 | note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
6f782fb7-1977-46c2-acf4-1205c79e15ac | checkpoint | Flushing Details:
2ed50258-b778-5ddb-8ded-37e9d0ac9983 | textbox | Level / building being flushed:
5221a4e0-8a72-5a45-b00e-f3911b91b3b2 | button | Time and Type of flushing: | Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
26653d26-e07c-5698-8e21-8ecdf2ce9ee5 | textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
5c6ebe2b-81fc-5493-8b08-102a9d2d829f | textbox | Start time of flushing:
14c08006-d18d-57a4-a212-25de820facb5 | textbox | Zone/branch to be flushed:
6ace5e72-c5e1-51e2-ab5b-eaa59e0db709 | textbox | Finish time of flushing:
5fba679f-b9cc-5816-a224-e869bdf7621f | textbox | Zone/branch to be flushed:
fef6ddfe-f6d9-40e0-9bc0-be4c6917b9ff | checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
223884b6-203a-48f4-8ad0-711cb7a34403 | checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
131c92d7-2695-44d3-89d2-865b7f624b7b | checkpoint | Have you set a reminder for the next flushing of this pipework?
dc26a49b-6a16-4302-9a0a-da98d96c83b0 | checkpoint | Have the hot and cold been interconnected for flushing purposes?
abc7fa1a-017a-4b3c-9440-2db10ed08826 | checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
bcb30090-a709-5874-89ef-d2b251b8be9d | textbox | Date for next flushing:
3624560c-ba05-50b5-996c-31a4423ef1fc | textbox | Test completed by:
e56aafc6-da26-501b-8a11-cfb492deb640 | textbox | Builder Representative:
895496fa-0314-4775-b44e-171e434c4583 | checklist | Quality Control Pressure Test Report |  | Quality Control Pressure Test Report
73bf053c-325b-4fc5-afd9-4319bb9deaff | checkpoint | Quality Control Pressure Test Report:
7e389bda-5238-58e8-9531-c9e8aee03689 | textbox | Drawing No.:
8fbe2e6a-96c1-55b3-adc4-3838728ae780 | textbox | Rev.:
751c9fab-6364-5edd-bf25-aef8535af27c | button | Test: | Air,Water
2a7c6ded-f830-5d20-a6b7-77a739cc3281 | textbox | Section
91798545-b737-5574-8ab6-747fa3c8d6bf | textbox | From
eddde015-f685-54f1-8d40-d9f6f630a831 | textbox | To
bcb1e385-040b-5ee9-a58d-28c3e800293f | note | Specified System Working
45f5e0a5-51e9-5ee1-ae78-5d971b32da3d | textbox | Pressure (KPA)
c350c184-8a8d-5bee-9ac9-2907a3a7647b | textbox | Duration (HRS)
29cb1413-d7f9-53d7-879f-7c6c15b07e87 | note | Specified System Test
1e5fdbef-86d9-56a9-bbdc-62917f507947 | textbox | Pressure (KPA)
9a5727c9-16ba-5d0c-be01-4c2e0e1bf03f | textbox | Duration (HRS)
69cc7cac-3795-4f7a-92cc-049ce12b932e | checkpoint | 1st Reading
f771b884-6fce-5f7f-97c7-692cd5a64b0a | textbox | Time
29da583a-bd28-53bb-a590-8c2c7a5ad198 | textbox | KPA
ece5968f-00fc-5972-be23-dd6da5ca426d | textbox | Ambient Temp
04f07701-3b80-4afb-a477-ee8db1f29760 | checkpoint | 2nd Reading
941b84cf-ee9e-5b3b-8302-0a37688bedf9 | textbox | Time
1477123c-4ad3-529b-8404-034cc66804ff | textbox | KPA
92e0183e-e5f7-5c9e-a800-ef7a6f1bc017 | textbox | Ambient Temp
4ac9bcec-7003-4376-bf52-5dd5cb5fa347 | checkpoint | Test Result - Passed?
207dce33-8eef-55a4-a3bb-34318897d2b4 | textbox | Repeat
581c600a-7a3b-4f9c-9c3e-ad60da22600d | checkpoint | Sign Off
fbacbc90-ee1d-528f-97c1-d68e3949e068 | textbox | Geschke Pty Ltd. Representative
a4882b3d-bc1f-5d23-8234-45d42ac14376 | textbox | Others Present
69724b66-ea6e-556a-b1ce-d74622d2ca8a | textbox | Date of Satisfactory Completion
1db2daac-7cd7-4f64-8436-e6e8c3d5f47b | checklist | Safety Shower Functionality Audit |  | Safety Shower Functionality Audit
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e4b7b4a3-1837-4dc8-b2aa-faa3fa799827 | checkpoint | Accessibility
5c49a56e-3b84-586e-9e9b-6fb103c3a3d9 | note | Is the location of the product in an accessible area, eg, no more than 10 seconds away from the hazard and has a clear path leading from the hazard to the safety product.
a953a1e6-e71f-4088-b14e-4cd049a857de | checkpoint | Identification
bea02844-c59e-51f8-aec2-ba0681060f34 | note | Is the safety product clearly identified with appropriate signage visible from the hazardous area
64717cd6-44eb-402e-9f5c-aa23f5c2110f | checkpoint | Support Brackets
10917575-c291-533e-a4a2-b1c558396a7f | note | Is the safety product securely fixed with corrosion resistant anchors and brackets
2d6a3e9c-d187-4897-a628-48d1b7e4d440 | checkpoint | Installation details
2d93171a-04da-59d2-aa11-5213b26f0cb2 | note | Is the safety product installed at the appropriate height
18ed1492-013b-482f-9a22-c70902a11604 | checkpoint | Exterior and operating instructions
cd233a06-77d4-5b44-9b4b-30e2cb65c641 | note | Is the safety product fitted with operational instructions and a test tag
a3d951b0-16d9-4536-83e9-c8c17e871a48 | checkpoint | External Damage
f2b35a0d-141e-54bd-8adf-11b7a928d17e | note | Is the safety product free from visible damage
98c9c7b2-6c3f-47a7-9029-e46f53d1cd5e | checkpoint | External Corrosion
f06ec145-c30a-5cfd-b02e-8c6ebe71d73d | note | Is the safety product free from external corrosion
e4923689-ed79-4630-a053-1af14462e2ac | checkpoint | Activation Points
8fe5238d-dbef-520a-b90d-ec18ee16b8b9 | note | Are all activation points secure and in good working order
9d03ce0e-f583-4b31-824f-3cb4b14810e9 | checkpoint | Leak Test
d3839b98-5cea-5ff7-9734-5c73f05fc889 | button | Check that shower/eye/face wash has no leaks - shower rose. | Pass, Fail, N/A
a7c5bded-1b8a-5bc7-aba7-d8e06a1edb02 | button | eye/face outlets | Pass, Fail, N/A
cd09e1a4-40d8-57e2-9db6-9f06ee93ec56 | button | ball valves - shower 1" | Pass, Fail, N/A
abbabefe-c9df-5183-9fc4-cbe6ee190214 | button | ball valves - eyewash 1/2" | Pass, Fail, N/A
3c5ff89d-f0fc-4aa4-8de8-9a50f8f35fdd | checkpoint | Dust Caps
2b37fada-9ce6-5ddd-acb9-11ff7dbe9c6b | note | Are the dust caps correctly fitted and in good working order
94a2f1c0-6b8c-4d50-8c19-67e586c5c595 | checkpoint-no-value | Flow details
f8645c38-eb9c-5a51-a1cc-c98e9042d82c | note | What are the flow details from the safety eye wash outlet
e7238459-24b6-57a7-84b5-ca4a30ee0cb3 | button | Does the flow meet in the middle | Pass, Fail, N/A
a3c4f4b8-ebfc-57d9-8460-2f1d3e3ba90d | note | what are the flow details from the safety product with all outlets flowing
635d43ac-88e7-5827-8a0b-495dfb2d35a7 | button | Litres per second | Pass, Fail, N/A
6dbb3659-8ca0-553b-a856-4be321402277 | textbox | LPS
62622cee-f16b-49a6-9a8e-e16b7493f6f7 | checkpoint | Temperature Test
32148a78-193f-5d82-813e-20aa78d6522c | note | Turn on shower, test temperature
f2aca789-0a33-5175-b056-73ff8897ff5c | textbox | Temperature
c037adf6-44a2-4a40-9069-067e8a2ceccd | checklist | Service Cross Connection Check List Report |  | Service Cross Connection Check List Report
48dc4ca5-4e6b-4e3d-a30a-da15cb816081 | checkpoint | Service Cross Connection Check List Report Details:
113f53c8-26da-5e3f-8a29-0edaf700d5b2 | textbox | Zone/Grid:
2697c86c-0d2d-53db-96f0-e38a9195f618 | textbox | Drawing No.:
d2d360d9-d9a1-5b24-9433-9d0744aa9a88 | textbox | Rev:
9b7333d8-e639-4cd1-bd5f-fac0b156004c | checkpoint | Service to be tested
81a12de8-dc39-5860-b6d7-46532ae453d9 | note | Isolation of potable supply in general.
56f7259a-8d81-4a81-b73e-d293ddfef008 | checkpoint | Potable Water Supply
36c0211d-53e0-583e-9835-bfdc1fb7804c | note | Confirmation of service isolation at all fixtures.
5adaaeeb-b922-5a16-891c-5857975cb75a | note | Keep potable water turned off.
59531b47-12e0-4ab6-afdb-da388c943e80 | checkpoint | Non Potable Supply
2a2f5a14-b003-5c59-a46b-0b320c9d8770 | note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
43f736ca-2ff0-41df-83e6-a1d6fef715c0 | checkpoint | Turn potable back on
2c2a467d-c915-5c3e-a60d-ad8b8c93d9ea | note | Potable back on
646c049a-9280-441d-840c-4c2469d22d10 | checkpoint | Non potable supply
0e33c1bd-b310-5973-aa17-cfdd338575c0 | note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
78fbe754-641b-4b86-881c-c2c4e2741d7c | checkpoint | Potable Supply
2ae6e229-4b83-5aa7-9d4d-82e03c1ea61f | note | Check all fixtures that receive potable water are still getting potable water.
2502ab60-a80f-4554-a5cb-b01538e3e20d | checkpoint | Pipe Identification
ab7a5246-7cdb-5a87-9cf3-45de25153120 | note | Confirm recycled water piping is identified by colour and noteling.
3e7e5e49-700c-44ae-966a-9be19f922547 | checkpoint | Other
2446ee9e-e182-45e5-be3f-16dff16de1b2 | checklist | Stormwater Drainage Inspection Report |  | Stormwater Drainage Inspection Report
433e281f-19ce-451b-80fe-7f9d22663095 | checkpoint | Stormwater Drainage Inspection Report Details:
4e8fc86e-95dc-578b-9843-2f24b5363466 | textbox | Spec No.:
bec0c40a-2a3f-5256-8aa4-a7c311170900 | textbox | Drawing no.:
c6cb5378-9a6a-57a8-9c36-3ca77994bc86 | textbox | Zone:
69ff256d-8d4b-48e7-bfa2-dfd59103a334 | checkpoint | Pipe Lines
195d344c-058e-5989-aca6-5ae2778c0139 | textbox | Date started:
1aa76f74-6487-50de-8e26-9d314769d3a2 | textbox | Drainage Line Number:
a1680e0d-d996-5dfb-85c8-e3ea326196e9 | button | Pipe Damaged? | No,Yes
c1faab2f-9984-5eb4-af4f-0c5b0de10b14 | textbox | Size and Class
17ac86cd-743c-5534-a666-d3d9ba520cc4 | textbox | Jointing Required
d7795c65-5c74-5fbb-94ca-d0163901e53b | note | Bedding and Haunching
e0524291-289c-5b3e-bbea-484270b2a099 | textbox | GPL - Initial/Date
171ffcbb-ff04-5b7f-b9f7-915ca8575465 | textbox | Builder - Initial/Date
55a75e6e-719b-5e1a-a383-29f5b9f23841 | note | Backfill
4ab44494-14e5-5e3d-9fe4-4d543819e7af | textbox | GPL - Initial/Date
d633149f-750c-554c-9c04-69ca91df4a9b | textbox | Builder - Initial/Date
c13e1d3b-1df4-50e7-be76-c7def647fcd3 | textbox | Comments
6f6606f4-d768-55f9-a228-0cf2686ddae7 | note | Final Sign Off (Initial & Date)
c59986aa-8b23-5dc0-b10a-2cbc7b3e5104 | textbox | GPL
242659e9-83fb-5815-90d6-df997a3fa136 | textbox | Builder - Initial/Date
a8c7229b-0b27-5415-ace4-b3aeb7ca5f2e | textbox | HCC/CARDNO
725933b6-20d4-4670-8fe2-4ddf2afaac48 | checkpoint | Drainage Pits
009b89ce-234e-52dc-85a2-5b6796526a90 | textbox | Date Installed:
144d069e-570a-528c-8f8f-c297905371ff | textbox | Pit Number:
1f3a525e-58e3-54dc-946c-e04b9c4c70a8 | textbox | Pit Base:
d8f3526b-5cff-5526-aef7-2d3ae37c0cc5 | textbox | Step Irons - GPL Initial/Date
e5eb0a61-0251-5ee6-8049-ad4f8b351ca3 | textbox | Bedding - GPL Initial/Date
f97eace8-a270-587b-afef-a0237ad90b9d | note | Benching, Grouting and Patching
876d6de1-5445-5c6d-8b9d-c25065cc7772 | textbox | GPL - Initial/Date
c7b6c58e-cb64-5609-aa08-bb63411e22dd | textbox | Builder - Initial/Date
47d69a44-6b5f-5c8e-bf0a-3647e6bdffd2 | note | Placement of cover
c069aff4-b2a4-5ff1-918c-cef896de6c26 | textbox | GPL - Initial/Date
0ac682d0-ec1c-56c5-a027-ab6d1d90daeb | textbox | Builder - Initial/Date
97fc6a4a-f5cd-5acd-88b6-929e6bb8a626 | textbox | Comments
cdb4cecf-8adf-581a-bfcd-b31b4b93e154 | note | Final Sign Off (Initial & Date)
d552ec8f-11d6-5411-a6ed-b23b06f4cd31 | textbox | GPL
e841422a-6a72-56f4-a8f9-49d4fd29f060 | textbox | Builder - Initial/Date
0346a082-86d8-5420-a559-381e353d5959 | textbox | HCC/CARDNO
e86479ef-99e8-40f5-a324-a2529a9a10db | checkpoint | Compaction Test Report No.
aed8cb1e-ef52-51a4-aa96-c465814adb38 | textbox | Compaction Test Report No.:
7d58d0b1-95d8-4ae3-a727-544dfd0c3c90 | checklist | TMV 12 Month Service Log V.040221 |  | TMV 12 Month Service Log (use a separate checklist for each valve)
f62689e8-9f83-430a-b765-bacc79bef1fd | checkpoint | TMV 12 Month Service Log
6f50691a-1052-508d-8942-49e4f9fee3e3 | textbox | Building name:
4b152a5c-c292-5f2b-b65c-9bd875e1b6b0 | textbox | Contact person:
9009d3d3-e172-5e90-98c6-2424962fd352 | textbox | Address:
fe012bfe-2595-5101-b131-a979e02183bb | textbox | Phone number:
2474ad68-5cf5-5eb5-bfbd-2aa6b41ee866 | textbox | Make of valve:
b58ba77d-9724-59e0-b632-a2c01965168a | textbox | Model number:
cec86261-f94b-5a41-ac58-08fa2f04f68d | textbox | Valve location:
e0416798-48a1-5701-87e1-805195bb6fda | textbox | Room name:
07f0cc2d-796d-535f-ad26-3220c5fe212e | textbox | Date of service:
74dc33f9-1bd1-5c78-a8ca-969583863bd7 | textbox | Temperature: |  |  | °C
34c78806-8271-5c24-911f-9d7ebdc7ae05 | button | Element: | Ok, Faulty
7b702738-5414-58fe-a150-2d29a9bfc558 | button | O' rings: | Ok, U, S
42b01cf6-fa34-54d8-8d06-354262c6949c | button | Strainers: | Ok, Dirty
5b9b3278-8c97-5b0f-849a-0a296e4355c0 | button | Non-return Valves | Ok, Faulty
3364de9b-9acd-5733-b0fa-6204cd3ed21b | button | Fail-safe test | Ok, Faulty
71c93ee4-c284-55ce-99e2-9bd18f206e34 | textbox | Serviced by:
4fd502bb-1d32-589f-b31f-cc82df6a231d | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
cd78f7fc-df1f-4d79-9552-e03d0e1f33d3 | checkpoint | Completion
bb196e3b-d980-5044-b91f-ae492fc70d5c | textbox | Plumber Name:
18bfb0b7-1442-46d8-82b7-9c63196ad0a1 | signoff | Add Signature
9316b6a2-18eb-4ec7-bbdb-0c0c7a60f727 | checklist | TMV Commissioning Log Sheet |  | TMV Commissioning Log Sheet
5dfb16ce-7d82-4d30-8201-a25980a0f8c0 | checkpoint | TMV Commissioning Log Sheet:
d7b26397-1c9e-50dc-924a-b3360e490e7d | textbox | Building Name:
df7ffcab-8289-53c1-8efc-961a3891cd38 | textbox | Contact Person:
f80186b4-daec-5b15-a9f9-dda7240b5299 | textbox | Address:
0b71479b-8a91-5a0b-a98a-7390842f7495 | textbox | Lic:
4366c4e7-cf8a-5e92-bb82-f9833485dcd8 | textbox | Registration number:
23179925-ae6e-5ac1-834b-445f6311a1f2 | textbox | Phone number:
89d9c5a0-95c2-5b3f-abad-0f9aeb4444df | textbox | Make of valve:
6df5879c-2dd8-5d20-a3b2-148bbf1268cd | textbox | Model number:
5aef6d45-9564-519b-bce1-fb709088d69f | textbox | Valve location:
3d6152ec-1121-5a83-9f44-4b83e33fe49a | textbox | Room name:
b1e8da01-4e0b-540d-b4a9-ce26c8cd694e | textbox | Valve purchased from:
8d6d9791-bce2-5d61-9f67-6cfc37f617b8 | textbox | Installation date:
af2f9f37-c4ba-584f-8464-8719183cc623 | textbox | Valve installed by:
96c54bf9-ea8f-5f1b-b64b-acaa46c07392 | textbox | Number of outlets served - Baths:
53168d95-e46d-5a94-9abc-d8aca0fea510 | textbox | Number of outlets served - Basins:
6c9c62f8-f930-563f-ab6f-4113a0a022f7 | textbox | Number of outlets served - Showers:
7afa47e0-b79b-5f6c-a3dc-56f0c91b2e4c | textbox | Total number of mixing valves on site:
086991ae-a801-520c-882d-eb3af042246f | button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
54d77433-7f81-5442-974d-bd9b4c4b02cb | button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
0b8e80b2-2a1b-5f5f-ac92-f88a65222e65 | textbox | Temperature of hot water supply?
b15edff2-c178-59f3-a06f-c7f99fbe5252 | textbox | Temperature of cold water supply?
1ec5182e-0a0a-5e54-ae48-e739cb241202 | textbox | Temperature of warm water delivery at outlet fitting?
2c433a62-698a-5f4a-977c-984c9089d262 | textbox | Dynamic pressure of hot water:
e1448514-cdb6-5409-bff0-abb1925c4d07 | textbox | Dynamic pressure of cold water:
bde4aa5d-fd78-4121-8b70-6fc4a7d58474 | checkpoint | Check fail safe operation (hot water at least 20c above warm water)
fb013667-d962-4022-b014-03aa1a857135 | checkpoint | Commissioned by
895423d5-3d15-5905-b1db-393b0409ec92 | textbox | Commissioned by:
44bda0c7-b53e-5185-af43-998be003aad2 | textbox | Company name:
e8085d3f-c8ec-4a35-92f0-e581ee4a304b | checklist | TMV Routine Service Log Sheet |  | TMV Routine Service Log Sheet
8560c11f-5486-4a5a-8b33-b068d989017c | checkpoint | TMV Routine Service Log Sheet:
d82ee720-7f32-545b-a3bd-64f3b03e02fb | textbox | Building name:
26bea24a-2b2f-5fbd-9d0f-14eece45eaaf | textbox | Contact Person:
86ec8a52-c4cc-5b92-9490-f874e7d3752a | textbox | Address:
475cf61f-fc72-52b9-9646-b0161a7f40ab | textbox | Phone number:
bf64a07e-0b1c-592a-94c0-b0678806d1ae | textbox | Make of valve:
d4bb1f3a-ac8c-5652-848f-03fe3da469f7 | textbox | Model number:
688f425e-dd36-53ef-a053-3dd0860b1a56 | textbox | Valve location:
466ec32f-c2b4-54ae-a9e5-dcee2ce9fc6a | textbox | Room name:
6a764419-cceb-50e3-9926-1420de43be09 | textbox | Date of service:
f0c8c43a-2679-59ae-9cbd-c56272b19017 | textbox | Outlet water temperature:
3cc841cb-aae8-5972-beee-007322fa166c | button | Outlets flushed for 15 seconds | Yes, No
e234dd33-682d-5a0e-8e7d-a206fe851496 | button | Shower heads disinfected | Yes, No
4993db5a-da52-510a-a86e-66bd14bd89c8 | textbox | Serviced By:
9b0b350f-292b-4e51-8ded-eb6972ed1e35 | checkpoint | Recommended Service Periods
d39bf8ad-7750-51ca-9579-faf5f2e84ebe | note | Outlet water temperature = Fortnightly
ca84d292-9d76-541d-9e5c-e66755601e29 | note | Flushing of outlets = Weekly
a5307ca8-ea46-555e-a2ea-f767f8a3c3ba | note | Disinfect shower heads = Monthly
b504b5e8-9703-4ed9-9e3c-f3760f654a36 | checkpoint | Completed by:
02011226-1fba-5d58-aa20-ec97ba16d4c6 | textbox | Plumber Name:
89550806-0134-4fdf-b3a2-64c59cce7e7f | signoff | Add Signature
3ffbb663-be61-4867-9caa-b5a96311548b | checklist | VHH - Water Protection - |  | VHH - Water Protection -
b79ff349-9964-42e3-b2c3-2a8d4791d422 | section | Part 1 - VHH Periodic Flushing / Copper Protection Test Sheet
273c1b52-ad99-4030-9684-95e7e68b5565 | checkpoint | ITP details
304602be-df7c-51e4-b48e-64332486dc7d | note | Copper systems are failing in the construction industry due to issues relating to design, water quality, the management of water during construction, long term maintenance of buildings with issues arising from building management team not following protocols outlined at hand over. Stagnant water being left in both hot and cold copper pipelines have been deemed to have been a contributing factor to recent copper failures. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water
1830ec43-9b74-57a5-8945-d3a0ca678321 | note | Geschke Plumbing in consultation with John Holland & AECOM have put forward a proposal of periodic flushing of the systems during construction to mitigate the stagnant water issues that have arisen in the construction industry. The purpose of this ITP is to help create a strategy to ensure water is flowing through the piping system and flushed at nominated locations
23bd7d7f-cd6f-5a2d-8f4c-9fbe75f2167b | note | Plans to flush to be submitted to John Holland prior to any flushing occurring on site
1252e1c8-70c0-457c-aba0-d6a48c80f59a | checkpoint | Flushing Details (Flushing to be Completed with Water ONLY)
3a5f46c5-1906-575f-99d9-c2d5f31a3bb9 | textbox | Level being flushed
83ecb406-3d08-5fb3-b852-6dad870228c9 | note | Stage of Flushing During the Project
1a821141-d558-5246-90ac-87dfb875dff5 | tickbox | 1. Initial flush after installation of pipework and prior to Quality Control Pressure Test Report (Geschke QA 6)
663fdc22-06c4-53b8-a85d-96f7739cd669 | tickbox | 2. Final flush post disinfection
5db543b3-e68a-5640-8815-fddb3b5bfa9c | tickbox | 3. Periodic flushing during construction (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
91cc8b37-d5e6-5a9a-be20-853a2b3abd07 | tickbox | 4. Periodic flushing from final flush until PC (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
ff22ad30-1b4b-4732-941e-02f8f7b8b212 | checkpoint | Time & Type of Flushing (As per reference table below)
ff695180-f4e6-567c-a68a-44919040d7bb | tickbox | 5. Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush
c1371cf0-7d1e-575e-a119-67e69736f202 | tickbox | 6. Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)
b1b25f4f-3ab3-59d7-b9e3-658200a52ff7 | tickbox | 7. Short branches of copper that feed rehau do not need individual flushing
bdeeaa75-27e7-4e57-ad2b-6b05b260fbb2 | checkpoint | Which fixtures are being used to flush the system (Point of Connection & Point of Discharge)
d9c06acd-24de-562b-a775-c0379117323c | note | Fixture 1
e1eec32b-a2d7-523f-b04a-d437157db0b6 | textbox | Start time of flushing
9706b423-ae92-5d9a-9c5c-ad4aa755f4cd | textbox | Zone/branch to be flushed
aceb7f58-7cb9-54fd-ae8a-50dda48d0334 | textbox | Finish time of flushing
854a8c70-7e16-59ad-9acb-b115f6100ac4 | textbox | Zone/branch to be flushed
474ab2fd-8849-5d67-acb1-718b9d40e000 | note | .. ..
97e655b9-c06d-5887-a285-8464f2746d3f | note | Fixture 2
5633da61-f986-5d61-93bb-5d351c0a3a8b | textbox | Start time of flushing
16150fca-c0c8-5e16-9f9d-d005d36bcc69 | textbox | Zone/branch to be flushed
4d732df5-7c6b-558d-8d9c-7c1ff8775784 | textbox | Finish time of flushing
7d11625e-a147-54e0-8035-d31459088794 | textbox | Zone/branch to be flushed
ab4cb7f7-7dd1-571b-900c-4f158ecb6f1b | note | .. ..
468cfb03-c9d5-5085-88d3-d7baf0440b91 | note | Fixture 3
91f76e00-f150-5d7a-aee1-bb3bae6a0d9c | textbox | Start time of flushing
51818487-8888-5381-8245-1038a83f1abc | textbox | Zone/branch to be flushed
5548eb5c-4081-5eb1-a44e-bf8abdb0e82e | textbox | Finish time of flushing
c553ecb7-d236-5a8e-9d00-1f2299f7e076 | textbox | Zone/branch to be flushed
248dcbf3-4b7c-5d85-a0d8-3604c2578618 | note | .. ..
197f00e8-6eb4-5211-b935-1f804740cc23 | note | Fixture 4
95dd5e74-8cb7-58cb-9d1e-b6d5fa725106 | textbox | Start time of flushing
8f7ffc5f-5c7b-553e-85cf-11387ee55932 | textbox | Zone/branch to be flushed
b582396e-1e10-564c-9d27-18efbeb78805 | textbox | Finish time of flushing
fe2d2112-1ab0-5963-90c1-05bbf908363b | textbox | Zone/branch to be flushed
90724697-d5ec-5e09-82fa-38a59e9e0804 | note | .. ..
b385953d-a098-53db-955b-a6f527166763 | note | Fixture 5
39993f5b-8835-5345-b2d2-ab8265d844e3 | textbox | Start time of flushing
810a0a13-229f-55ac-8314-bd9e5c3b5741 | textbox | Zone/branch to be flushed
038e09c2-e527-5ede-b8b0-1b637ff08012 | textbox | Finish time of flushing
121a88ff-7342-54f4-ba35-4fbecc8a2801 | textbox | Zone/branch to be flushed
99e19ef9-c677-5991-86e9-7b0ad3e5b429 | note | .. ..
e9d96798-1953-4e11-9130-951ea265c876 | checkpoint | Sign-Off - Pass once entered
9646f3da-de2d-5e59-b916-bee49d8726f9 | note | Add comments/photos below as applicable
6dbd4e73-2212-5d9a-a6e5-33807be9d9f5 | button | a. Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated | Yes, No
79a72222-74a2-5127-9a5b-c8065e3be762 | button | b. Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case | Yes, No
0e5473a7-2fa2-5b11-be08-f46b6d81f45e | button | c. Have you set a reminder for the next flushing of this pipework | Yes, No
89c2680c-7925-5470-8d1c-663a08fb9dd0 | textbox | Test completed by
0271e1b6-6201-5e8f-9668-62c233e6a368 | textbox | Date for next flushing (Flushing to be performed every 4 weeks at a minimum)
ceb51cc8-9a3f-4acc-af6c-c068273a57e6 | signoff | Click to add Builders Signature(s)
c35fa643-4b59-48dc-b6b3-1805752a7ca8 | checkpoint | Reference Table
30858edc-876a-58df-b044-a3b61f81e946 | note | 25mm Pipe / 0.49 (L/m) / Flush for 0.15 (Mins)
f16f9811-100b-5c63-a813-e09a443b29ff | note | 32mm Pipe / 0.80 (L/m) / Flush for 0.25 (Mins)
ac1f8ad4-4434-5f30-a043-7f9801a54e35 | note | 40mm Pipe / 1.26 (L/m) / Flush for 0.39 (Mins)
22f036cc-6351-54bd-84a7-dcf094f48319 | note | 50mm Pipe / 1.96 (L/m) / Flush for 0.61 (Mins)
dbadb29d-f155-507b-82f9-8b6df01f1eb6 | note | 65mm Pipe / 3.32 (L/m) / Flush for 1.04 (Mins)
9fbdae18-6149-5a16-839e-d4fccb3a1dbb | note | 80mm Pipe / 5.02 (L/m) / Flush for 1.57 (Mins)
6600068b-8f31-5168-b831-1602252215ed | note | 100mm Pipe / 7.85 (L/m) / Flush for 2.46 (Mins)
5d66da68-7bbc-5338-9b2a-a3d55efefd53 | note | 150mm Pipe / 17.66 (L/m) / Flush for 5.53 (Mins)
135c2da4-2bca-500f-af46-d5c0e0b901bf | note | NOTE: The table flushing time is based on 100 metres of pipework discharging through 16mm nozzle at 350KPa
3fb0c259-7198-4020-ba66-c4377b344d3b | section | Part 2 - Water Quality Testing Frequency
db2ccabf-070b-4ef2-b3b2-6b642bab85e6 | checkpoint | Water Quality Testing Details
8904686c-74fc-51d1-b6f9-ff012920ab1f | note | Stage of water quality testing during the project
f95af07a-e50a-5ff1-9a4d-a9ec0a97ebb6 | tickbox | 1. Periodic water quality testing during construction (to be completed every 3 months)
73f7ffd2-fea8-5121-929c-4c89d4704ff1 | tickbox | 2. Water quality testing post final flush
da99fe9b-83ad-4e86-af07-117003e27f52 | checkpoint | Sign-Off - Pass once entered
b03e35a8-a38d-5fe3-9ffd-74886e35c5c7 | note | Add comments/photos below as applicable
07f85d27-55ee-5c65-ba2e-48db0359d703 | button | a. Geschke and John Holland management informed of sample / testing | Yes, No
205e5455-226b-54c8-8c25-d51b3878a253 | button | b. Has the schematic / location of the sample collection been highlighted, attached, and nominated | Yes, No
fa085a0e-b447-58e8-a838-283bdfe257be | button | c. Sample captured as per laboratory requirements | Yes, No
98a9a343-0ece-5b57-b499-4313146be02a | button | d. Time and date of sample recorded | Yes, No
118059eb-1896-5e83-807d-c9b226b47fc2 | textbox | Time of Sample
8c488704-bf2d-5eec-8e35-fda79a76f445 | textbox | Date of Sample
b159e52d-b37b-5e2f-afcc-8a9f8c4266ce | textbox | Location of Sample
a7dde9f4-5054-506b-a27c-221e4dae43d1 | note | .. ..
0a4184f7-4c7b-5f96-b62c-0938f3f1c6b3 | textbox | Sample collected by
540cf84f-65b0-596c-877b-6698883fa13a | textbox | Date for next Water Quality Sample (Water quality testing to be performed every 3 months at a minimum during construction)
bae77f95-da38-4b60-aa35-5311f99c1c48 | signoff | Click to add Builders Signature(s)
4371e39a-c472-45e7-9c06-31a629d4ffe1 | section | Part 3 - Disinfection of Pipework & Tank
b18ae587-0483-4315-9f69-dd8bb623b4de | checkpoint | Disinfection Checks - Pass once below completed
a54c13d3-4308-59e5-ad8a-78dd8cc5ad0d | note | Add comments/photos below as applicable
467dbd69-0715-5fe2-a0f0-1a07d2251bf7 | button | a. Geschke and John Holland management informed of disinfection with plan provided | Yes, No
43e8e4d8-15a9-5e1b-a693-cf58fc72546e | button | b. Has disinfection occurred for 6 hours as per AS/NZS 3500.1 appendix I | Yes, No
18ff9a87-bd39-5ebc-996e-6ecf784f5db3 | button | c. Time and date of disinfection | Yes, No
d532f986-f9dc-5d1f-9247-bb0a87d44844 | button | d. Flush all levels and branches until chlorination levels have reached safe chlorine levels as per Australian drinking water guidelines. | Yes, No
bcc8d36b-d849-5911-a95f-56123e9a6ddb | textbox | Time of Disinfection
e5bd1f8a-262a-55a2-9caa-107046f1f391 | textbox | Date of Disinfection
43aa8963-f18f-545d-9594-3b60fd969ed6 | note | .. ..
7ef2ea52-9f1e-5791-a06e-6dc259f3e4c8 | textbox | Disinfection Completed by
450924c7-2f0e-4711-a670-f2c68461c426 | signoff | Click to add Builders Signature(s)
1854b741-011c-4fa2-be2f-4f0ec48bd8c7 | checklist | Water Meter Accuracy Test |  | Water Meter Accuracy Test
4e4f80a4-7152-410d-af94-aac90a3796ab | checkpoint | Water Meter Accuracy Test Details:
da9cf2a3-50cd-50fa-8c45-06842a6ebbf1 | textbox | Date:
0a1ff7ca-a54d-57e0-a5a7-eb574220221a | textbox | Project:
43016548-b452-5f0e-b290-f7ecc9cea8bc | textbox | Location of Water Meter:
e0b8d097-ed20-547f-896d-ddafe4dee825 | textbox | ID Number of Water Meter:
22306bc3-8fab-5144-8bf2-c0551d406ea5 | textbox | Model & Manufacturer:
7b254a8e-c938-59da-b2e0-38db43b7f296 | textbox | Current Counter Reading:
ef7d467b-a848-51aa-ad90-eb84a5a7a7a7 | textbox | Zone/Appliances to be Metered:
7912476e-00db-55ef-b1cb-9c1061a1ac46 | textbox | Pulse Rate:
16e396a8-954f-4aa4-be54-258df1aee1e8 | checkpoint | Measurement Apparatus
95145b99-34fe-5192-8d5b-356cf591a7c1 | tickbox | Bucket
ff225274-29bb-5237-9908-725ab1775aea | textbox | Bucket Size
e6404bb6-662a-5cca-8a1d-dcddaffa881b | tickbox | Water Meter
779b1002-9c37-5f38-8ef5-c2cb5ac7a0a5 | textbox | Calibrated Date:
9070d994-c93d-55f9-8dfe-4834a238eb48 | textbox | Other
e9afc3ca-972c-4eb6-bde0-6e2e3c6eba7b | checkpoint | Measurement Method
b8f312bb-9c37-593d-ab04-0bdbfd7db039 | note | Isolate all fixings
afe0e57d-876c-5ee9-9cf3-27ac196f19f9 | note | Place bucket at outlet of fixture and fill
bf246c4f-fdc0-52f5-ac3b-b5a211c04bfd | note | Fill in completed counter reading and minus "current reading" to measure accuracy
51e419cf-3faa-55d8-8f31-b57cc91142b5 | textbox | Completed Counter Reading:
59b93979-7577-5977-9c2d-ea762566c790 | note | Accuracy
a1aacf67-e1c5-5c29-8cce-53f8e748b020 | textbox | OK
e588b04e-6fbc-5249-8b3d-ab2655e42669 | textbox | FAILED
6957b9d4-1d74-5b07-8ccb-49f6e4d834ac | note | Replace Counter and Re-Test
3eca172a-d444-5dbf-8fa4-e4d3687c164e | textbox | OK
8e1c28a5-a470-5562-a88d-aa4a275a881f | textbox | FAILED
f0377598-f014-4f40-b959-b001ce56d2ca | checkpoint | Pulse Check
6807290d-a2de-5109-96d1-02d505ecbb1f | note | Method:
32585795-fb0a-590d-93c5-0da776373214 | note | Connect multimeter to the 2x wire connection points on pulse kit and set multimeter OHMS
f69100d9-fb9a-57a3-aef2-b17841127e3b | note | Turn a fixture on and wait for pulse reading on multimeter, then stop flow immediately
cde9ec2d-c7e2-5ceb-9bb9-c59065834976 | note | Measure bucket contents:
24499cee-4550-53e2-a197-9f02b304ab77 | textbox | Pulse Registered:
cef532e1-96c1-5fb7-b976-fe0162c03099 | note | No Pulse - Install new pulse kit and repeat process
c0fd3e25-063a-5f66-9d31-7f573dab155d | note | If Pulse registered OK
41eabd20-68b8-5093-a8c0-3ebb2c99b817 | textbox | Pulse Accuracy:
82bc8b36-389b-5293-a736-0ca0f92e3fd1 | note | (Bucket contents match spec at top of page)
5a8ae226-6504-526e-9db4-28244c92ec99 | note | Failed - Install new pulse kit and repeat process
f8d10578-f070-4dd8-b3e1-f709aa6609e0 | checkpoint | Sign Off
ce0102d9-1fc4-503e-855d-523656c41862 | textbox | Name - Geschke Representative
1aa67891-4485-4868-ad2d-59f2e7aa5581 | signoff | Signature - Geschke Representative
48dcf689-7744-4e83-98da-8935d031d79f | checklist | zSYS - TMV 12 Month Service Log (use a separate checklist for each valve) [old version] |  | TMV 12 Month Service Log (use a separate checklist for each valve)
eb87c6d7-ca3f-41ad-bbe0-cc2fcecc2b0c | checkpoint | TMV 12 Month Service Log
81f1da49-a87a-5004-bc58-16262e0885c8 | textbox | Building name:
01be9336-2aea-5daa-9897-6c21119ae6dc | textbox | Contact person:
1433301f-e822-51be-8358-b36a52777edc | textbox | Address:
c1411109-af43-5d73-a3ff-1796b060a843 | textbox | Phone number:
f2cd9b06-0eb5-50c5-ba8c-3c8c4f1c5f52 | textbox | Make of valve:
c67ff76a-464b-534b-bb12-65b7843468aa | textbox | Model number:
78a03b41-395c-5a31-b31f-44985330cd57 | textbox | Valve location:
048fa518-c30c-586a-be4b-c238cc70c044 | textbox | Room name:
b7f97d93-4dc4-5173-aa2a-dfd609c8ec85 | textbox | Date of service:
4875ebff-66d7-51eb-993a-e799c0131acc | button | Element: | Ok, Faulty
e747e047-54d3-5928-88a0-ca1f1e7bc57d | button | O' rings: | Ok, U, S
cf39538b-39ed-513b-ac8d-4a7ac468c81b | button | Strainers: | Ok, Dirty
c824b053-0a15-5c0c-986c-f722702f51be | button | Non-return Valves | Ok, Faulty
e26e091c-f7a4-5250-aa6e-a747b3b47956 | button | Fail-safe test | Ok, Faulty
fa07663b-b8a2-563a-8eba-f6e24a11a6d8 | textbox | Serviced by:
6d0a35b9-0148-5757-9bed-303a0bbc429d | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
4f82a952-6716-4dcf-af55-fb7ead8dde19 | checkpoint | Completion
1bdec24d-72a3-56cd-8641-3e3a3730b720 | textbox | Plumber Name:
edcfb685-7473-4e78-ac8b-1b208e083be2 | signoff | Add Signature