## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 9e261283-8d97-4668-8c11-7faad08ce31e |  | checklist | Vertical walls only H: 1.3m with 200mm wrap up on both sides |  |  |  |  | Yes | zSYS - Vertical walls only H: 1.3m with 200mm wrap up on both sides | 020e3dfb-ddea-49c8-928e-aef2ae23986b
checkpoint-status | 78ead779-76f1-4107-912c-e77d719d686a |  | checkpoint | Relevant Australian Standards Checked
label | b8d7054c-2d79-554b-bfc7-522bb43ccd8e |  | note | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint-status | 7944bd19-7acf-4af9-aa9a-7347670ebfdf |  | checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint-status | 17c476ef-7b56-4ef5-b42a-4253fd878fad |  | checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | 8bffce31-57bd-54e2-bb0d-00dbb1896edb |  | note | Attach Photo
checkpoint-status | 4fde316c-a1af-43e3-98e2-5bbc53a09289 |  | checkpoint | Moisture Content Test
label | a7d463f7-a541-5b70-a5d5-d678567c9673 |  | note | Attach Photo
checkpoint-status | 3c503f0b-16bc-4a64-bcb5-9eb669e94693 |  | checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | 4d47a539-d467-591c-8276-441ba3f75910 |  | note | Attach Photo
checkpoint-status | 8009faed-c32a-4d0a-be2c-fe8323eca1ef |  | checkpoint | Apply primer using a brush or roller
label | def4ff4d-3dff-534f-b675-6e47b8d7fd87 |  | note | Attach Photo
checkpoint-status | c5821bd8-e227-43fb-ab62-3e15cc2e8eb6 |  | checkpoint | Mixing
checkpoint-status | 244d47aa-f632-4376-ad9c-2fd35da6741a |  | checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint-status | bc51d328-2fd4-4885-b5de-d8529148444d |  | checkpoint | Curing
checkpoint-status | 91111439-873a-420e-b0de-9f8845e9e5e4 |  | checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | adbe3938-7994-5c7f-8b4c-f376839d0bfb |  | note | Attach Photo
checkpoint-status | 8c80992a-8c16-4ddb-8582-8e8dc477ae97 |  | checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | 5d3d3912-de0f-45dc-bb4f-0676e833e241 |  | signoff | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-sectioned | c7050a6f-1973-4351-8787-1b6959bcc6c9 |  | checklist | 200P Ultra V01 |  |  |  |  | Yes | 200P Ultra V01 | 050c0976-f931-4e13-abdc-eb98f9232f89
checkpoint-group | 88466057-49cf-4cd7-9148-959a5ef816c8 |  | section | DETAILS
checkpoint-status | 56a6f3a8-1b79-4279-b9f6-c84b4466ab76 |  | checkpoint | Attach any relevant documents or photos
text | 8bf8049f-541c-5dec-a91a-e0076e222535 |  | textbox | ITP No.
text | 6bfd893c-8d8d-5ecc-ab89-7569a6830e80 |  | textbox | Revision No. & Date
text | eeb63688-9f05-5c73-a702-30ef7122e65b |  | textbox | Prepared By
text | c1c7332d-f454-546c-8560-c98b53871379 |  | textbox | Reviewed By
text | 48f012bc-8129-5126-b904-84b3ac897257 |  | textbox | Approved By
text | 5bb3b702-a603-5f36-bbc4-ec402dfa85ce |  | textbox | CIDD Alerts
checkpoint-group | 18a89818-094e-45c0-8cca-568065b771c3 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | c1262e0b-c973-4c1d-bc11-e07c2c899a8f |  | checkpoint | Enviro Shield
label | 53263a52-18c8-5f70-b582-b40870dd76e2 |  | note | Records - Time stamped photograph
select | 271a82c3-ba2c-59a8-88ad-13c49248ebe5 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 3a87b3bb-94d4-49ba-83a0-cacbd203e380 |  | checkpoint | Enviro Flex FC/ Sika Flex FC
label | 26ea71b6-15e8-598c-a5a2-8c3c08715d7b |  | note | Records - Time stamped photograph
select | e0a7173d-00c6-55bf-a7b1-adaf59259b49 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 14e02b2a-520a-4f01-aaa8-913a9a46f990 |  | checkpoint | Enviro 200P Ultra
label | f9b49a28-d79e-5e12-bebf-1daa9d12ca59 |  | note | Records - Time stamped photograph
select | 4b86d52d-a854-5430-81b6-ca16c94c2e63 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | cdff692a-af24-475e-9e39-68d4cb6020b4 |  | checkpoint | Site engineer/foreman batch inspection review
holdpoint | 86b4416c-027e-40f9-a64c-a4b61ef6704c |  | signoff | site engineer/foreman sign off
checkpoint-group | 6ecf9d82-5419-496a-a2da-66be8901b88e |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 7f857e7f-0a4b-488d-b596-1481d691849d |  | checkpoint | Samples Submitted
label | 6fb8cb5c-35b8-5d2e-ba27-b05314b4d1ba |  | note | Submit samples for approval as per Specific Material Requirements.
label | c0c39b02-161d-5df7-a29a-cf57e07e24f2 |  | note | Sample Approval Ref.
holdpoint | 9e72fdc7-e440-4fab-8cb4-c2a0c5dab5d3 |  | signoff | Hold Point (Mandatory) - Subcontractor Contracts Admin inspection sign off
checkpoint-status | 97617cd5-86a4-46ad-844a-eb19b66f6be0 |  | checkpoint | First Of Type Inspection
label | f37a3c24-5897-5221-a50c-8ee4816e43bb |  | note | First of type of inspection conducted by builder prior to commencment of works taking place.
label | b8446ec8-2453-5e57-825d-f40e1f682417 |  | note | Records - Site Engineer/ Foreman Confirmation
holdpoint | 12397408-5a37-49db-b9f4-6dcd58f8743c |  | signoff | Hold Point (Mandatory) - Site engineer/ foreman first of type inspection sign off
checkpoint-status | 31711a40-ef81-4a9b-8273-f2082d99f08f |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 25367a9f-2d2d-57cc-851a-193cf265331f |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | c455e862-ac3a-53fc-9ee2-d2fcd06cce6f |  | note | Records - Time stamped photograph
select | ed88965e-ea13-5ccd-bdf2-adce640324a4 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 134d3893-5145-458a-b9ee-93c922a32d58 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 3f502ed6-dad8-47c9-9f74-e8c669bc5e8d |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 71885b43-ccc4-58c3-9daa-87163637ed18 |  | note | Obtain clearance for work initiation.
label | ebf2494d-6d01-505e-8d20-877a93fbe849 |  | note | Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes.
label | 09615970-4504-5e54-95ec-806949bc7f7e |  | note | Patching products must be fully cured as per PDS before applying the membrane.
label | b1113e38-7052-5b6e-8b26-820bad48eeb1 |  | note | Records - Time stamped photograph
select | f82dcb2e-48ec-5892-b09d-c2bb69de848b |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 222076ab-f9bf-4000-91fa-45fcbeb7346a |  | signoff | Subcontractor inspection sign off
checkpoint-status | ba1e3514-beb1-4af5-bdcc-7859d1751b63 |  | checkpoint | Acceptance of Puddle Flanges - AS3740-2021 Section 4.3.1
label | fc19b574-849d-5240-aaee-8298b6ee29e7 |  | note | All Puddle flanges to be recessed into substrate to finish flush ready for waterproofing.
label | bce6548f-0e0e-5f23-99b3-f28fec2e5cdd |  | note | Records - Time stamped photograph
select | 349a4787-e5d9-5b6c-9300-eaae5dbe4f4b |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 9cde006a-50b8-4339-b7a1-eedc076d6091 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 872a8849-ff6d-455e-a1bf-1fcbe4f8bbdd |  | checkpoint | Acceptance of wall - AS3740- 2021 Section 4.4.4
label | 1197488a-48a4-53f2-969b-c194e26cf5fd |  | note | FC sheeting to have max 6mm gap at floor/wall junction.
label | ed763f59-8576-53fc-bd05-1a340f673c21 |  | note | Sheets to be set with manufacturers base coat, including all nails, penetrations and corners.
label | d853df90-9e03-529a-a2a5-108497cd04c0 |  | note | Mortar in block work needs to be a flush joint, smooth and level with the blocks, no blow outs of mortar.
label | 86e9df03-c6da-5d21-bbf2-0061f60732ab |  | note | Records - Time stamped photograph
select | 52e348d9-83f7-51a4-854b-9e04da35b6a1 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 5ff781a3-019f-42ed-9564-f16f560c114c |  | signoff | Subcontractor inspection sign off
checkpoint-status | 577a4d5f-4d76-4a3a-b182-1613d88fee14 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3
label | 44c83cb6-4e10-5d96-9588-94222c2456c2 |  | note | Builder to confirm compliant falls; minimum 1-100 falls and 1-80 in Showers
label | 927a9cfb-2daa-528c-8b76-c2861b792f61 |  | note | Records - Site Engineer/ Foreman Confirmation
holdpoint | 28e41260-51d9-478a-84f1-6c3bfeb3968d |  | signoff | Hold Point (Mandatory) - work not to proceed without approval
checkpoint-status | c5b0e436-ac10-4d0d-8497-eeea65710e53 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | cba16a60-1dbb-5e11-9ce6-11b4cddd4de4 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 9172796b-0d66-5ed1-992e-844438640298 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | 21ee1e19-aff3-5d87-8506-a0f41962c276 |  | note | Records - Time stamped photograph
select | 0eed3625-0c76-5038-9a64-4bb2a29ab81c |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | bc653a7a-df4a-44e4-a37b-e7045d2bc322 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 21a4449e-6340-4840-8818-c53d3e50047f |  | checkpoint | Site engineer/foreman pre commencement inspection review
holdpoint | 14805d70-54c2-4e33-87c0-47a661f17e67 |  | signoff | Site engineer/ foreman inspection - sign off
checkpoint-group | ec45d6d8-0da9-4ba2-b8d6-ba881360b1ad |  | section | SUBSTRATE PREPERATION - EACH LOCATION
checkpoint-status | 78c39e6b-9df6-41eb-9e3b-73c84a8ab817 |  | checkpoint | Substrate Preperation - AS 4654.2-2012
label | f225dce4-d5ec-5992-934c-a62ad612147a |  | note | Ensure Surface is prepared to receive primer application.
label | dc9d7dc8-4821-5168-89b4-b8adb6fc6f83 |  | note | Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion.
label | 41d5b9f5-d5b1-52ad-a206-62f2bc0ecaf5 |  | note | Achieve CSP2 and CSP3 Concrete finish.
label | 9c24f3e0-cda1-5775-87d3-7dc563e2935b |  | note | Remove all sharp edges including screws, nails and concrete/mortar projection.
label | 8dc785fd-5849-56eb-8f32-dc6f99bf7a28 |  | note | Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | d993e4dc-ba77-5a44-aa47-a9d6fa944cb9 |  | note | Records - Time stamped photograph
select | 1ba7911e-adee-5126-bd5a-ecb62effc4af |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | dfcc5c6c-3e85-4cf6-bba8-5d7e39a3b4cd |  | signoff | Subcontractor inspection sign off
checkpoint-status | 991ac85e-a765-41ac-8dd2-afaf625f57ce |  | checkpoint | Site engineer/foreman substrate preperation inspection review
holdpoint | 37798ea5-254f-4f6f-94a9-6810dcc34e98 |  | signoff | Site Engineer/Foreman Inspection sign off
checkpoint-group | 753f36de-aa2b-4a6f-b930-b74e4ad872e5 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | 1762305a-5068-4f26-b21b-89fefad6f373 |  | checkpoint | Moisture Content - Enviro Shield Product TDS
label | 5128d1a0-b280-54d1-a6c4-153042df69ce |  | note | Check Moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 80014ebe-8c44-52bd-9468-2678ee4dbe6d |  | note | Records - Time stamped photograph
select | 5f74b39e-e2ad-57bf-b651-a8b905f99e30 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | d6824db3-2b34-40d0-8d9c-a54f774456b2 |  | signoff | Subcontractor inspection sign off
checkpoint-status | be598f0e-e464-4bdf-9c80-ded2a5509554 |  | checkpoint | Weather/RH - Enviro Shield Product TDS
label | ff917656-8691-5a8a-8d1e-f25ec26e0c43 |  | note | Apply within 10-35°C
label | 23b195ec-a596-567d-ba6a-72ba1b45aae5 |  | note | RH must be 0-85%
label | e900bdd0-bffa-571b-bf95-dd1e7ade7b0e |  | note | Screenshot - Temperature and weather forecast
select | 1351a434-3e3c-5ac7-aa38-d500f4d0e295 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | fb11c2f1-0b7e-4143-95cd-f3e5c8ed81fe |  | checkpoint | Mixing - Enviro Shield Product TDS
label | 99cbb6a2-d3be-5d99-839d-e381e2b59df5 |  | note | Add Enviro Shield Part B (grey liquid hardener) to the Enviro Shield Part A (base Thoroughly mix with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 8ea85e55-9c4a-5e5b-afa6-9da24c2e0e7e |  | note | Mix for 5 minutes or until uniform.
label | 3d03b4a1-dbb2-5963-aafc-68db1e4b55e3 |  | note | Allow to stand 5 minutes after mixing and then mix again for a minute.
select | 4386869a-84f2-5119-8905-5527acf7977a |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 147f541d-6a05-4c19-8741-a9c9b45f50d6 |  | checkpoint | Application - Enviro Shield Product TDS
label | ed461660-98b1-5c6e-b8a3-df83a69e6ed0 |  | note | Apply primer using a brush or roller.
label | dab92e41-45a2-5aca-bbb9-238693b3d0f8 |  | note | Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface.
label | 01e324e7-4188-5adc-9d73-a1a4c58c8a4d |  | note | Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | c71d6db1-6660-5517-a2eb-f18865ddb45c |  | note | Records - Time stamped photograph
select | 9fcbc418-29e7-51ad-bf9a-9489a4ad6c82 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | cf1df4ad-fa88-4d01-8504-aafa67e96cb7 |  | signoff | Subcontractor inspection sign off
checkpoint-status | bf56614c-a0ad-4bdb-a8a9-3335bab3382a |  | checkpoint | Site Engineer/foreman Priming Inspection Review
holdpoint | 4e3d8f9c-fa81-4560-bdac-4a13ae481d64 |  | signoff | Site Engineer/Foreman Inspection sign off
checkpoint-group | 28c22283-c0d5-4225-b261-b3d0900ede0a |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 607c0f59-6f70-4493-b8ad-1619543fbf60 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | fa66b444-1ba3-511e-b588-5c24d6453241 |  | note | Apply Enviro Flex FC/compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints.
label | 2380358e-85c8-5810-ab0a-2b0f381aafc5 |  | note | This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas.
label | 810c4307-958e-52d3-b0c2-92d3f66a7d5e |  | note | Allow to be tack free prior to over coating with membrane coats.
label | 2ae9b72f-707e-5508-af5c-abd23b025c78 |  | note | Records - Time stamped photograph
label | aee8fb86-4601-5107-9b2c-e9546ba5cc3b |  | note | Records - Thickness with fillet gauge
select | b2b8cfcc-f9c8-5533-b89b-a8ed256ad68e |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | dc655379-054e-4d63-aa3e-ab01ad6ce2e0 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 63288aa3-0f32-45e0-b082-a2f98a091977 |  | checkpoint | Site Engineer/foreman bond breaker inspection review
holdpoint | fa65e877-271b-4790-9785-44710d1cdc2e |  | signoff | Site Engineer/Foreman bond breaker inspection sign off
checkpoint-group | 5fc12286-cfe2-42ba-ab8d-7c7416b6fde7 |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | 84deea33-fe6e-49ca-b5e5-a0a8aeb1cdb0 |  | checkpoint | Weather/RH - 200P Ultra Product TDS
label | 494e7477-e8ed-58f3-8990-456e140db13b |  | note | Apply within 10-35°C
label | a206edf2-0156-5d45-bc18-29f85557f0c8 |  | note | RH must be 0-85%
label | f6dc4358-d526-56b7-adf0-b47910235ee6 |  | note | Screenshot - Temperature and weather forecast
select | e5ab4f1a-e383-5a35-9cb1-92fb8f15834c |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 8f5f3ad5-468c-4eb2-b777-54a330f1ab7a |  | checkpoint | Mixing - 200P Ultra Product TDS
label | 095ae891-4185-5c4e-a005-97add4bacda7 |  | note | • 200P Ultra should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
select | e139d0c5-7701-559d-8763-c6edc75950c3 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 67ed197d-ca1d-478b-9e53-e6e924703208 |  | checkpoint | Application - 200P Ultra Product TDS
label | dd5e087a-1dc0-5a79-a7c8-bc6ab85b9b41 |  | note | • 200P Ultra to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | 95dae775-74ac-5cc5-b2b8-829462a91be6 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 3c008728-fd12-5f50-b095-c9bbdff793d1 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | f9336a01-1bb9-5bb7-8ba4-4d6cd2675d04 |  | note | Records - time stamped photograph
select | 59b0ab16-8223-59df-b888-4a2b7bd61af4 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | c032cfc5-14c4-4166-b3a3-7893ca73d0cc |  | checkpoint | Subcontractor first base coat inspection review
holdpoint | bdf1963c-425a-4ea9-8e81-3771eb44425d |  | signoff | Subcontractor inspection sign off
checkpoint-status | 95712b31-f2bd-4abe-bfca-f45778b6b6fd |  | checkpoint | Site Engineer/foreman first base coat inspection review
holdpoint | be3e1a71-a31e-454e-b61e-ddb497346644 |  | signoff | Site Engineer/foreman base coat inspection sign off
checkpoint-group | f185fef0-568f-4561-8961-4745c31d5adb |  | section | SECOND BASE COAT- EACH LOCATION
checkpoint-status | 8b8b71aa-2324-40fe-8cce-c39a161cc3d1 |  | checkpoint | Weather/RH - 200P Ultra Product TDS
label | 5638c458-1e2e-55f0-a86a-92ab145f5a5c |  | note | Apply within 10-35°C
label | 06a3f156-d5c1-5f4c-b215-24c614e5b454 |  | note | RH must be 0-85%
label | 7e7799c6-4d43-5071-81f0-64294cca4daa |  | note | Screenshot - Temperature and weather forecast
select | 9ce59582-40b9-58ae-9074-226f61bb4aef |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 891da508-b795-4cc9-bb96-0f35f5f59eda |  | checkpoint | Mixing - 200P Ultra Product TDS
label | 2dbef502-84af-572b-907b-3f541afa32de |  | note | 200P Ultra should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
select | e90cdb40-7779-5bb5-ae99-75fb8023621b |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | e23289a2-2ed3-4b76-b98a-1ec36df40fdf |  | checkpoint | Application - 200P Ultra Product TDS
label | 84e0a3d4-96c4-547d-bc0f-e4cfd1945384 |  | note | 200P Ultra to be applied by roller Horizontally on substrate and terminating min 150mm with brush.
label | 43b05fac-03e8-5078-a9f7-afcd024c751c |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | d4f3fa87-8bfd-502e-a327-1c84d0d7fb04 |  | note | Allow membrane to cure for 3 days prior to testing.
label | c2867e4e-5cad-5b8d-afc7-005fcd203ca5 |  | note | Records - time stamped photograph
select | ab5a31b4-38e7-5c08-a25e-b6922227e6c7 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | f879a727-b865-4c0d-95be-caa4e761fa59 |  | checkpoint | Subcontractor second base coat inspection review
holdpoint | 302fc9ff-59a7-407c-bc2d-6885cc7efd2a |  | signoff | Subcontractor inspection sign off
checkpoint-status | 2c0eb71a-7776-4478-8323-5d19e6f67543 |  | checkpoint | Site Engineer/foreman second base coat inspection review
holdpoint | 5d6e957d-2083-4636-be34-2f381016d8ff |  | signoff | Site Engineer/foreman base coat inspection sign off
checkpoint-group | 74f0d470-906e-4288-a233-05a0a6d08a63 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | a2247d59-f70b-4718-bb47-fa212e5ee2fc |  | checkpoint | Inspection
label | 386ea325-c873-5cd9-9b24-07e9f7c16588 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | 033880c4-7081-5c47-a240-f814964b7437 |  | note | Records - time stamped photograph
select | 26178662-febd-5007-9cfa-a7e50e4c16f8 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 34ad6126-def1-4d4a-928a-07e272d2d487 |  | signoff | Subcontractor inspection sign off
checkpoint-status | d3ed2d04-44e1-49c0-b074-febcd2656cd4 |  | checkpoint | Thickness Testing - Delfasco Positector
label | 532bd01c-8ec4-59cc-89ce-509fba7f7255 |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | 9b2db5b5-c147-5b51-a3a0-00e5218652ee |  | note | Records - time stamped photograph
select | 62a72c48-a560-5767-add3-39d7520ad8b8 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 7388b4e2-06cf-400d-932b-fb7b3720b2da |  | signoff | Subcontractor inspection sign off
checkpoint-status | 1420a64b-763d-45cf-acba-feed0cd2f657 |  | checkpoint | Flood Testing
label | ef4beef2-d953-5420-bffe-9a837e69e95b |  | note | Mark water level and conduct a 24 hour flood test for internal wet areas
label | faca497c-f9bd-506e-bf34-4d98088bbb08 |  | note | Records - time stamped photograph
select | a38ce732-b95e-53a9-829d-727e455d2b5f |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 4876ae7a-e0e2-4aeb-b0a7-0d5d965d4b7f |  | signoff | Subcontractor inspection sign off
checkpoint-status | 76272cad-9788-40b9-a722-65342e8b0528 |  | checkpoint | Site Engineer/foreman QA inspection review
holdpoint | d5e7b7c5-b69e-4f13-bcd5-5682345759a1 |  | signoff | Site Engineer/foreman base coat inspection sign off
checklist-sectioned | f767e606-38b0-4e58-942c-25a8e595d53b |  | checklist | Enviro Clad V1.1 |  |  |  |  | Yes | Enviro Clad V1.1 | 118bc846-b640-4a34-b7ab-a3edf715cd2f
checkpoint-group | e48511b8-c97e-459d-8333-4dafb979a89c |  | section | DETAILS
checkpoint-status | ee7a7215-d9cd-42da-9099-a421e81da91a |  | checkpoint | Attach any relevant documents or photos
text | c565bdcd-48ae-5f2d-8e7b-8945370c0fea |  | textbox | ITP No.
text | e5cc0123-10f5-5cf1-8c5e-18a7aa06eff3 |  | textbox | Revision No. & Date
text | b5145835-9229-53c8-beb1-69b3f91d6daa |  | textbox | Prepared By
text | 361565f1-0ed7-5735-b462-96cf82a76ccb |  | textbox | Reviewed By
text | 281ba57d-6564-56d0-8f56-deb87678e531 |  | textbox | Approved By
text | ed65260f-4b63-5415-8ebe-21bc406a77ff |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | bcf109c5-da6e-4286-8b0d-ac521d1f5661 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 72529bf6-3c4b-4111-af42-00634c8153d2 |  | checkpoint | Enviro Shield
label | 79091be9-762e-5892-968d-b18dbae3435d |  | note | Records - Photograph
label | a9b47656-3d99-55fb-94cb-00aa8c8f19b4 |  | note | Surveillance point
checkpoint-status | 38a53aa1-2ca0-47f3-88d2-c09582f4ba48 |  | checkpoint | Enviro Flex FC/ Sika Flex FC
label | 3d938343-8ebd-5537-b7e4-6a0b13f39a83 |  | note | Records - Photograph
label | f54d3e0e-5740-57ad-ab48-2112d433ced0 |  | note | Surveillance point
checkpoint-status | 50bae88d-130e-4624-a194-4e35fa202139 |  | checkpoint | Enviro Clad
label | 2a4c8b79-9064-5ec8-bfe0-dfdc24c405af |  | note | Records - Photograph
label | 75710360-8010-552b-bb92-6c5380001c10 |  | note | Surveillance point
checkpoint-group | ca3a5b69-7479-4044-8af1-79e68d6db58e |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 2a7b1a6c-48d0-497d-9897-d4cb4476c6ef |  | checkpoint | Sample Submissions
label | fce9c24b-d741-5d80-88f5-9d2770298d66 |  | note | Submit samples for approval as per Specific Material Requirements.
label | abef6f43-58de-50cd-8866-5c7774d8654f |  | note | Record Submissions
checkpoint-status | ff6eae30-d2e3-4a48-8dce-e3e304bdff77 |  | checkpoint | First Of Type Inspection
label | 44826ac8-09d0-5b76-960f-6b6619f24251 |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | e8258609-0d7a-5b4f-a39b-41bb0e32d208 |  | note | Record Submissions
checkpoint-status | 2a07d1fd-5a22-43fc-890b-694409a295ef |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 6be7163b-3c93-5c6e-bdc4-9f8f0624c2f5 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 216eed52-5e73-5e6e-8c58-0ea307af1a62 |  | note | Records - Photograph
label | f32dcce0-65cb-5d73-b1ba-dc5469393dce |  | note | Witness Point
checkpoint-status | 598a705c-be95-4be6-a03a-5839adefafe4 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 1020da57-55a2-5a8a-b9b3-2b4a1db653d7 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | 7df3e753-e48a-5943-8e32-32624e3378e7 |  | note | Records - Photograph
label | da8119ad-7a89-5a70-89ca-76d61bdf1486 |  | note | Witness Point
checkpoint-status | 6eff1e1d-f79b-480c-b2a5-6e30ec3954e6 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | ae2f4bef-befd-5a38-88ec-176134367574 |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | 8b17a834-083e-57b5-b3f1-14a451fe4dad |  | note | Hold Point
checkpoint-status | a42720e9-613c-4f0e-8d55-c7c3517bae48 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | fb0d972a-c926-517d-9c84-9bf15a55df9e |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 62322e86-a208-574d-9f21-eded4ca33a94 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | ad6c9386-0ff3-5102-827f-4e96dd9b38cd |  | note | Records - Photograph
label | fc619b00-01bb-5f53-882c-b64ffaad6720 |  | note | Witness Point
checkpoint-group | 91a46f9f-f090-4465-bce6-bc24ce2645e6 |  | section | SUBSTRATE PREPARATION - EACH LOCATION
checkpoint-status | 4fba137c-8f2a-4df3-9d4f-b67c9f384a80 |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | 051eb147-8b3e-53f9-baae-28897c5e0b33 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | d7ebf829-eed3-5625-b99c-3e6db77db40e |  | note | Records - Photograph
label | 71d4b43e-e294-5db1-b769-a10b85fcdff7 |  | note | Witness Point
checkpoint-group | 56b27464-55d9-4465-a36d-c3ce04533be2 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | adfed39f-53b3-4776-b31a-a3d30f6c2eef |  | checkpoint | Moisture Content - Enviro Shield Product TDS
label | dc483fe5-f9e7-5f72-842d-57a728f70275 |  | note | Check Moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | e10cca0d-0655-533f-af38-e7ed8ad73143 |  | note | Records - Photograph
label | 1a1e4e29-5d8c-5638-b1e3-7470a2e2858a |  | note | Surveillance point
checkpoint-status | 26c0d6c6-8b40-4c0b-a2e4-0ad360e22871 |  | checkpoint | Weather/RH - Enviro Shield Product TDS
label | b0609456-48c7-5a4c-a182-6f3c07c08294 |  | note | Apply within 10-35°C RH must be 0-85%
label | 397d6fbc-ec13-50ae-9122-7e902c64b877 |  | note | Screenshot - Temperature and weather forecast
label | eaaa5960-46d3-549f-85ef-43703cd66a3e |  | note | Witness Point
checkpoint-status | 4f4edf17-4313-4ca8-b182-fffd1e725204 |  | checkpoint | Mixing - Enviro Shield Product TDS
label | 893d0100-1a70-5f84-aad3-cca558a75796 |  | note | Add Enviro Shield Part B (grey liquid hardener) to the Enviro Shield Part A (base Thoroughly mix with a mechanical mixer at low speed (less than 400 RPM) prior to application. Mix for 5 minutes or until uniform. Allow to stand 5 minutes after mixing and then mix again for a minute.
label | 1a959328-94d6-5307-a8ce-cf6e848fca87 |  | note | Witness Point
checkpoint-status | 451c6c71-75c7-4352-bbfb-8e3121473915 |  | checkpoint | Application - Enviro Shield Product TDS
label | d7531912-f258-54f7-a560-9c83a66f5168 |  | note | Apply primer using a brush or roller.
label | f8493757-d73f-5ab5-9886-c6d07ba381a5 |  | note | Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface.
label | 97e4c4d2-2cc5-591f-a1a2-d81ac3356f51 |  | note | Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 333f67f5-7c44-5029-b773-182e7c423d58 |  | note | Records - Photograph
label | c2ed88cb-d479-5287-b7aa-4b98321a23e2 |  | note | Witness Point
checkpoint-group | e18ff51f-94ea-4558-9541-cc6dac1f7ff5 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 2d522956-5019-4965-a909-a3b23730fea3 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 2a31523c-20ca-5a41-8984-95d57707d17a |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | 83c0334d-f07d-5f48-8a12-c4764d617d77 |  | note | Records - Photograph
label | 00f7cede-7e29-5abf-b597-a7c3f8247db4 |  | note | Records - Thickness testing with fillet gauge
label | 60942b0e-82d3-5909-b107-003ba1acd0eb |  | note | Witness Point
checkpoint-group | 673db756-3dc9-4ffb-ab7f-b4d1c9df8435 |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | 79b5003d-4cbc-452e-a113-4406b0d0da44 |  | checkpoint | Weather/RH - Enviro Clad Product TDS
label | 6b08b4e1-a4bf-5b9f-95d8-676dea1c6ee3 |  | note | Apply within 10-35°C RH must be 0-85%
label | a7c8853b-c933-51af-925d-366efc54cf1e |  | note | Screenshot - Temperature and weather forecast
label | ddfa8381-5950-574c-9128-3db1df385245 |  | note | Surveillance point
checkpoint-status | c055e6ef-e7db-4fd5-bcd5-22ad7444847b |  | checkpoint | Mixing - Enviro Clad Product TDS
label | 7ad3b2d5-5bef-5e4a-b540-8cdbd0a4446e |  | note | • Enviro Clad should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 06046f76-c1ef-569d-baaa-5ac975b58c88 |  | note | Witness Point
checkpoint-status | 10e11342-cb28-41b4-b737-f11c8befea76 |  | checkpoint | Application - Enviro Clad Product TDS
label | 1b8d58e6-a353-5b6b-ae96-b72aff10b93e |  | note | • Enviro Clad to be applied by roller on substrate and detailed with a brush
label | e6d9c669-4142-53f9-aa3a-4ef410b9a5db |  | note | Coating to achieve a wet film thickness of 600 microns
label | 818f377e-f52f-5a26-b567-11899f7df202 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | cd1993bd-c4a5-52d6-83a2-295ff2fec970 |  | note | Records - Photograph
label | 306a526c-07cd-5ae9-8ec5-95ffb17f1491 |  | note | Witness Point
checkpoint-group | 148f2c5c-b560-4cc6-b479-e6892e69d614 |  | section | SECOND BASE COAT- EACH LOCATION
checkpoint-status | 2d150a08-c970-44be-83ee-c7fb7a281ddd |  | checkpoint | Weather/RH - Enviro Clad Product TDS
label | b87b07a3-d362-5ef8-91d8-c1d4119a9a13 |  | note | Apply within 10-35°C RH must be 0-85%
label | b008183a-76ed-5910-ba6f-c988859d6c82 |  | note | Screenshot - Temperature and weather forecast
label | d444cb66-fe3b-5b78-94df-76685071825a |  | note | Surveillance point
checkpoint-status | 82903022-de74-46f6-8a6d-e54856cb36a5 |  | checkpoint | Mixing - Enviro Clad Product TDS
label | fb0e6d77-0275-5bd2-8f78-467a943b6cec |  | note | • Enviro Clad should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 9e04c7f1-585a-5c0e-a33a-41f757f64f23 |  | note | Witness Point
checkpoint-status | de25cabf-f4e2-49c5-9d0d-f5cc9868f492 |  | checkpoint | Application - Enviro Clad Product TDS
label | 419120df-0462-592e-9cfa-601388cd558f |  | note | • Enviro Clad to be applied by roller on substrate and detailed with a brush
label | db7ee189-77b4-50c1-8857-d905eb0ac03a |  | note | Coating to achieve a wet film thickness of 600 microns
label | 0b3fd688-d304-5514-9c7a-2a31ddf0b9a6 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | d673e2c1-6150-5320-bdd4-0b02d2916cbe |  | note | Records - Photograph
label | b197ab90-0fc0-59ae-98e6-55cf5b9f674f |  | note | Witness Point
checkpoint-group | 5c767ccc-4d19-4f2f-b3eb-30509a61c529 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 42ea8388-0906-492f-b9d7-e424b5b8b534 |  | checkpoint | Inspection
label | 5ab1160f-3fd6-56e6-ab3d-2e322910a427 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | fb402d23-2000-5e84-a9b2-e99c3f0a4dd5 |  | note | Records - Photograph
label | d0ad581e-645d-5ca3-88d5-428a237449e3 |  | note | Witness Point
checkpoint-status | db43e6b9-5077-430a-b069-ee394a574dc8 |  | checkpoint | Thickness Testing - Delfasco Positector
label | a235206e-a120-5099-a1d2-9c56e6293a06 |  | note | Thickness testing of application to the recommended DFT of 1.5mm to manufacturers instructions.( 1 test per 10m2)
label | 970b083c-0c39-5f7f-8551-4aea15e5ae7a |  | note | Records - Photograph
label | 6d743b40-baf8-50f6-9e16-51c16e274c57 |  | note | Hold Point
checkpoint-group | 1c2e4b7d-cabb-40ea-9a5a-6df19e9331ad |  | section | SIGN OFFS
checkpoint-status | e6715d84-0f84-43c9-bd08-66fd989da33b |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 9788cd87-2d95-4c62-846a-3d6292b0332d |  | signoff | Subcontractor inspection sign off
checkpoint-status | 5885ca53-41ac-4428-ad94-f963e803f89c |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | 3ceccb42-df73-48d3-a29d-777c56b82c5f |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | da296e4d-9923-4b86-8bb4-ca2104749afc |  | checklist | Enviro 700X V1.0 |  |  |  |  | Yes | Enviro 700X V1.0 | 14eb502d-3f68-4f61-a6ce-55640a8f055f
checkpoint-group | cca36928-58e7-411b-a3f2-f0521ced9ab4 |  | section | DETAILS
checkpoint-status | 20bd484f-46bd-46de-98ca-424e0ba5e415 |  | checkpoint | Attach any relevant documents or photos
text | 87e65c91-7b68-5310-af73-b26fbee25f6a |  | textbox | ITP No.
text | 34b9e350-ee60-58dc-b215-b59fdfb02ade |  | textbox | Revision No. & Date
text | e2ce1d94-f00a-5e0e-8819-b5d5427b949e |  | textbox | Prepared By
text | b43cea91-2f2a-5eb1-a61c-6a38d17cc87b |  | textbox | Reviewed By
text | ecbdef1b-a5c2-501a-9fa4-4ed7c6e6b59b |  | textbox | Approved By
text | e1a0f824-2969-5c83-a852-b28da724e188 |  | textbox | CIDD Alerts
checkpoint-group | 41a2b269-0f71-4852-b754-3a20de7786a6 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 1cee78a9-8683-449c-9725-5140476c1b9a |  | checkpoint | Enviro Flex FC/ Sika Flex Pro
label | b852c9d7-9487-526d-aecf-67923841253f |  | note | Records - Time stamped photograph
select | 92a04eb9-c17b-5bdf-8022-2deb6de2228f |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | ceddf465-64ff-47ea-b44b-a6acb173585a |  | checkpoint | Enviro B-LV
label | 4e04ddd2-ca14-5b8f-8ba9-db3533e68f6d |  | note | Records - Time stamped photograph
select | 568eb1be-aef9-51e5-9883-18973b2aad2a |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | b24dfdaa-1824-4679-90df-58033492dd8a |  | checkpoint | Enviro 700X
label | 48a8f90b-1e8a-542c-b510-a46aae08c829 |  | note | Records - Time stamped photograph
select | f3455359-ef68-559d-b27d-98adf7d63832 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 2d4750ee-3f29-451e-8fce-94dcfac8c47c |  | checkpoint | Site engineer/foreman batch inspection review
holdpoint | 80967018-7fc1-4bba-93eb-fe446ee95d16 |  | signoff | site engineer/foreman sign off
checkpoint-group | 3e9737f5-77c9-4512-b5bf-540104b37cc8 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 07cf1e1e-8267-4fbc-82de-e5cc359b9d2f |  | checkpoint | Samples Submitted
label | d3c6bdec-f061-5750-b0e8-1d3d94a95ca6 |  | note | Submit samples for approval as per Specific Material Requirements.
label | 5171d4c8-87d7-5f94-a9f9-8bcc766d5133 |  | note | Records - Subcontractor Contracts Admin Confirmation
label | a80a15fb-fc9e-5770-8bbe-63eb3e4f682a |  | note | Sample Approval Ref
holdpoint | a52ebbb4-4fcf-4d94-b225-e10c59956a8b |  | signoff | Hold Point (Mandatory) - Subcontractor Contracts Admin inspection sign off
checkpoint-status | 9847345c-9a38-4d97-952a-b6a271c23f57 |  | checkpoint | First Of Type Inspection
label | 5d69d16f-5e6a-52dc-94d2-d709e77d58ca |  | note | First of type of inspection conducted by builder prior to commencment of works taking place.
label | f58c83de-8fee-53bf-9d6c-139c27606883 |  | note | Records - Site Engineer/ Foreman Confirmation
holdpoint | 6d17f78b-6dbf-4d06-91d9-63f3428dd73a |  | signoff | Hold Point (Mandatory) - Site engineer/ foreman first of type inspection sign off
checkpoint-status | 08061f91-517b-4017-9c3c-bd5d1b1af382 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 7c6ad560-b277-5fb7-b884-a089f5607446 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 7a804f34-ea05-56b2-9a71-fd77740fe9cd |  | note | Records - Time stamped photograph
select | d4485d89-6953-5ca9-a7aa-274a0b24ed05 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 145b4674-bb8e-4155-83e5-cec726d47435 |  | signoff | Subcontractor inspection sign off
checkpoint-status | b413b80f-a45e-41ac-a514-04c3f29b7171 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 7cce6fc1-23e3-524a-ad7d-80448c2cdd56 |  | note | Obtain clearance for work initiation.
label | 4c493887-9b9d-5f69-8e33-d512c5b987ad |  | note | Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes.
label | 5f5deb02-a087-5a76-89af-04c154266e35 |  | note | Patching products must be fully cured as per PDS before applying the membrane.
label | ec338a3f-68f5-5aff-b082-8f09ba47ed6a |  | note | Records - Time stamped photograph
select | d4a10c0c-8892-59a7-82e4-d4815a932a94 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | c3787631-89c8-485c-9fdf-698f80d8dd7d |  | signoff | Subcontractor inspection sign off
checkpoint-status | 51b1aa7e-a757-44ca-a167-ba20be7d16d6 |  | checkpoint | Acceptance of Puddle Flanges - AS3740-2021 Section 4.3.1
label | 79e20cd7-5a28-51a0-9770-eb7a9b7f02c1 |  | note | All Puddle flanges to be recessed into substrate to finish flush ready for waterproofing.
label | 9ae84ce0-a1bd-50dc-847d-88143b1fdb6b |  | note | Records - Time stamped photograph
select | 96cc545f-e2ab-5f98-bd6b-a4e6e6d34e5e |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 11b6b37f-69f7-4496-b508-f765fab12a3a |  | signoff | Subcontractor inspection sign off
checkpoint-status | dd05356e-e3fb-47f5-b0d4-bdc93c87bc5e |  | checkpoint | Acceptance of wall - AS3740- 2021 Section 4.4.4
label | 21af6f3b-2bd4-52ef-b255-b0287eddd939 |  | note | FC sheeting to have max 6mm gap at floor/wall junction.
label | 18e10f81-adf7-55b7-9ffb-a8f07594cf7f |  | note | Sheets to be set with manufacturers base coat, including all nails, penetrations and corners.
label | e146befd-01f4-5925-b8ba-7903a094af85 |  | note | Mortar in block work needs to be a flush joint, smooth and level with the blocks, no blow outs of mortar.
label | 5c4f1565-8d02-5e3d-bd81-7433f18b2ed0 |  | note | Records - Time stamped photograph
select | 4bbbae17-bdb9-5a53-93ff-7472e37fb506 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | aaee1d0e-8f42-4d3c-9ad7-b2f66d4c85be |  | signoff | Subcontractor inspection sign off
checkpoint-status | b80e14f3-2030-4891-b63f-b856ecc8fedb |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3
label | c96ebdce-02fb-57a6-936c-ec91012ccfa6 |  | note | Builder to confirm compliant falls; minimum 1-100 falls and 1-80 in Showers
label | dc7ad5a2-a3e0-5726-9343-d092c1044d45 |  | note | Records - Site Engineer/ Foreman Confirmation
holdpoint | 179126ce-182c-4dfe-bc10-b3b1926624f9 |  | signoff | Hold Point (Mandatory) - work not to proceed without approval
checkpoint-status | 3b51c325-08b8-42ee-8801-bfda95a47530 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | e3ae8f7b-68e1-58b4-a6fa-f0c34ad2a092 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 47f440d9-d7c9-563d-bc6b-fd9b97cf6a73 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | d36f7f88-98e3-58a3-84bf-e55400817330 |  | note | Records - Time stamped photograph
select | 1dbbc85f-79fa-58e5-9565-24f3c923fd34 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | af247760-c4bd-4323-bfbe-6eb56d93c714 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 3b81069c-3906-438f-8a75-b5c474da6127 |  | checkpoint | Site engineer/foreman pre commencement inspection review
holdpoint | d6024451-ffe9-40b5-816d-286ec158ba0e |  | signoff | Site engineer/ foreman inspection - sign off
checkpoint-group | 07ba8b07-c803-4b9d-88f0-ba2b1a9f0433 |  | section | SUBSTRATE PREPERATION: AS 4654.2-2012
checkpoint-status | 413aab91-325f-4aa5-9ac3-2de22cc53146 |  | checkpoint | Substrate Preperation - AS 4654.2-2012
label | 5102c300-d540-524e-bd61-aebacbfee632 |  | note | Ensure Surface is prepared to receive primer application.
label | 93c40def-de53-5b8c-9e41-a4125a1866bf |  | note | Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion.
label | b4d47da4-c744-54ec-804f-8a28b92f6c7a |  | note | Achieve CSP2 and CSP3 Concrete finish.
label | bb031dd4-c371-588a-af4d-166530646ed8 |  | note | Remove all sharp edges including screws, nails and concrete/mortar projection.
label | 7f1523a8-6b85-565e-a4f9-c154f0278539 |  | note | Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 9136c5de-abfa-5a95-9c93-b1b4ba87875c |  | note | Records - Time stamped photograph
select | c3bbaf25-a36b-598f-b8f1-8b63b2dd497a |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | f0e8d217-a398-48cc-b8df-63969f8f30fb |  | signoff | Subcontractor inspection sign off
checkpoint-status | 43f91aba-cfe6-4a00-bb48-b0201d163567 |  | checkpoint | Site engineer/foreman substrate preperation inspection review
label | 54ad968b-bce5-5d45-84c6-398fd8a1a6d6 |  | note | Ensure Surface is prepared to receive primer application.
label | 599a0280-fc44-5e64-8e83-d41ec2efa70f |  | note | Clean Substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion.
label | a596ecca-6cef-5627-b62d-7b553ad5c5b9 |  | note | Achieve CSP2 and CSP3 Concrete finish.
label | a7300891-d03f-5cf2-a8f3-9d9ee6647ec2 |  | note | Remove all sharp edges including screws, nails and concrete/mortar projection.
label | 2153e184-5202-5fe2-ad06-ec246527f124 |  | note | Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
holdpoint | 8da48acf-be27-4a0e-80cc-114d3762038f |  | signoff | Site Engineer/Foreman Inspection sign off
checkpoint-group | b60a2d8b-1bd3-43c2-9754-c67ee0aec010 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | 001fa7aa-960d-459e-bd8c-74ea89cf4c0f |  | checkpoint | Moisture Content - Enviro Epoxy B-LV Product TDS
label | 02b17268-37a0-5920-aada-e9460f3e21de |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | b0696ea1-5627-5ab1-a312-32e3823195b0 |  | note | Records - Time stamped photograph
select | 06ca84e6-5f55-5050-9bdf-e9b2c2fd8d60 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 40ad5b96-9824-4fc0-9231-b2d76bc3f2c7 |  | signoff | Subcontractor inspection sign off
checkpoint-status | e39773db-a386-4711-a3e0-6c21538f7c67 |  | checkpoint | Weather/RH - Enviro Epoxy BL-V Product TDS
label | 9c329917-4192-5080-8258-90f87fc94b73 |  | note | Apply within 5-35°C
label | c5589271-3ac2-58d2-9bf4-21c7c435a2bd |  | note | RH must be 0-85%
label | 17743667-da6b-5517-8368-41b3700f20d0 |  | note | Screenshot - Temperature and weather forecast
select | 3aeba620-dec3-51d6-ba49-d421679710eb |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 6e12925d-e9e9-46e4-953a-985b454b4bff |  | checkpoint | Product Mixing - Enviro Epoxy BL-V Product TDS
label | 0d8d7b4b-bac8-5bd5-82b6-f66334bedb54 |  | note | Mix Part A (12L) and Part B (6L) seperately add Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base.
label | b62f959a-cfbb-5d44-af3f-313d5eabc0bd |  | note | Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached.
label | b7ef0bfd-ecef-5a10-b581-f248a308e11d |  | note | Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
select | f8399b05-a981-5a11-977a-478085550f96 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 7893fdbd-9883-42d3-bb48-6ee4823f9774 |  | checkpoint | Application - Enviro Epoxy BL-V Product TDS
label | 076fa037-58c9-503b-a6a9-cf7f9dde4a7e |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied.
label | 422a6828-7211-57e8-93db-a4511b48afb4 |  | note | Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface
label | 571d3483-b400-553e-b611-24cad8d1f1e4 |  | note | Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 722e7bd3-eeaa-5503-838a-9d402d110502 |  | note | Records - Time stamped photograph
select | 556ef9d9-1792-5586-9ae4-1129a54416ef |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 67383cf9-6415-4561-92d7-87964f3879df |  | signoff | Subcontractor inspection sign off
checkpoint-status | 1df15d49-2adc-4cb6-9d6d-d774c828a1d3 |  | checkpoint | Site Engineer/foreman Priming Inspection Review
holdpoint | 2c20bc2e-a3df-4b8b-bf25-ab78074c9b83 |  | signoff | Site Engineer/Foreman Inspection sign off
checkpoint-group | a07c69ac-f0e2-4746-b282-664ade5dcf26 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 75ebbc64-d5d7-4091-863f-7ead34cbd2e0 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 52fe28ed-202e-520b-aad7-b296e64e7504 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints.
label | b4181ade-57cd-543c-8ea0-190e3fdc2173 |  | note | This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas.
label | cafdc463-59bf-5caa-8da9-f3454a28a414 |  | note | Bond breaker to be tack free prior to coating.
label | c6f58f24-0123-5395-ab94-02c225524ba2 |  | note | Records - Time stamped photograph
label | ebde83f2-510d-56b5-84d2-bcc35714aa11 |  | note | Records - Thickness with fillet gauge
select | 1e0a49ce-e9f8-5dd5-b39d-982adb762968 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 1fe0903c-fb27-4e6e-9122-d8603582e897 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 503ea7de-dfea-4eeb-ab64-b9f8150a18a3 |  | checkpoint | Site Engineer/foreman bond breaker inspection review
holdpoint | 62469d6d-11d1-4bfd-a304-2bddf5d8af86 |  | signoff | Site Engineer/Foreman inspection sign off
checkpoint-group | 98d1ea20-8773-4e6a-8316-239a51b4b647 |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | b11bea22-17e2-478b-9416-b051b5171f12 |  | checkpoint | Weather/RH - 700X Product TDS
label | a425ea8a-e459-518e-9ddd-1cda5263d42c |  | note | Apply within 5-35°C
label | b0e748f5-1629-550d-ad0a-f4d696b50d78 |  | note | RH must be 0-85%
label | ca815c69-225c-5512-8707-09b651012206 |  | note | Screenshot - Temperature and weather forecast
select | 52ebba3a-af27-5851-b05d-6ac9bf6fbf00 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 96456081-66be-4637-8b3a-ad36a55039c0 |  | checkpoint | Product Mixing - 700X Product TDS
label | 187fbbdc-337a-5805-8196-c39fbc229db4 |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 25e7e202-50fa-522c-81d3-6caf97ee899d |  | note | Records - Time stamped photograph
select | c6cc35cf-594f-529a-8f0b-b50bafa52979 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | ccbd79db-b1ae-4268-b23c-5a64c6ee856e |  | checkpoint | Application- 700X Product TDS
label | eea4052d-b7b5-5f98-8fa4-9b6cdc2cd2cd |  | note | • 700X to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | fa94b9ae-a6d5-53a1-ba79-7973769df2d2 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | a2a0a41d-c52c-5937-b3d6-67c29e81062e |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 1597cbfd-3b5d-596a-8d8f-f3de66dc65a2 |  | note | Records - time stamped photograph
select | eb3ab580-3a00-52fd-a1bb-4b86a30ce6ea |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 09f4f95d-78ed-4c95-8c7f-a6dc01c5fa6d |  | checkpoint | Subcontractor first base coat inspection review
holdpoint | 2acccbfb-a6b1-49af-9348-b39aa3084acb |  | signoff | Subcontractor inspection sign off
checkpoint-status | 633fcfee-e350-4adc-a24d-a4b82d52d93f |  | checkpoint | Site Engineer/foreman first base coat inspection review
holdpoint | e075a937-5c6a-4a6e-8af1-af03ccee393a |  | signoff | Site Engineer/foreman inspection sign off
checkpoint-group | 423d4ac0-feab-4e20-887c-1681a86818f7 |  | section | ENVIRO 700X - SECOND COAT
checkpoint-status | ccd5bdfc-de9b-488e-9244-457306b0b0dd |  | checkpoint | Weather/RH - 700X Product TDS
label | 45e0fcfb-1e5e-50a8-aa58-4b1f7618db3f |  | note | Apply within 5-35°C
label | da63e75e-a552-5278-9194-b4d6b883156f |  | note | RH must be 0-85%
label | 49065873-126e-5dc1-9158-3d0d77247b72 |  | note | Screenshot - Temperature and weather forecast
select | 76bca100-0613-5cd5-837a-0dd7ef23411c |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | b3bc42a1-8c6b-48e2-b83c-57c76a53c0f5 |  | checkpoint | Product Mixing - 700X Product TDS
label | 77ab2295-45b6-58b1-8cb0-1bb6df7aaa3a |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 040a1850-061f-5a3f-b995-f9ea5e627b33 |  | note | Records - Time stamped photograph
select | c8819489-e187-590a-b6ec-29cb984dad54 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 9cada90e-f302-4ab8-8473-dfd8327f121f |  | checkpoint | Application- 700X Product TDS
label | dacc2263-eae4-5db3-9125-5d1cb63282f0 |  | note | • 700X to be applied by roller Horizontally on substrate and terminating min 150mm with brush.
label | 618eb451-7925-5fc7-80a7-36c0674d718e |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | c96d8958-7847-5d71-8635-d2479405db6c |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 177a6365-7667-5960-8473-0224c670fd6f |  | note | Records - time stamped photograph
select | 8adaf006-2f99-5581-87f2-dddd10f67060 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-status | 82b03f09-b70d-4960-844b-e4ec2151a8e7 |  | checkpoint | Subcontractor Second base coat inspection review
holdpoint | 4f8c9ad3-49d9-4b4f-a384-ee2856b9b622 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 168c939c-7e16-4069-badb-dbf71c06c452 |  | checkpoint | Site Engineer/foreman Second base coat inspection review
holdpoint | 37278d72-c2c2-467c-8ad6-caf459453618 |  | signoff | Site Engineer/foreman inspection sign off
checkpoint-group | ad50754b-ac12-4b78-a3e7-238e72492767 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 349af8a2-c2de-4894-acb0-d11034809e04 |  | checkpoint | Inspection
label | ff3cc332-b87e-5299-a6b9-77d28d9e0eac |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | a00e0f51-11a1-5483-aa76-81affdde62c1 |  | note | Records - time stamped photograph
select | 42aca190-5a7c-56dd-a057-a30fb5c8d426 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 3cb6c000-3748-4cef-bb69-2a6666d963d1 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 3b502b5c-611f-407f-8796-62ad2959f978 |  | checkpoint | Thickness Testing - Delfasco Positector
label | c7a3f27f-5e63-590a-990a-b2aa5a78a841 |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | 83f7ddbf-5f36-53dc-a1a4-42632a2e3a38 |  | note | Records - time stamped photograph
select | f1d0c4cb-3262-5f0b-89e0-07e47c4ec6c4 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | ee98ffe9-df73-4f2f-b76b-2ba9a32d5f33 |  | signoff | Subcontractor inspection sign off
checkpoint-status | c999643b-f2a8-42a2-b62e-a5d653cebaae |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | 2cf31767-04d9-52ed-b72e-e6d460845a48 |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | ed1c133f-502c-57f3-ad23-ea83aec6f13e |  | note | Records - time stamped photograph
select | 834f6bfe-2e0d-5cd5-a471-acad53bc0191 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | d372dc59-a1a2-448c-9799-d255426ecb3d |  | signoff | Subcontractor inspection sign off
checkpoint-status | 738e8cdb-6cb0-4206-a191-572879dd3cf0 |  | checkpoint | Site Engineer/foreman QA inspection review
holdpoint | f692e116-5970-4d04-a8c0-8256bc5c3c9f |  | signoff | Site Engineer/foreman inspection sign off
checkpoint-group | 1fdb5d41-e647-4fa8-803c-6ffb9243ae3f |  | section | DETAILING- EACH LOCATION
checkpoint-status | 4f1b4c57-e5c8-4a46-b4f6-939194d2bfc5 |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | 15043794-2d96-580a-bb34-39667afceaa3 |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | cd03f1e1-61b3-5c46-9551-7db8d9501c27 |  | note | Records - time stamped photograph
select | f3d52266-e334-5b0b-8e47-b2aedf97c7e1 |  | dropdown | Inspection | Surveillance point, Witness point
holdpoint | 2dd35d07-4595-445f-a3e5-3a30ef77b45c |  | signoff | Subcontractor inspection sign off
checkpoint-status | f5167e62-b11b-4292-935a-6799fb40e394 |  | checkpoint | Site Engineer/foreman Detailing inspection review
holdpoint | 621ddd51-5d60-4a91-a193-631b9cc2b22a |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 208a6250-0304-4c17-8b4e-d5701f9b51c5 |  | checklist | Enviro Ultra Tuff V1.1 |  |  |  |  | Yes | Enviro Ultra Tuff V1.1 | 1f81ce32-fa3f-43fa-b43a-23df73984280
checkpoint-group | ad68d9ec-5958-4dd3-90f0-448657c26d56 |  | section | DETAILS
checkpoint-status | 25a0d302-a3c8-4016-abbd-506ce9e8feb3 |  | checkpoint | Attach any relevant documents or photos
text | dbef50a5-f8ba-5c22-86ab-2ee717515b92 |  | textbox | ITP No.
text | 4dcfe418-8db8-5d7a-824b-9997681296ec |  | textbox | Revision No. & Date
text | ac5987da-2dd2-5317-9234-e2028ad128d4 |  | textbox | Prepared By
text | 6c60055b-29b8-5a2a-a598-a05a2a526ea5 |  | textbox | Reviewed By
text | cf6a2a72-ffd2-57e4-b7f2-f70eade3473d |  | textbox | Approved By
text | da23a945-efe7-5945-9d0d-f83b0cf509f6 |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 3eac8957-0615-49e0-a2c6-1f96f0569784 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 6e1a952d-14cc-4980-811d-6e0db5ec1abe |  | checkpoint | Enviro B-LV
label | b2cc7745-ca5a-5ae2-9943-3a6968eb261f |  | note | Records - Photograph
label | ad046e2c-fc57-59eb-bc29-55c5df8edce4 |  | note | Surveillance point
checkpoint-status | d8f91130-ff9d-47c6-a898-9989f38b4fb7 |  | checkpoint | Enviro Ultra Tuff
label | c27d4fb3-06e9-5f44-b9b6-d5710b78777e |  | note | Records - Photograph
label | b8772dad-425f-53cd-ba5b-fcc4fc391e1d |  | note | Surveillance point
checkpoint-group | e8ae2fd5-a9da-4982-b067-bbf1fc3b50ab |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | ebc0e1c7-44bd-4a45-ba5e-87e00ef46762 |  | checkpoint | Sample Submissions
label | 79842f91-8d86-5e87-8da0-d4b8eda25130 |  | note | Submit samples for approval as per Specific Material Requirements.
label | 4763fd36-cb9e-5b46-94b3-95a3a340c041 |  | note | Record Submissions
checkpoint-status | 2b95b8b1-4736-444e-8aa2-52d23aa729a0 |  | checkpoint | First Of Type Inspection
label | 30f6624e-0db6-5193-9238-df69cb70e4bd |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 13a8ec9c-d6d4-5e69-820e-fca804e5d982 |  | note | Record Submissions
checkpoint-status | 174bec67-78b7-4c00-a8bf-5abf5b592be1 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | ba6a01d2-fc7c-5eff-b9e1-98fe0ddb77ce |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 9915ef62-e9bc-521e-a61b-a1fcb18c4926 |  | note | Records - Photograph
label | f5a2232c-5124-5d46-b508-edf106dc9fee |  | note | Witness Point
checkpoint-status | eb1c65da-8f3e-4183-a0bc-bec044c856c8 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 94fa73d2-1402-5c40-86a4-e9b18e885081 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | 801a260b-63f6-5dea-91ab-04c925c687fd |  | note | Records - Photograph
label | c01d822b-4d75-5c98-b194-e4c2a8dab64a |  | note | Witness Point
checkpoint-status | db6671e0-348c-4ba6-b5e7-eaf65022b86c |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | 0939a1d9-e251-5a70-b2ff-08f6635736c8 |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | d6601edf-c008-531c-b8bb-82660ed670d4 |  | note | Hold Point
checkpoint-status | a6bc38ae-b7da-4793-80e5-d73afdf6915c |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | 1e1d9fbd-c278-5e0d-9e6e-9dd0984ad2fa |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 70250f33-6e8a-550c-8e45-7dd8ce64ec49 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | fb5aa4e0-664d-5041-90c7-0d45c6b5ae32 |  | note | Records - Photograph
label | 38b1fad4-fed6-5fed-8313-275fe7bbbfa8 |  | note | Witness Point
checkpoint-group | e3255ef5-fd94-4b7a-932c-875e13eef719 |  | section | SUBSTRATE PREPARATION: AS 4654.2-2012
checkpoint-status | 8dae74ab-7aea-45b0-b91c-e0bc722c8183 |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | 9f6d2a0c-5897-50a9-bf02-842477e82268 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 876b9825-6227-5b4a-91cb-f610c483afd1 |  | note | Records - Photograph
label | 9d069634-1e92-5593-9793-135a461c3333 |  | note | Witness Point
checkpoint-group | c4b91893-ff3c-4a6e-a5fa-6a83e0852c97 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | 85bbe47d-3ffc-429a-8fc0-82d3a50eb07e |  | checkpoint | Moisture Content - Enviro Epoxy B-LV Product TDS
label | ce28a0aa-d535-56c6-a453-46c97eb478c9 |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 62e72914-a648-5513-b1c3-883049aef540 |  | note | Records - Photograph
label | d854ea12-8a27-55d5-993b-294c949652d5 |  | note | Surveillance point
checkpoint-status | 19f979c2-58ad-413c-ab3a-2d686a14a4d7 |  | checkpoint | Weather/RH - Enviro Epoxy BL-V Product TDS
label | 43f2bfef-9e82-56ca-999a-4ad0568a5d8f |  | note | Apply within 5-35°C RH must be 0-85%
label | d2549cb6-5360-5dac-a3e4-b23165b98c28 |  | note | Screenshot - Temperature and weather forecast
label | e2c73323-1a98-5eb7-a290-949c2e4cde2f |  | note | Witness Point
checkpoint-status | 42fe468e-8a31-49d7-8240-990aeef2212c |  | checkpoint | Product Mixing - Enviro Epoxy BL-V Product TDS
label | 2bdc7f78-cdd1-566f-a078-53b09634a446 |  | note | Mix Part A (12L) and Part B (6L) separately add Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached. Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 994e22b3-350a-5020-8cc9-7ac1d391d7a5 |  | note | Witness Point
checkpoint-status | 73e31615-1066-45db-beba-b2c42d140471 |  | checkpoint | Application - Enviro Epoxy BL-V Product TDS
label | 42c94a63-c77d-51ec-abf8-2cd19f005394 |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied. Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 68458f28-5911-51fa-94c0-f842787073d9 |  | note | Records - Photograph
label | c43af6c3-fc88-5a2c-85c5-38304429ed85 |  | note | Witness Point
checkpoint-group | 5d2923e7-2c38-462b-9cc6-a6b2a6569b64 |  | section | EPOXY COVING - EACH LOCATION
checkpoint-status | d57ec7ae-47aa-4b77-9445-8d346c32fd72 |  | checkpoint | Coving - Enviro Epoxy B product data sheet
label | d112aabf-de6a-5ed5-9297-a8c764ac9f2d |  | note | Mix Sand plus Epoxy B according to the works' design specifications to create minimum 75mm coving
label | ded8eddb-3832-5762-accd-a0addd2e2818 |  | note | Records - Photograph
label | 3da2c7fc-71de-54b1-8d73-46d82e06367d |  | note | Witness Point
checkpoint-group | 23a27d1b-7f89-47ea-a2d4-42410622b204 |  | section | FIRST EPOXY COAT - EACH LOCATION
checkpoint-status | d7c6ab16-48dd-44d2-af27-ec33140748a7 |  | checkpoint | Weather/RH - Enviro Ultra Tuff Product TDS
label | 8f98506f-13ea-514d-ba66-9f9bb9756b9b |  | note | Apply within 5-35°C RH must be 0-85%
label | de100b5d-7ef7-5ee4-b0ee-77782811bae7 |  | note | Screenshot - Temperature and weather forecast
label | 6188f666-f46d-53a4-a274-75d5f1f39e43 |  | note | Surveillance point
checkpoint-status | 87758d0c-945f-410e-98d5-233778fc954b |  | checkpoint | Product Mixing - Enviro Ultra Tuff Product TDS
label | c7b0f014-fb3d-572b-b461-90f648d4b603 |  | note | When using a colour pack add to Part A and mechanically mix until uniform. Add Part B and re-mix until components are uniformly mixed. Colour Packs Rations: 1 pack to make a 8L kit and 2 for the 16L kit.
label | 4d94ecd8-53ba-56e5-a8a9-35d32cdf5653 |  | note | Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) for 3mins prior to application.
label | 427fa7ba-e577-59df-923b-d66c533074a2 |  | note | Witness Point
checkpoint-status | 0e1710e4-ff38-4047-8b1f-6e658f40eabf |  | checkpoint | Application- Enviro Ultra Tuff Product TDS
label | 846bae38-5909-5178-bc60-cb4ed545ac51 |  | note | Enviro Ultra Tuff can be applied by brush or roller to minimum dry film thickness of 250 Microns
label | cf2094a9-17b2-5ef5-bc96-2e38b69c4581 |  | note | Broadcast selected aggregate and allow to cure for 24 hours prior to second coat
label | cd5c5d5e-f5a3-5340-9370-766072d3c116 |  | note | Records - Photograph
label | 214b338a-5c27-5355-a95b-d38540f29aeb |  | note | Witness Point
checkpoint-group | fc254fb9-2afa-45e4-8dc6-9c296b22128c |  | section | SECOND EPOXY COAT - EACH LOCATION
checkpoint-status | c1c6eff6-cdc3-4cb1-92f8-1312a2690015 |  | checkpoint | Weather/RH - Enviro Ultra Tuff Product TDS
label | 0f2b8f81-6484-5452-b6b6-b5394128c3b7 |  | note | Apply within 5-35°C RH must be 0-85%
label | baff2d4f-5ecd-525d-9feb-78043321dc73 |  | note | Records - Photograph
label | ba82a41c-cc05-5c49-a48d-edfc3a15da4f |  | note | Surveillance point
checkpoint-status | f9e787c1-47b2-4184-9598-bf7dd2764725 |  | checkpoint | Product Mixing - Enviro Ultra Tuff Product TDS
label | a8ed6cc5-412a-5f7c-9acb-ca7522e15c68 |  | note | When using a colour pack add to Part A and mechanically mix until uniform. Add Part B and re-mix until components are uniformly mixed. Colour Packs Rations: 1 pack to make a 8L kit and 2 for the 16L kit.
label | 1c548b58-0525-56ae-8aed-d0dc0471abbf |  | note | Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) for 3mins prior to application.
label | 912fa007-d6f6-51f4-a070-ad2c46ead1e8 |  | note | Witness Point
checkpoint-status | 22d6e227-ab56-4aca-bfab-c5afaa3cb8c3 |  | checkpoint | Application- Enviro Ultra Tuff Product TDS
label | 70aed27f-c6a7-5791-8b8a-4d606d81dcdc |  | note | Enviro Ultra Tuff can be applied by brush or roller to minimum dry film thickness of 250 Microns
label | 39047a1e-def9-5fc6-86d1-67d31c70aa76 |  | note | Records - Photograph
label | 6b7db1fa-4b5e-53b8-bd84-4ed645671022 |  | note | Witness Point
checkpoint-group | ae1dcc04-cd42-4a39-bad3-871f6b1e998e |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 6f9c1811-d45d-4ef5-b177-a9ca8b40cbb6 |  | checkpoint | Inspection
label | 450746b7-18bd-53a6-a153-71cc67901a9d |  | note | Inspect after installation of reinforcement/finishes to check for any damage to coating and rectify as required.
label | 84c84797-3741-585e-a28f-ddf0afb48852 |  | note | Records - Photograph
label | 9db0a58d-fd66-5764-88ff-65e92d6482fa |  | note | Witness Point
checkpoint-group | ffc2be09-fd66-4501-ac30-4c7c377603ff |  | section | SIGN OFFS
checkpoint-status | 89e8d133-eeda-4220-8e86-4385a97fdfc5 |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 9a704d8d-94fb-4f45-a10e-6ed65218240e |  | signoff | Subcontractor inspection sign off
checkpoint-status | d63f1e4c-ec81-4fa7-b54a-e184e2f0c1c4 |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | fc3a92c1-6cb0-4097-bb5b-3b2071bdc996 |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | ed2ae31c-eb7e-4813-931e-600e9996f3dd |  | checklist | Enviro BSM- V1.1 |  |  |  |  | Yes | Enviro BSM- V1.1 | 25ec694f-dc7c-4a36-b058-f86614b98d33
checkpoint-group | e97861f8-f63b-4fc7-b387-66c230729a02 |  | section | DETAILS
checkpoint-status | 5643f729-b3cb-4af4-a099-c65f2414957a |  | checkpoint | Attach any relevant documents or photos
text | 21c35447-e983-5fde-891e-c82b46bfa78b |  | textbox | ITP No.
text | c9ddb462-e1d9-501c-9175-40428aa8ea42 |  | textbox | Revision No. & Date
text | afc922a8-988b-55d2-a445-9414385b1f56 |  | textbox | Prepared By
text | 93085681-930d-5411-ad33-8e9cdc05c214 |  | textbox | Reviewed By
text | dcf5dccd-5924-5592-8a2f-b1da8a3cb649 |  | textbox | Approved By
text | 5afa07af-1045-5d09-98db-b04e16e50ea2 |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | b1ed79a5-f803-4f87-beef-9b0e84e63d45 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 9f877a5d-a4b1-40db-a531-60b379b435fc |  | checkpoint | Enviro BSM
label | 22c17f62-9d26-5aa6-9547-2c9d35d42e81 |  | note | Records - Photograph
label | ba10209d-4f8a-5dca-9e51-7c6d7e0e2fa7 |  | note | Surveillance point
checkpoint-status | 5d23c65c-c7e8-4d3a-bb00-c5727daa6b59 |  | checkpoint | Enviro Epoxy Grout 100
label | 4f43fa4f-bae3-5425-ac38-4dba9d6177aa |  | note | Records - Photograph
label | 9638648a-ed9d-5a8f-8a50-981c2b82f05b |  | note | Surveillance point
checkpoint-status | be2510dd-45d2-4d13-8e30-41e212a2f6d2 |  | checkpoint | Enviro 700X
label | 770e4f7a-bcc4-56a2-94d9-a735e287a448 |  | note | Records - Photograph
label | 46f0435f-5d93-5299-a733-1c8af49ff543 |  | note | Surveillance point
checkpoint-status | c686912b-92b0-4ac7-8956-a1b7ff0297bf |  | checkpoint | Enviro Flex FC/ Sika FC
label | 4de4fd08-4a5d-59b9-9358-143e538f920b |  | note | Records - Photograph
label | d8a16839-8e09-5e1c-87b8-b08b6b633155 |  | note | Surveillance point
checkpoint-group | b7b3ca9a-f5c2-40e8-afa4-0e1d10ba3efc |  | section | PRE COMMENCEMENT- EACH LOCATION
checkpoint-status | 1a32afb9-ce94-4afb-bdc0-b5e5465c6c6e |  | checkpoint | Material Management & Storage
label | fb3bb5c1-03b3-5dd0-add7-c5cf2c6dc08e |  | note | Enviro BSM to be stored upright in dry, cool conditions out of direct UV and weather. Maximum storage temperature is 45°C.
label | f4610ce5-5533-56df-8e93-8e475ae89c86 |  | note | Records - Photograph
label | f75c3ae0-608d-55cf-bba5-52db66d3738e |  | note | Witness Point
checkpoint-status | 26c1beb2-72e6-4b0a-9faf-7473d7b78948 |  | checkpoint | Acceptance of Substrate
label | 1689c1c4-b0cb-5329-962d-0e788ed6433f |  | note | The substrate should be sound and even, thus preventing movement or subsidence during concrete placement. The substrate in which BSM is to be installed should have no protrusions, gaps or voids greater than 10mm. Penetrations such as plumbing and electrical pipes should be stabilized to prevent movement during membrane and concrete placement. For horizontal membrane placement, ensure that the substrate is sound, especially when installing over compacted fill so to avoid displacement from traffic or pouring of concrete. For vertical placement, ensure substrate is sound to provide required support for membrane during concrete placement. |  |  | `
label | 9d77d3f1-2c06-561e-836d-914bb524b516 |  | note | Records - Photograph
label | 7157fa5c-6749-5fcb-a3b9-c651b9db4c48 |  | note | Witness Point
checkpoint-status | cc202d5c-69be-4d73-8e0f-32338c2fa9b2 |  | checkpoint | Samples Submitted
label | ee1d5405-0a09-5c17-8d54-cc15699a9b0f |  | note | Submit samples for approval as per Specific Material Requirements.
label | 5ffec563-d46b-5ecc-aedc-df8d5e7352b3 |  | note | Record Submissions
checkpoint-status | db619714-df5e-4a51-a40d-08954f4117ff |  | checkpoint | First Of Type Inspection
label | 2f393044-f2e0-5786-b921-5dd0090d78bc |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 2bde6384-3d81-5b93-9d6d-be927956aa74 |  | note | Record Submissions
checkpoint-group | 6c1beab8-378e-4f98-a4b7-c8ee3a0170ab |  | section | APPLICATION - EACH LOCATION
checkpoint-status | f8e42d02-5a34-4084-a37a-ec9426e79704 |  | checkpoint | Horizontal application
label | 1627bc0e-69ff-5b8f-834f-90b34ec83a95 |  | note | For horizontal applications, Enviro BSM should be placed with the coloured protective layer facing upwards and the white HDPE layer facing the substrate. Stagger end laps of each run to avoid a build-up of layers. Overlap each previous sheet by 75mm ensuring membranes overlap edge is positioned correctly. Ensure the back of each subsequent roll is clean prior to overlapping and once in place remove the plastic film (on the overlap section) to bond the sheets together. Ensure a complete bond with no creases by using a heavy roller across overlap areas. Once overlap bond is complete the plastic film can be completely removed.
label | 65b5f683-10e7-5bfd-94b6-f805e849161a |  | note | Records - Photograph
label | 6ce805d5-039b-55db-9e04-57328c65a5a8 |  | note | Witness Point
checkpoint-status | 856807d6-c8a0-4b0a-9c11-7c7a54ef605f |  | checkpoint | Vertical application - Witness Point
label | e673daa3-7402-5ba1-8113-da220a24fc6d |  | note | Enviro BSM should be mechanically fixed to the substrate using (substrate dependent) fixings with the coloured protective layer facing the concrete pour. These fixings should only be placed in the overlap section of the membrane and have a low-profile head so that the sheet overlaps can lay flat and rolled evenly for optimum adhesion. Overlapping in vertical applications should be done in the same manner as horizontal applications ensuring subsequent sheet is overlapped by 75mm, adhered, and mechanically fixed correctly before proceeding with the next. The plastic film can be removed immediately in vertical applications. All cut edges and roll ends should be overlapped by 75mm, be clean and dry and sealed with Enviro BSM SeamTape.
label | 555bf315-94a4-5e10-91d4-a3f4125a2c2e |  | note | Records - Photograph
label | e7a4dedb-9836-5c30-a029-d7c66568de46 |  | note | Witness Point
checkpoint-group | 8faf3438-d2c6-4e9e-a20f-4464600dc8ed |  | section | DETAILING - EACH LOCATION
checkpoint-status | 2eb356e7-3a07-4cb4-a9f2-3bd97b90a9da |  | checkpoint | Reo Bars
label | 07698dad-0812-5c99-a145-e9a9c59f5018 |  | note | Ensure bars are chemset and fully cured prior to detailing. Use Flex FC/ Sikaflex FC to caulk around reo bars and overcoat with Enviro 700X. Membrane to return out minimum 50mm.
label | 60c7fd41-c53c-54bd-83c2-1bae7e306a1c |  | note | Records - Photograph
label | 76cda6fc-93fd-551e-a846-59bbf0b8afc3 |  | note | Witness Point
checkpoint-status | 91d0aef6-7d6f-45d9-9584-e5797ea4f6fb |  | checkpoint | Pile Caps
label | 340fa962-0902-5324-b40c-f4f5d8d81518 |  | note | Pile cap to be encapsulated with Enviro epoxy grout 100 achieving minimum 50mm finished height.
label | 9d253233-3441-5f8a-affb-6574b92b68b7 |  | note | Records - Photograph
label | 2dbb7a86-9fbc-5e90-8019-386fc58e1692 |  | note | Witness Point
checkpoint-status | 4093df5f-5546-4da1-8c25-2e85da62b78c |  | checkpoint | Sub columns
label | 5c86d4a6-0aff-5191-bfbc-9536c3085928 |  | note | Sub columns joints to be caulked and overcoated with Enviro 700X terminated minimum 100mm high and 100mm lapping on BSM sheet.
label | b27b9b81-2c83-5200-883b-27d2852fb1e7 |  | note | Records - Photograph
label | 41b7f8a9-47f0-501f-b731-4b49aabbb62b |  | note | Witness Point
checkpoint-status | 78545035-883e-4f25-9eaf-16098466e059 |  | checkpoint | Service Penetrations
label | f7aeef4a-2bfc-58c7-92bd-43cead20d6da |  | note | Service penetrations to be caulked around with Enviro flex FC/ SIka FC.
label | 1a484f3b-3342-5136-a82b-985e25502d24 |  | note | Records - Photograph
label | e4b794e1-6253-558f-91b6-ad8b24ecb976 |  | note | Witness Point
checkpoint-group | 9337920d-a514-4acf-98bd-52281db15513 |  | section | SIGN OFFS
checkpoint-status | 65cddc10-b33d-4e0b-b5ef-50677fe898b7 |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 9bc81e2d-a83b-4b11-b8f5-1bac15b1209d |  | signoff | Subcontractor inspection sign off
checkpoint-status | 4b073f11-f1d8-43ac-9e80-2da8679405ed |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | 83a6e0e0-708b-4aea-a1b1-9f63f8d918a1 |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 4a01cc71-1982-4ea7-b827-752a347c9f58 |  | checklist | HP1200+ 800TC V1.1 |  |  |  |  | Yes | HP1200+ 800TC V1.1 | 326cfce1-51f5-4e05-9db3-5709df058435
checkpoint-group | e278f922-6def-44c7-866a-f346b919a5b1 |  | section | DETAILS
checkpoint-status | 5ee9c4f9-bd4f-4c9c-a7b0-9a94928dd5a9 |  | checkpoint | Attach any relevant documents or photos
text | 53adc960-a6f3-5641-97d8-bce68c5bad1d |  | textbox | ITP No.
text | d76d0a30-40cc-590c-9710-ab22d458061b |  | textbox | Revision No. & Date
text | 4c50a180-d3a5-5ce8-9560-d9d1e59c843e |  | textbox | Prepared By
text | 1a03d363-5d07-5cbb-a746-bc81ab495131 |  | textbox | Reviewed By
text | 3e88f8a1-949f-54cb-bee4-8f0be3d0c3e5 |  | textbox | Approved By
text | 26b8e0ce-9915-5ea1-b085-fad8e93588e6 |  | textbox | Suppoting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 80585ec6-4523-47df-815b-86943850fcda |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | d2cd23fa-c190-42d3-a60d-88dce970ccbd |  | checkpoint | Enviro B-LV
label | 6c2e72d3-f526-5458-b394-6aa9c5af1bf0 |  | note | Records - Photograph
label | ec3b2a7d-00f6-5e85-b742-7c3f39c94f0d |  | note | surveillance point
checkpoint-status | e1157ca0-9989-43c1-860a-7050f7d4749e |  | checkpoint | Sika Flex FC/ Enviro Flex FC
label | 931597c8-ea18-52cb-8d3f-737f2182a149 |  | note | Records - Photograph
label | 94a7c023-c757-567e-b6a5-9989346b9a32 |  | note | surveillance point
checkpoint-status | 5ed72760-106b-460b-b5e0-77a3b7ba7383 |  | checkpoint | Enviro HP1200
label | 1a7d7975-3741-547d-839d-85652d3cf2d9 |  | note | Records - Photograph
label | 521fbc04-c064-5f72-b378-db3bf45484f9 |  | note | surveillance point
checkpoint-status | 6cf46284-a3f0-4fd1-a87e-d07c2109509c |  | checkpoint | Enviro 800TC
label | de925226-c7c4-5117-88c4-af8265ff4eb0 |  | note | Records - Photograph
label | 2ced1880-44be-504c-b98a-a553c7e3f72a |  | note | surveillance point
checkpoint-group | 487f3562-a685-43cb-bb41-d34e73019a33 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 83201a7b-54f7-4a16-93f3-89f814e18b37 |  | checkpoint | Sample Submissions
label | c6f44c1f-479f-5c5d-b072-dabece4bfc39 |  | note | Submit samples for approval as per Specific Material Requirements.
label | 2644b454-a253-5621-8e83-330522fb76aa |  | note | Record Submissions
checkpoint-status | b2c7a564-769a-4c19-9359-6619db071e9b |  | checkpoint | First Of Type Inspection
label | bf959f94-6736-5f57-bfa1-458aef27a196 |  | note | First of type of inspection conducted by builder prior to commencment of works taking place.
label | 47370cc6-740e-578f-bc7f-3d4f6e4a74ef |  | note | Record Submissions
checkpoint-status | 966fb04c-fd28-40fb-be32-141c7c159f94 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | e3dbe1c6-d6d8-59ad-9409-541bf01ed2d1 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 43f57b0a-83e8-5e26-892a-f49305cacc9b |  | note | Records - Photograph
label | 69a4cca1-3c02-5af6-a14d-f8634681975d |  | note | Witness Point
checkpoint-status | 176f1548-24e9-4db8-b4ab-ce45457dd9b5 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | becbbbfa-5d60-5ac8-8d5e-324ef9d5a595 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | 7656104c-1f93-5515-9497-873b9730e7b5 |  | note | Records - Photograph
label | f6e5b291-daaa-5afa-be77-fa3ee11f9434 |  | note | Witness Point
checkpoint-status | cf8fae40-5e7b-4cdc-8d9c-fa491f4bcd72 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | a31de240-bf2f-53d5-b893-c8fbdbb2dda8 |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | a6c25a60-24e5-5723-819c-3d790a753a0c |  | note | Hold Point
checkpoint-status | 11395adb-02c0-4e41-a547-3289e647ec6f |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | deaa3d21-dfe5-5c1b-b588-eaa919cb879a |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 418d0e70-55eb-5947-82e8-60ccb6cadc1e |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | fcd74346-a8f7-510f-8463-e8b58d0f9885 |  | note | Records - Photograph
label | 96fa615b-b3e1-5e1d-962c-4396b127e27a |  | note | Witness Point
checkpoint-group | 4e15d3d9-5d67-4989-b982-fb106a91e4d1 |  | section | SUBSTRATE PREPERATION: AS 4654.2-2012
checkpoint-status | d8e82bc5-8d0c-46e4-847e-53112486ba39 |  | checkpoint | Substrate Preperation - AS 4654.2-2012
label | 090ca384-c046-5651-881d-4a9f8984b87b |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | d32e5f85-efc9-596c-bf14-daff161c46d1 |  | note | Records - Photograph
label | 103886d7-ad3e-5694-ae9a-5385aea9620e |  | note | Witness Point
checkpoint-group | bcb7ed6a-39b0-4772-a332-80aacfb7c747 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | bf9419a1-73ce-4e6e-a571-c5b5b0b60c6a |  | checkpoint | Moisture Content - Enviro Epoxy B-LV Product TDS
label | b763e95f-a840-53c7-ae2b-4c5d69a37275 |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | bad46f13-8549-58c3-b260-3e76873176cb |  | note | Records - Photograph
label | 2c4dc2ac-8921-526d-978b-2ed89bfe1df9 |  | note | surveillance point
checkpoint-status | eed0e268-e5bb-4ceb-a64c-46ef28cd759d |  | checkpoint | Weather/RH - Enviro Epoxy BL-V Product TDS
label | 8f2d6788-352a-5791-96eb-f7f62b0cf5b4 |  | note | Apply within 5-35°C RH must be 0-85%
label | 934292ef-003b-5f5e-b251-049e00271298 |  | note | Screenshot - Temperature and weather forecast
label | 7c8c5e9d-944b-5765-90bb-71a9e0bede4b |  | note | Witness Point
checkpoint-status | 10e3c5a4-3087-46ff-b988-b6e343101a14 |  | checkpoint | Product Mixing - Enviro Epoxy BL-V Product TDS
label | 1d048984-8d8e-5234-8744-4795cb03b4e4 |  | note | Mix Part A (12L) and Part B (6L) seperately add Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached. Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 57144d30-495e-5912-97a2-3a1c525952b8 |  | note | Witness Point
checkpoint-status | 278f9a8b-7c54-4930-b9d4-96092567c6e5 |  | checkpoint | Application - Enviro Epoxy BL-V Product TDS
label | aeba70ae-1d6b-5474-90ba-e4c93cc59690 |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied. Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 68288c55-6b0a-5fce-b94a-8d2f2bf63e47 |  | note | Records - Photograph
label | a1833d96-39f5-53e3-8c71-3b72aa717dc5 |  | note | Witness Point
checkpoint-group | 41189040-8a0f-439d-aa56-14802d7dedd4 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 35570172-2f76-406e-9240-0a28e5c73cc1 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 31e33de6-1bb9-5510-8774-43debb9f81a0 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | 994a6595-6275-5f57-be30-ddd3698885c9 |  | note | Records - Photograph
label | 9bf91269-e620-5f84-bb40-9180cde62fa4 |  | note | Records - Thickness testing with fillet gauge
label | ddc3a1d4-2488-5978-957d-8fb1361808b9 |  | note | Witness Point
checkpoint-group | 79b20fe6-52e5-40b4-8a3e-e72ff133a0f1 |  | section | BASE COAT - EACH LOCATION
checkpoint-status | be774e05-9b39-44e6-9173-2e1bd45fae44 |  | checkpoint | Weather/RH - HP1200 Product TDS
label | 62793deb-34a3-5fc0-9db8-0cdea55c1e4f |  | note | Apply within 5-35°C RH must be 0-85%
label | 0c89e3f5-e6c9-5b92-b303-542e0bd5318f |  | note | Screenshot - Temperature and weather forecast
label | 82feb5d2-b22f-5dcb-9257-1b1ae799cacb |  | note | surveillance point
checkpoint-status | a3dce3ad-ea74-4256-b5c8-29f18daafdab |  | checkpoint | Product Mixing - HP1200 Product TDS
label | db562d42-aeb8-5a7d-90c2-230fb2d7aee8 |  | note | Mixing by way of 1:1 mix ratio (by volume) in heated plural component. Mix Part B thoroughly with a mechanical power mixer before use
label | e10af0cc-e50a-5986-83b4-c8d4c5e3e8f9 |  | note | Witness Point
checkpoint-status | e5446f35-397d-4787-b74f-416d6fbf7207 |  | checkpoint | Application- HP1200 Product TDS
label | eff16d3f-a470-5f02-9fe0-f408825afd4b |  | note | HP1200 must be sprayed using high pressue plural component dispensing equipment - Drums of component must be pre-heated to at least 25C prior to mixing or dispensing
label | 6c7dbf80-d505-5483-ac5b-b1090d59adf6 |  | note | Records - Photograph
label | 06946edc-16ca-55de-a3fd-36a8941bf460 |  | note | Witness Point
checkpoint-group | 78ad7e4e-6301-4782-88d8-e12e64d81b15 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 4cc8b37b-d0cd-4e8f-b59a-58f294ecfb7d |  | checkpoint | Inspection
label | 66426e94-d1cc-5eb7-ad0a-35eb4c7b7716 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | 9914df90-18d3-5dcf-b6b0-07fe686be5d8 |  | note | Records - Photograph
label | 1b22dafc-93cd-5640-a80f-51b5f0870fd7 |  | note | Witness Point
checkpoint-status | e1335d6e-5204-435b-a8f9-aff303632fd8 |  | checkpoint | Thickness Testing - Delfasco Positector
label | 6610ef2b-6fc2-5a19-b128-2a512efc17f9 |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | bfabc3af-f1ee-5418-acc1-89fe41f327aa |  | note | Records - Photograph
label | 1584940e-38d4-5076-8591-3a08b681d9a5 |  | note | Hold Point
checkpoint-status | b4520e60-9fc6-47f1-b17b-6a854eee3492 |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | 395e5148-0bdc-5708-8783-3d72853885da |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | 3f7fa844-8ce5-56f6-a83c-59a65dc8a43c |  | note | Records - Photograph
label | f4f96e4e-c7a7-502d-85b8-44bc617d811d |  | note | Hold point
checkpoint-group | b649dbb2-ca8e-4d37-848f-dfd51e3810be |  | section | WEAR COAT- EACH LOCATION
checkpoint-status | 8d6f02ac-f826-49bb-af8c-f08800a46062 |  | checkpoint | Weather/RH - Enviro 900 product TDS
label | 1b1598ff-9c25-5a74-8dac-bf5e60fd0f89 |  | note | Apply within 5-35°C RH must be 0-85%
label | 95c1d905-a42f-5f0a-862d-d0549a121594 |  | note | Screenshot - Temperature and weather forecast
label | 9a4e60b3-e181-5c9a-8058-35ab53f8fe94 |  | note | surveillance point
checkpoint-status | b8b1e641-62f2-45f0-a38a-b79a18bdce1b |  | checkpoint | Mixing of Product - Enviro 900 product TDS
label | e004934b-d380-5d02-a789-ade22cced465 |  | note | Mix Part A and Part B separately, before combining. Enviro 900 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) for a minimum of thirty seconds prior to application.
label | 2cc0717c-303f-57df-84b4-c6e1693a6ea9 |  | note | Witness Point
checkpoint-status | 9618928b-8667-441a-8860-3bea061417c1 |  | checkpoint | Application - Enviro 900 product TDS
label | ab5bbc23-1208-56bd-bfc2-adec7761d725 |  | note | Enviro 900 to be applied by squeegee, roller or brush to finished membrane. Aggregate should be uniformly broadcasted to the wet Enviro 900 within 10 minutes.
label | 6794534f-f5d1-5fd4-8ae1-992dea91aaa2 |  | note | Records - Photograph
label | 050f8deb-0672-5b64-9953-509facb44100 |  | note | Witness Point
checkpoint-group | 125055fa-1395-4723-bc7b-44c51d8bfda5 |  | section | FIRST TOP COAT - EACH LOCATION
checkpoint-status | afa69d76-0261-46d0-9529-ae7c74f0cb84 |  | checkpoint | Weather/RH - Enviro 800 product TDS
label | 9170cccb-f04c-516b-950a-eb5c241f180a |  | note | Apply within 10-35°C RH must be 0-85%
label | f8adfc0d-fdcb-55d1-b43d-02cd23e882eb |  | note | Screenshot - Temperature and weather forecast
label | c28cd885-811d-50c9-b0b2-31c2da7203a1 |  | note | surveillance point
checkpoint-status | ffac845a-814b-4c7e-8c1e-76229dff1bfa |  | checkpoint | Mixing - Enviro 800 product TDS
label | 640b339f-b851-59a3-a82b-9e834bbef391 |  | note | Mixing by way of 4:1 mix ratio (A:B) by volume. Enviro 800 TC should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Add Part B to Part A and mix to a uniform colour and consistency of a minimum 3 minutes - allow to react for 10 minutes before application.
label | 2df65922-5b58-586e-88b6-ab16cbf8a752 |  | note | Witness Point
checkpoint-status | 9b6afe82-9721-4ec2-875b-203fddd511e3 |  | checkpoint | Application - Enviro 800 product TDS
label | bdfd07f4-91b7-5ef5-ae62-d77be0b5457f |  | note | Enviro 800TC to be applied by roller or brush to finished membrane. Allow coat to sufficiently dry ( 24H) before proceeding to the next coat.
label | b88b7a23-69ce-58b1-86e3-d2cab43ce911 |  | note | Records - Photograph
label | c9e074cd-4569-53cd-b94d-b753d1ea5f81 |  | note | Witness Point
checkpoint-group | 45825b9d-d9b8-4694-8924-f19b963f1c17 |  | section | SECOND TOP COAT - EACH LOCATION
checkpoint-status | 146d8aa6-37eb-434c-9bc7-838d86d7c95e |  | checkpoint | Weather/RH - Enviro 800 product TDS
label | 0c102c5f-7b0e-52f5-9458-b90ca2d3b438 |  | note | Apply within 10-35°C RH must be 0-85%
label | 7594af12-8781-5c5a-abc7-f4038a409a43 |  | note | Screenshot - Temperature and weather forecast
label | e27c88b4-8b60-5074-80dd-40d890c67b3a |  | note | surveillance point
checkpoint-status | 98ecc323-53c4-4e70-a6c3-734c31cf6079 |  | checkpoint | Mixing - Enviro 800 product TDS
label | 212a7e65-79e5-50ab-a780-2db763fb0f5a |  | note | Mixing by way of 4:1 mix ratio (A:B) by volume. Enviro 800 TC should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Add Part B to Part A and mix to a uniform colour and consistency of a minimum 3 minutes - allow to react for 10 minutes before application.
label | 9a73e2a1-e068-5bab-92a6-85afeadefaca |  | note | Witness Point
checkpoint-status | 7efb90fc-eb10-4c70-abcf-1564fe880ff1 |  | checkpoint | Application - Enviro 800 product TDS
label | f9d32c5c-a859-5249-bc0f-74d4e3695a3f |  | note | Enviro 800TC to be applied by roller or brush to finished membrane. Allow coat to sufficiently dry ( 24H) before proceeding to the next coat.
label | d7f90f4f-9403-5b5d-81d1-77b42fe556ca |  | note | Records - Photograph
label | 0531bf41-2fae-570d-af89-8860c86923d3 |  | note | Witness Point
checkpoint-group | 36b68ee4-2376-4ee8-b733-e7cf10056c72 |  | section | DETAILING- EACH LOCATION
checkpoint-status | ae27279f-1802-471e-aafe-1333a49e9300 |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | 5e342f0e-8481-5b7f-a525-90865c342d91 |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | 80f44fa5-5100-5cd8-9ccb-756b515893c9 |  | note | Records - Photograph
label | 22e0b9f8-7652-5ec6-ac28-d6d4ee50b47d |  | note | Witness Point
checkpoint-group | 255da4ec-d0ef-48dd-97cb-e5fed537f511 |  | section | SIGN OFFS
checkpoint-status | 3be2b0ac-678f-4e67-baf3-7d3302194c8c |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | aa63b98c-b648-4b9d-bfbb-5cb9669340cf |  | signoff | Subcontractor inspection sign off
checkpoint-status | 392531b2-265d-48de-a0ae-4a00c2cd5f74 |  | checkpoint | Site Engineer/foreman ITP accceptance Sign off
holdpoint | 7e5ded00-30ba-45af-abde-03a03fcee57c |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 51bc138e-275a-45b9-9c56-6f7afcd52a1b |  | checklist | Enviro P2 + 700X V1.1 |  |  |  |  | Yes | Enviro P2 + 700X V1.1 | 4134b5b9-0ef5-456f-a107-d9002d5f7e78
checkpoint-group | f213eaec-f85f-4b98-9358-56fbb9fba09d |  | section | DETAILS
checkpoint-status | bd9d3dbd-3ede-4e42-94a4-31e98d3cb61d |  | checkpoint | Attach any relevant documents or photos
text | 439fce36-49e1-5864-9444-91a46061175b |  | textbox | ITP No.
text | 660b7e92-cad3-557c-9022-c6fec89d34a2 |  | textbox | Revision No. & Date
text | 9f0bd1b9-0bbd-55bd-92ab-e8fb5fc4a1e8 |  | textbox | Prepared By
text | 991d49e3-ebd8-5b87-897e-c4e3bec96792 |  | textbox | Reviewed By
text | 91fbdc79-006d-55f7-a968-9f5f35275b09 |  | textbox | Approved By
text | 368210cb-21f6-5bef-9b5a-70a5a1f4c4f2 |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 8349e6bb-8da6-4822-ac12-94a121b23547 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 497fe4f3-1577-4947-9825-d9943e967222 |  | checkpoint | Enviro Flex FC/ Sika Flex Pro
label | 49eb958e-1c04-557d-9399-726e574e0299 |  | note | Records - Photograph
label | 172f7498-196f-5b1c-855f-28a3a967985c |  | note | Surveillance point
checkpoint-status | 286d2cd6-9b18-4e6d-9087-ac82f102052e |  | checkpoint | Enviro P2
label | 93e952eb-ce33-513d-b9a5-e134f5158636 |  | note | Records - Photograph
label | 91cc96f9-64e4-586a-a2df-d585a2a38dbb |  | note | Surveillance point
checkpoint-status | 9302df57-4630-4ad4-9825-a059a6d581bf |  | checkpoint | Enviro 700X
label | f6fc9cb9-1e9a-5b3e-830b-6404c45bf1c0 |  | note | Records - Photograph
label | 902eb463-5599-53a2-a94a-c59fac816052 |  | note | Surveillance point
checkpoint-group | 24e003c9-8fbd-4b4e-ae7c-989c811a1aba |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | bb8043df-fd5e-4282-8cdb-c6f0f9a692fa |  | checkpoint | Sample Submissions
label | eff3a01b-24ae-5479-8981-5d33f9200f77 |  | note | Submit samples for approval as per Specific Material Requirements.
label | 6cf0ef80-a295-5534-9e23-b047181d136b |  | note | Record Submissions
checkpoint-status | 7f962004-d27e-4915-9b5e-aee7de73a2a3 |  | checkpoint | First Of Type Inspection
label | 86f77ddc-8d8b-5835-a9b0-cd7606c7f1a2 |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 094478a1-b651-5d42-ba4f-a389691fe98a |  | note | Record Submissions
checkpoint-status | 73f83786-3ed1-4017-aa60-7aa841fda1c9 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 68e1c0ee-99d5-558d-9722-d49da3910265 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 59ccd607-3ebe-55c3-a2db-e44157172116 |  | note | Records - Photograph
label | 61c12bde-5519-5c75-971b-91f0843d33fb |  | note | Witness Point
checkpoint-status | a9d654e7-e4e7-49e6-90cb-d2b51197a733 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | d429f096-b2fe-57f9-ab71-4529ded719e1 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | b1ee30b6-5fb3-53a4-94a6-dff34abc7a42 |  | note | Records - Photograph
label | 6cb3717a-53bc-5856-8fcf-73b0387afeb8 |  | note | Witness Point
checkpoint-status | 66cccfdd-1cb4-4d92-b87c-7d9870207233 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | 8feb4869-9760-5289-98f3-691a0f395656 |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | 003c3239-16a6-5f6c-857a-9da081fe1e8e |  | note | Hold Point
checkpoint-status | 55c8bb3a-c7aa-49f2-98cb-47455308c51b |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | a0329f54-429a-5977-b55c-5cb1b8c67e97 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 9ee4fbcd-ff6c-5123-ab19-8f3a4124a6a7 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | de9b2c54-c114-5ef5-b31a-4af919144f49 |  | note | Records - Photograph
label | f8620f86-569e-52d0-9ee9-b003439c7c5e |  | note | Witness Point
checkpoint-group | eba9912d-7a6f-4895-ae7c-4351e03576a2 |  | section | SUBSTRATE PREPARATION: AS 4654.2-2012
checkpoint-status | 5dec2925-ffae-474e-9921-bafd0a4d4446 |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | 2a473c9d-f4df-5465-aa6b-a8720acc5e37 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 85fba8ee-75e2-56c5-897a-b2f612a74eb2 |  | note | Records - Photograph
label | 500da9f8-a357-5fb1-ba9b-2dcfd08c7dd7 |  | note | Witness Point
checkpoint-group | be8f5a0f-feab-4d33-a425-3dec293a53f2 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | a6907815-0fd8-4b02-b17d-77d0ac821e9d |  | checkpoint | Moisture Content - Enviro P2 Product TDS
label | b9157d17-7f2f-5f19-a034-85f35637f9a0 |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | af63a46f-437a-5a86-9c5a-bfbda8ccd67d |  | note | Records - Photograph
label | bbf07649-90ad-542a-8aee-5216e6685f6d |  | note | Surveillance point
checkpoint-status | 9b65bef2-e8e1-4e3a-8896-b3058f485f68 |  | checkpoint | Weather/RH - Enviro P2 Product TDS
label | 27c54eea-c817-558f-bc90-12997eefc892 |  | note | Apply within 5-35°C RH must be 0-85%
label | 7f8306ab-4a67-57d0-b3a3-9775ae6e76a3 |  | note | Screenshot - Temperature and weather forecast
label | ed55e5b5-b042-521d-ac69-d296c249465c |  | note | Witness Point
checkpoint-status | af4163dd-eb40-40f1-9f88-f879f3f8c03e |  | checkpoint | Product Mixing - Enviro Epoxy P2 Product TDS
label | fe9b400f-ae66-51ee-874a-7ec75da80520 |  | note | Mix Part A (12L) and Part B (6L) separately add Part B, liquid hardener, to the Enviro P2 Part A base. Enviro P2 should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached. Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 68be46b7-ac93-5b22-8ac9-99110d5208c5 |  | note | Witness Point
checkpoint-status | 8aca2e2b-a117-46c8-bc91-2b9a6229b8b6 |  | checkpoint | Application - Enviro P2 Product TDS
label | e29e71da-cc8c-574b-bfe3-29d67b48f647 |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied. Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 195f5211-48e3-5545-8855-f0a7966d0c75 |  | note | Records - Photograph
label | a26086de-4060-574e-a4ea-e04bea6ae08d |  | note | Witness Point
checkpoint-group | cc6edff4-7965-4797-b2ac-8ab6872af929 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 78f9380d-4912-4689-8be6-ba95b4a463e9 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 738d9a8b-3f0b-54fc-99ce-57cfb6451235 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | 55c3807a-68dc-5d61-81e2-877af6314d3f |  | note | Records - Photograph
label | 49db2d68-a958-529d-8588-48bbcdd91483 |  | note | Records - Thickness testing with fillet gauge
label | eefef7e3-3e4c-55f9-88c9-be80dbd351b1 |  | note | Witness Point
checkpoint-group | 29e7cd42-e3fb-4841-9fea-b420e73f42f5 |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | c1ca7df5-fd12-472f-865e-1868d063f356 |  | checkpoint | Weather/RH - 700X Product TDS
label | 544a6dcb-a788-5f19-a111-7eda81698ea9 |  | note | Apply within 5-35°C RH must be 0-85%
label | b8faa132-a3d0-506c-a6df-abd5816a2f82 |  | note | Screenshot - Temperature and weather forecast
label | 49f94207-913d-57e2-ab35-9b675429e745 |  | note | Surveillance point
checkpoint-status | 07e8fb36-a3f2-48dd-82ca-40cd28f044b4 |  | checkpoint | Product Mixing - 700X Product TDS
label | f61bc8d1-7c10-50c6-8c2f-9b8c86b1501b |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 30fcea78-1f89-549b-9ff6-840709b25471 |  | note | Witness Point
checkpoint-status | b143a6e1-b537-4d78-9ba2-0128ea8c67ab |  | checkpoint | Application- 700X Product TDS
label | a3405ffb-2cdc-5f6d-9855-fb7b62aa37ad |  | note | • 700X to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | 21a1d6be-21e1-52a4-8a28-5514dced9047 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 6654642f-5796-5a71-8a7f-aed4a1816cb7 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | ae547069-0d36-5943-a125-b81fbead8477 |  | note | Records - Photograph
label | 14901540-a8a0-5e0d-a870-112002efb586 |  | note | Witness Point
checkpoint-group | 4550cbfa-ec84-4e93-bc58-77fea6144141 |  | section | SECOND BASE COAT - EACH LOCATION
checkpoint-status | fe3b8692-f615-45cf-a53c-bdb3d120babb |  | checkpoint | Weather/RH - 700X Product TDS
label | 3e648d60-0d31-5495-9580-0dafd727867a |  | note | Apply within 5-35°C RH must be 0-85%
label | 45b471ed-4258-5b69-995e-55e679fe2104 |  | note | Screenshot - Temperature and weather forecast
label | 9263b547-a85e-5971-9c2c-4133d79f71f3 |  | note | Surveillance point
checkpoint-status | c3a8f6a5-5fa7-4248-b0d7-5956deb45de7 |  | checkpoint | Product Mixing - 700X Product TDS
label | 027fed68-18a5-5c22-bb15-a9846429a744 |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 15dfeda1-a525-5443-af73-b3764ef406d2 |  | note | Witness Point
checkpoint-status | 13196cd2-8333-4afd-80b7-0549544cc65f |  | checkpoint | Application - 700X Product TDS
label | 3aecbb82-830b-5bd9-a85e-33a571c0ba52 |  | note | • 700X to be applied by roller Horizontally on substrate and terminating min 150mm with brush.
label | 95b8c142-3d4c-5f12-8713-5c58bc8209d0 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | d102911c-c04c-581f-a857-12cb861d08ba |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 146ca74a-47ef-58de-9e69-8abd5755550e |  | note | Records - Photograph
label | ff3e939c-d2d7-5458-9aa5-5588d313f50c |  | note | Witness Point
checkpoint-group | fb104baa-17c0-4db8-8616-2553dfe5ddff |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 5a72be3c-f1be-4ab4-a61c-1de05b6e6acf |  | checkpoint | Inspection
label | d0434bda-1b66-5991-bc52-145467e09f49 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | 10e020d7-4a1d-5827-9175-1906f96a47df |  | note | Records - Photograph
label | 13626a49-32ac-5d33-ae37-f654167f8e2c |  | note | Witness Point
checkpoint-status | 577402b9-72a0-4304-a76e-7bd9a783439f |  | checkpoint | Thickness Testing - Delfasco Positector
label | cf8020eb-0aec-55f1-8513-c3904a5a2722 |  | note | Thickness testing of application to the recommended DFT of 1.5mm to manufacturers instructions.( 1 test per 10m2)
label | dfd5864c-ace8-584b-ad45-d9041e34ae7f |  | note | Records - Photograph
label | a283840d-6756-55b2-9fbb-4ae9594a0d80 |  | note | Hold Point
checkpoint-status | 7d9a807e-a6b6-4f8b-934f-8189c63de0a3 |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | 211a74ad-14b9-557b-8810-903c0145bf6b |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | 527ab520-99b8-50cc-8cbf-50e2f055bc67 |  | note | Records - Photograph
label | 4f5f6abc-e32c-5bee-9f37-d0ba553d980b |  | note | Hold Point
label | 05cee398-3c03-5248-857f-b05452944cb3 |  | note | Records - time stamped photograph
checkpoint-group | 1452d348-ea15-41b2-a2d8-9a6f8760c5fa |  | section | DETAILING- EACH LOCATION
checkpoint-status | 98b0395e-c47e-4653-b646-f24a7b35e9fa |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | 005c8f1d-355c-5fb3-8b9b-abadc5fbc118 |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | 8dfd1253-ef45-50f4-876c-efed51d6ca89 |  | note | Records - Photograph
label | b13cf0b7-006d-55d4-99ce-63ebfe1989fb |  | note | Witness Point
checkpoint-group | 362463c4-d0b3-4c91-a852-5d4eca8a43ee |  | section | SIGN OFFS
checkpoint-status | 95f8e85d-1651-4b03-900b-bd1183efb4d6 |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 84990679-dbac-42a3-8ba0-c66233d54023 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 2c99692b-ec51-4181-ba8f-440d76afff67 |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | 1f687263-f5c9-4244-976a-875af01abe5f |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 0dfdae82-c600-4ccd-a5e2-33f31465eba0 |  | checklist | BLV + 700X + 250NS V1.1 |  |  |  |  | Yes | BLV + 700X + 250NS V1.1 | 4815969c-5155-44dd-8d75-19673c80c374
checkpoint-group | 3c38c77d-ad0b-4dea-a3fc-a2fc36a8fb98 |  | section | DETAILS
checkpoint-status | ef9768a8-7ec7-49d4-9323-07402cb4927d |  | checkpoint | Attach any relevant documents or photos
text | 756ac8ed-34df-5be6-81be-eb6d0b8af8a9 |  | textbox | ITP No.
text | 3c6a4e46-ea4d-5290-a659-2a0c2a52840d |  | textbox | Revision No. & Date
text | d4041fcf-7a7d-585a-a82c-8ca9294c0520 |  | textbox | Prepared By
text | bf179938-3fca-5492-a7e8-485e16ee40fe |  | textbox | Reviewed By
text | 2b9d4421-8c56-5955-9bab-daec03216da5 |  | textbox | Approved By
text | fe63c678-222e-5873-9c49-2e17aa612ede |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 19ef0596-333b-451c-9209-810265efda55 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 88f22eb6-6167-4e31-bdc8-5867d2010e25 |  | checkpoint | Enviro Flex FC/ Sika Flex Pro
label | 2f170141-0887-5527-bb5c-afc387769a2e |  | note | Records - Photograph
label | 5f421cef-9092-5770-8874-05210603a774 |  | note | Surveillance point
checkpoint-status | 982d0588-f6b8-4796-8d78-8a9ae7f030c1 |  | checkpoint | Enviro B-LV
label | 71ff6a1f-2208-5cbd-b3d0-013178f4970a |  | note | Records - Photograph
label | 75a97e0c-4eef-598e-a01c-dd50feea19b6 |  | note | Surveillance point
checkpoint-status | eae038da-0373-4dd2-86d3-e019ffa62f44 |  | checkpoint | Enviro 700X
label | 39f62ee4-40eb-5539-b8e0-c0f54b6a73dc |  | note | Records - Photograph
label | 0a631322-aa1b-543b-907c-db88bccd3a2b |  | note | Surveillance point
checkpoint-status | b5ea9683-bae6-4118-8ca3-e6909ff146e0 |  | checkpoint | Enviro 250NS
label | d055fa44-4b1a-59c7-9c88-9b9d16e04096 |  | note | Records - Photograph
label | c2622c85-12db-5e88-b28d-e82fc0606a78 |  | note | Surveillance point
checkpoint-group | 0846db21-cf42-42a5-8c48-d582ffd218e4 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 8d187ee0-7de3-410d-817d-aca18301001f |  | checkpoint | Sample Submissions
label | 43e2526f-2362-50d8-be69-97917e73223a |  | note | Submit samples for approval as per Specific Material Requirements.
label | 6b6b7589-362b-5b00-ab07-b2420b896c90 |  | note | Record Submissions
checkpoint-status | 7f6f6eac-cabc-4d4a-ac51-527152b36a24 |  | checkpoint | First Of Type Inspection
label | 5df3a861-3631-54cd-8609-70fb7ea25d8b |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 9998cfed-5e0d-5d52-a07b-31d35c2fe11a |  | note | Record Submissions
checkpoint-status | 3f2d0f62-726b-4cce-b150-28b31dc16a3f |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | a5929cc9-7677-57b8-ab7d-d2cacb66c9fc |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 90120a40-b21d-5d2f-9cc3-7688ea35b7d2 |  | note | Records - Photograph
label | b781491b-fe88-5deb-9256-fcd0619a8b3b |  | note | Witness Point
checkpoint-status | bd9fb236-9b14-48a4-a1bb-f3772376191a |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 8cd7bd65-bdff-5398-a7d6-f1b497d6d847 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | 0f1c4a74-0170-565e-87ff-7d7bae0a5b27 |  | note | Records - Photograph
label | f25b9cc0-1ca6-5732-b1e8-8bcfa51ee579 |  | note | Witness Point
checkpoint-status | b4f967e3-0af6-42a3-bae2-c7394219f571 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | 2379e154-74a1-56ec-9830-ecb5c775f01a |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | 4d836394-d961-51a1-83fd-5f87d9e2d942 |  | note | Hold Point
checkpoint-status | 58a69fe9-eaca-4f8b-b41e-9422945d3449 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | 8bd154b2-6b7d-57cb-a4ba-e3c942e84b05 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | bd660d28-177d-5ea7-ae6b-30489b61a5aa |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | 408baf17-d70a-5ad0-9fb6-030390bdb13f |  | note | Records - Photograph
label | 5df50456-b24e-5fed-9af0-2431e1569d51 |  | note | Witness Point
checkpoint-group | 32ba2ac3-0715-47e2-8ffc-afeaa78df5e6 |  | section | SUBSTRATE PREPARATION: AS 4654.2-2012
checkpoint-status | 5b766053-46b4-4264-8836-32ba52734bf0 |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | afce02fb-8c6b-56b5-9e7f-3c0a2665cc97 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 9f6e4687-5ef9-55e9-b925-ce792ad7029e |  | note | Records - Photograph
label | 343dd259-0c9b-5d9d-a0b3-a5e4b4d70719 |  | note | Witness Point
checkpoint-group | 7cfc29b3-e7a5-4149-b84a-715d7671f931 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | 3667e2d1-6a53-4231-b606-a9c0221485be |  | checkpoint | Moisture Content - Enviro Epoxy B-LV Product TDS
label | 7faecb81-4a63-51e1-9605-fb1706450e4f |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 700fcece-6df4-5b06-b87c-6e3f6d9a6fb3 |  | note | Records - Photograph
label | 64e56da3-053b-534f-b57f-1c5335af17ab |  | note | Surveillance point
checkpoint-status | 3ee8fbf9-2664-4463-ab22-0d28b5e272b4 |  | checkpoint | Weather/RH - Enviro Epoxy BL-V Product TDS
label | 67e9542b-788d-541f-8971-312aef41410c |  | note | Apply within 5-35°C RH must be 0-85%
label | ab279189-a43e-5f88-9687-eabbfea7ef7d |  | note | Screenshot - Temperature and weather forecast
label | 517b787d-a143-50f8-8e55-37ce403c12ab |  | note | Witness Point
checkpoint-status | 0fbe0ee9-6f42-4ebe-b8c2-fc85ff99f5d0 |  | checkpoint | Product Mixing - Enviro Epoxy BL-V Product TDS
label | 0b5e38c9-f066-5c57-9cf6-b0be9e123f32 |  | note | Mix Part A (12L) and Part B (6L) separately add Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached. Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 85fa097d-1372-5718-9746-86ec47ecfe0e |  | note | Witness Point
checkpoint-status | 6ae13670-7639-4dfb-9223-eca765e1a84a |  | checkpoint | Application - Enviro Epoxy BL-V Product TDS
label | 1204ae8d-78e4-5638-a0fa-400deb613282 |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied. Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 453eb911-14a9-5acd-a570-26369c533ad9 |  | note | Records - Photograph
label | dc1fd18a-cd68-55b5-8414-b3c0d2dc5a2f |  | note | Witness Point
checkpoint-group | d3a96c04-18c7-4e1f-93c2-410a0e8e72ac |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | a339fd6c-0fb3-4c2a-a3dd-c99775287c11 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 8828e3df-1ecc-54be-95e8-d7d055475430 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | 1bcb3847-b329-5333-ad7d-85a3de7fc06f |  | note | Records - Photograph
label | 5db58df0-50eb-51c0-a45a-a99d92a2d3cb |  | note | Records - Thickness testing with fillet gauge
label | 7b5c62fe-b4a4-5253-b234-9b9afc1bb0bb |  | note | Witness Point
checkpoint-group | 46752f2f-1ed8-42a9-89cb-9073f656dcbc |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | 00ba46c9-6b38-4df1-be12-b376be922e07 |  | checkpoint | Weather/RH - 700X Product TDS
label | b9f995ee-f147-5a66-9157-0df07fbd7e10 |  | note | Apply within 5-35°C RH must be 0-85%
label | b60648d9-01f2-5155-9187-c59417846f8d |  | note | Screenshot - Temperature and weather forecast
label | bc81fc75-dc75-585e-aecd-e6275ad97ab5 |  | note | Surveillance point
checkpoint-status | cbc9ef19-1c92-46a2-b12c-9ebedcb09dea |  | checkpoint | Product Mixing - 700X Product TDS
label | bdc25190-89bd-5b1b-b0f9-ddc22200667d |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 6fa0f9dd-b0a7-588a-8d73-778ce838997f |  | note | Witness Point
checkpoint-status | 7b29e007-0803-43fc-aadb-70791b2edfd6 |  | checkpoint | Application- 700X Product TDS
label | 9b862f76-ef24-5197-a6d8-f770a59ae7f5 |  | note | • 700X to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | 0392a88b-35ef-5143-9fcc-94e5a6b3c439 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 71563e47-65db-5cf2-b245-bb2338811e84 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | bcf464dc-2660-520c-8f03-2e1993d55c60 |  | note | Records - Photograph
label | 59241394-55bc-52a7-bbb8-424b7a9390c2 |  | note | Witness Point
checkpoint-group | edb47b31-fa89-4f9f-b577-3b5e69b244c2 |  | section | ENVIRO 700X - SECOND COAT
checkpoint-status | db107404-f697-41c8-95f6-cd99ed4a69a6 |  | checkpoint | Weather/RH - 700X Product TDS
label | 9f9abe88-f3d6-51fb-a20d-d0e5032676ba |  | note | Apply within 5-35°C RH must be 0-85%
label | 6f44689c-8dc5-54c0-b210-3d2d7202dd2c |  | note | Screenshot - Temperature and weather forecast
label | 6bde8881-9278-536f-b86b-5f1277615383 |  | note | Surveillance point
checkpoint-status | 260cbbb3-454f-42b7-9d91-506bda2a68d7 |  | checkpoint | Product Mixing - 700X Product TDS
label | 7f31b8d4-4110-5280-813b-58d3a21e6ace |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 7a0d2c72-57a0-5d54-ade6-cfeba5658cc0 |  | note | Witness Point
checkpoint-status | 75545541-64fa-438a-9788-6f583bf7a849 |  | checkpoint | Application - 700X Product TDS
label | 2abda81f-3958-56e2-9686-5eff5181918e |  | note | • 700X to be applied by roller Horizontally on substrate and terminating min 150mm with brush.
label | 13c591ab-f08d-5154-8e64-6ca322759224 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 2edfd1a8-dbc5-508a-9e66-c6c3fa90ad35 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 741bc22d-eadd-5e10-802f-3f555abec606 |  | note | Records - Photograph
label | 07ac5aa8-9ed9-5fbe-b2f1-acaffd5afde2 |  | note | Witness Point
checkpoint-group | 9913c44b-e5fe-41bf-a4bc-e869120ed8f8 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 57083c69-7379-4d49-a938-539e08d93a9d |  | checkpoint | Inspection
label | 6b5c4d25-ea0c-53e4-b3fc-7e3d05d679d3 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | 34beda43-f077-5f5d-a987-adcdd0af00ec |  | note | Records - Photograph
label | 01c2d57b-b8ba-524a-9acb-9b40b5589865 |  | note | Witness Point
checkpoint-status | ba60d873-498d-4450-b6b1-8ac8ce9ea9ad |  | checkpoint | Thickness Testing - Delfasco Positector
label | f286d846-dca7-5f24-beac-6824974900e0 |  | note | Thickness testing of application to the recommended DFT of 1.5mm to manufacturers instructions.( 1 test per 10m2)
label | 3e69b8f3-1063-565b-9062-dc21fd736ef7 |  | note | Records - Photograph
label | d1acf1c5-dda5-5c49-a215-0e9c7ef893d6 |  | note | Hold Point
checkpoint-status | d14e3fae-992c-45c8-8536-037206d05a02 |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | b61b3f4e-cfbc-59ad-bb42-d8232530678f |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | f630da59-7466-54ae-bcf2-c4401a70ed0f |  | note | Records - Photograph
label | 32d3bb2b-56ed-5203-a223-cef8ceb216d1 |  | note | Hold Point
checkpoint-group | be0ff302-7a53-48fa-ab20-043add9100a2 |  | section | DETAILING- EACH LOCATION
checkpoint-status | 4c7cae6d-a825-48c0-bd5a-dff17abd5559 |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | a427cbda-2d62-5901-8037-9b165910d788 |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | 73f70f96-423b-54b0-ae22-384da97153b6 |  | note | Records - Photograph
label | 8fa8574e-8516-54bb-8dfd-c01c66b63538 |  | note | Witness Point
checkpoint-group | 4c573638-733f-4b5d-bccc-45f6263bf127 |  | section | FIRST TOP COAT - EACH LOCATION
checkpoint-status | 2b340791-2165-46d1-8e63-bcf507a25a83 |  | checkpoint | Weather/RH - 250NS PRODUCT TDS
label | c09dc8d6-5362-5fff-aba7-83daeb841957 |  | note | Apply within 5-35°C RH must be 35-85%
label | 9c56730d-67ee-5f32-a295-7a125f2cced0 |  | note | Screenshot - Temperature and weather forecast
label | a31bd873-cfde-5cb0-81da-cba5c31c1440 |  | note | Surveillance point
checkpoint-status | 24384708-d808-41ed-825c-1401a2ddc38e |  | checkpoint | Mixing- 250NS PRODUCT TDS
label | 03c80b26-9364-5704-839b-72d8ee0eadb7 |  | note | • Enviro 250NS should be thoroughly mixed with a mechanical mixer at low speed (less that 400 RPM) prior to application.
label | 77b8ab25-9ae8-5081-82d1-8b7e37582ea7 |  | note | Witness Point
checkpoint-status | 66c6f699-f636-4f37-bef7-e7bdcd49cdda |  | checkpoint | APPLICATION - 250NS PRODUCT TDS
label | ba2358d9-ef4c-5852-93e3-7e1c28d2577e |  | note | • 250NS to be applied using roller and brush. •Ensure Product is cured for 24 hours prior to second coat.
label | b68dfa0d-cbc8-50d3-b3f5-d49bc7bfec16 |  | note | Records - Photograph
label | 68ae1b16-3b2b-5ce9-931c-a03dca06337b |  | note | Witness Point
checkpoint-group | 224970bf-a423-412d-963f-5c1aebb00cd8 |  | section | SECOND TOP COAT - EACH LOCATION
checkpoint-status | 52b0c422-1f1b-4c7b-8d62-6c60e186b484 |  | checkpoint | Weather/RH - 250NS PRODUCT TDS
label | d02d15a6-ca9e-5e7a-81d8-e2a5005f1f6b |  | note | Apply within 5-35°C RH must be 35-85%
label | 36a833c5-91a2-5aed-bfc0-a8a908757cd5 |  | note | Screenshot - Temperature and weather forecast
label | 3c1d02f2-c944-581f-8fd4-c36d89975c37 |  | note | Surveillance point
checkpoint-status | 53cb28ae-95cd-440f-b334-2503830821a2 |  | checkpoint | Mixing- 250NS PRODUCT TDS
label | 27f47b11-8b8f-5fc7-b770-9a397a7d0a02 |  | note | • Enviro 250NS should be thoroughly mixed with a mechanical mixer at low speed (less that 400 RPM) prior to application.
label | 3e065674-4919-5fae-ae72-38ab858530cd |  | note | Witness Point
checkpoint-status | db461105-d8ba-4654-a642-53015112c4b8 |  | checkpoint | APPLICATION - 250NS PRODUCT TDS
label | 42cab51a-ccfb-57bd-a0d7-f75327b4433c |  | note | • 250NS to be applied using roller and brush.
label | e36cfdeb-622d-5524-847c-52eab9d2b653 |  | note | Records - Photograph
label | bdb1dcee-b6e5-5cc3-a041-15121fabfae2 |  | note | Witness Point
checkpoint-group | 21eae03b-2c78-49c5-a272-80a01141f3ce |  | section | SIGN OFFS
checkpoint-status | 56c76549-18f5-4b41-837d-85281d4af7f0 |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 20cf77c0-b3ac-4635-8e90-9c32fd34a029 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 32f754e7-c7f1-4cf8-bc34-e339b0ea06bf |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | 49da3365-2a93-46f3-86f9-e205ee69ce1b |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 72b29bc9-d3cf-44f2-8b78-dd3a21f49d92 |  | checklist | Enviro 200P V1.1 |  |  |  |  | Yes | Enviro 200P V1.1 | 5d3c29c5-1c7d-4010-bb0d-3250201138b1
checkpoint-group | 4e5c1e63-fc45-450d-ab90-a05526d00f81 |  | section | DETAILS
checkpoint-status | 1fab87fa-bf46-4fdc-8a13-5d1463932164 |  | checkpoint | Attach any relevant documents or photos
text | fe406685-4820-55b5-aba5-57c7adc14bb9 |  | textbox | ITP No.
text | 16df1d26-bc22-56dd-b2fc-63d2a653d6fc |  | textbox | Revision No. & Date
text | 3a288ee7-e798-539e-aad8-11389b078c91 |  | textbox | Prepared By
text | 8cc9ff42-a295-5edc-b7c9-26ff9ac12a39 |  | textbox | Reviewed By
text | 1ae43d01-b0a1-51ab-8cad-b9f28e49aa67 |  | textbox | Approved By
text | 16d26a1c-a102-5951-ae20-543a2868ba6f |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | cd818394-0dc7-4b10-a5e4-739b9b28b203 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | d0f19d71-1182-448c-92b7-7089e9d4fa3d |  | checkpoint | Enviro Shield
label | e5deac6a-725b-5f65-a500-15b06a6c21d1 |  | note | Records - Photograph
label | 2538378c-cd6d-55a3-aae2-bf7c6a90abac |  | note | Surveillance point
checkpoint-status | 709cec20-d680-4d69-95d5-bc449546845e |  | checkpoint | Enviro Flex FC/ Sika Flex FC
label | 031d5600-439c-51ad-afcf-bbbc3d2033d1 |  | note | Records - Photograph
label | f0fb363c-4ce8-5d5f-816b-74a8eb66c080 |  | note | Surveillance point
checkpoint-status | 0db1580d-382f-4309-a114-583c62be722f |  | checkpoint | Enviro 200P Ultra
label | 42601eb6-3380-5e27-adc3-3e20e9f949aa |  | note | Records - Photograph
label | 459686e3-8b0f-544f-9234-b55e973cf73c |  | note | Surveillance point
checkpoint-group | 2b44ce1e-9333-4876-a7e8-b8b8c807b1f9 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | ec7cedc0-f457-4d75-a40e-e09bf1d0a5f5 |  | checkpoint | Samples Submitted
label | 387fe9ed-d9fe-5783-a20c-0c3ffe571b13 |  | note | Submit samples for approval as per Specific Material Requirements.
label | 95d9d2c1-280d-5795-9a4f-3f2c1be9a5a5 |  | note | Record Submissions
checkpoint-status | 25072779-8917-4fda-a04f-dd441216af05 |  | checkpoint | First Of Type Inspection
label | 8c07d23d-3a5e-5a2f-8458-5146d78b9ac4 |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 17fb1b73-4c7b-59da-9040-1c79be15a971 |  | note | Record Submissions
checkpoint-status | 8ab0a7c2-9c93-418f-ba25-90e44e7bae58 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 505db79e-c6b8-5882-9d20-c5322bb7a065 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 7de9a528-dc32-57ea-a06c-029b496b4614 |  | note | Records - Photograph
label | 48f077e6-ab58-5e02-a193-44288fa63f26 |  | note | Witness Point
checkpoint-status | 91d7493d-c56f-43f3-8008-dd0a7c6e65bc |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 224fd862-6647-5f42-9f4c-55569f2f277f |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per PDS before applying the membrane.
label | f537e721-db5d-5e6d-b8f5-ee9f8513e435 |  | note | Records - Photograph
label | 4a65e7d5-c8ba-5690-9d35-a74c4e223a9e |  | note | Witness Point
checkpoint-status | 214bf2dd-3337-4ea8-a80f-42f59781017f |  | checkpoint | Acceptance of Puddle Flanges - AS3740-2021 Section 4.3.1
label | 87481212-438e-52e6-a68c-bd48b67f0dd9 |  | note | All Puddle flanges to be recessed into substrate to finish flush ready for waterproofing.
label | 7fbc1c57-c53e-520d-84c9-ddb6dd76683a |  | note | Records - Photograph
label | 5c7d3d4c-7693-54f5-ad10-decbee92dbc7 |  | note | Witness Point
checkpoint-status | 063a3580-3339-43d7-8b80-787ac158078b |  | checkpoint | Acceptance of wall - AS3740- 2021 Section 4.4.4
label | a98b6f4b-1040-5a5c-a7cd-07963bf6a4ef |  | note | FC sheeting to have max 6mm gap at floor/wall junction. Sheets to be set with manufacturers base coat, including all nails, penetrations and corners. Mortar in block work needs to be a flush joint, smooth and level with the blocks, no blow outs of mortar.
label | 8ffcf01c-d667-5a72-a591-b14d310c0e80 |  | note | Records - Photograph
label | 8298b222-aa6a-58cb-b735-1fcc83afae8d |  | note | Witness Point
checkpoint-status | 2029204e-5a43-4d8c-9ce8-999c51da9a52 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3
label | 93981e91-dbc7-5fed-8e8d-facef84c45ab |  | note | Builder to confirm compliant falls; minimum 1-100 falls and 1-80 in showers
label | b2c8f952-7d44-59ae-ac53-5e8acc610275 |  | note | Hold Point
checkpoint-status | c7a811bc-83f2-4f9f-b84a-599a62de6659 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | 1acd2c09-727f-5c94-bddd-1b8978034f70 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 6a68540a-07ab-5d73-a747-ba2e0c8b6c36 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | 7ff01738-0e5f-56e2-90bd-c7d3e458c8b0 |  | note | Records - Photograph
label | 9c325b6e-ce34-5dc0-a968-963eca90cc66 |  | note | Witness Point
checkpoint-group | 9b689a82-d840-425c-b9da-43c6eb27fa76 |  | section | SUBSTRATE PREPARATION - EACH LOCATION
checkpoint-status | 323a0606-376b-4fcd-a736-8c19cadf86ef |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | c5076dd4-c715-54d0-9f16-1eb29a0cc6ae |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 1552dc80-8247-5e67-9cdd-69c26ce7e363 |  | note | Records - Photograph
label | 729b5383-739c-5869-8b0e-007597f2a388 |  | note | Witness Point
checkpoint-group | bcb2d9ff-9364-470c-a2df-0c909f16fac6 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | 8bde22bc-1d1b-4349-b3fe-9542abea5e76 |  | checkpoint | Moisture Content - Enviro Shield Product TDS
label | cf6fb555-0ccd-5402-a36d-3c56b16a680e |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 9aa54a30-19f6-5408-8900-4e8efcfcc949 |  | note | Records - Photograph
label | dd177d50-5ad9-50bb-8be6-e29ca6ad81bc |  | note | Surveillance point
checkpoint-status | 3cf20c28-cfa7-402c-a304-ed08b61a7350 |  | checkpoint | Weather/RH - Enviro Shield Product TDS
label | b38626fd-17a7-52fb-a3a5-b30f5f9ba003 |  | note | Apply within 10-35°C RH must be 0-85%
label | 7f09bef8-78e3-5581-a76d-c2627a730670 |  | note | Screenshot - Temperature and weather forecast
label | fc1d2bc8-8c23-5638-a9f5-0f1b5192435f |  | note | Witness Point
checkpoint-status | 57e685fc-3747-42db-8749-0489297905de |  | checkpoint | Mixing - Enviro Shield Product TDS
label | 93f9ea37-dd95-51ec-8d06-98bb2c7e2b2d |  | note | Add Enviro Shield Part B (grey liquid hardener) to the Enviro Shield Part A (base Thoroughly mix with a mechanical mixer at low speed (less than 400 RPM) prior to application. Mix for 5 minutes or until uniform. Allow to stand 5 minutes after mixing and then mix again for a minute.
label | e1620dee-2fe3-50d6-9aa6-a3bad0343e30 |  | note | Witness Point
checkpoint-status | 4decb05f-c3bf-4f81-b547-1e83638782c4 |  | checkpoint | Application - Enviro Shield Product TDS
label | 264f5581-8808-5130-a572-3d4b42d60153 |  | note | Apply primer using a brush or roller.
label | 8731aa24-69f2-575f-aaa2-93768b6f9745 |  | note | Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface.
label | 5998ebb3-a54c-51bf-bc98-2bc7f82af4d6 |  | note | Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 99e07067-a5ff-552a-a7ef-91c99bad736a |  | note | Records - Photograph
label | 3516b337-eb69-5426-ab3f-e8aeed0373c1 |  | note | Witness Point
checkpoint-group | 29095e29-a4ce-4663-8005-fcba7929d0f8 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 9a11dd1d-4ea0-439f-a515-5685fabd1000 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 20c86d84-7ecf-547b-8f81-70fa2f834adc |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | 213f002b-9965-51d5-989b-0c30e9860a9a |  | note | Records - Photograph
label | e4a88bbe-4045-5e6a-b94c-297e2e38b69e |  | note | Records - Thickness testing with fillet gauge
label | 94e408bf-5699-52f1-9a69-99e3989ec0b2 |  | note | Witness Point
checkpoint-group | cc2fc336-7ef6-465e-81ee-91d792492b39 |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | 5c81173d-376a-4593-ada3-90114182ff76 |  | checkpoint | Weather/RH - 200P Ultra Product TDS
label | 8cdd6254-db03-50f1-8441-f6ea31b09071 |  | note | Apply within 10-35°C RH must be 0-85%
label | 0cc9beab-a9d8-5b94-a2ba-90ffc8ee6ace |  | note | Screenshot - Temperature and weather forecast
label | 7aae2ac1-7bc1-5193-865d-f48b981c55fe |  | note | Surveillance point
checkpoint-status | aa0b9c1e-0a1f-46a8-bb21-51dbc211017e |  | checkpoint | Mixing - 200P Ultra Product TDS
label | 715ca235-a240-5ea6-9f9e-f75f58507566 |  | note | • 200P Ultra should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 2138eeef-d884-56bd-b5ce-843172a8cd24 |  | note | Witness Point
checkpoint-status | 4c1c8e05-ee6d-4b61-9bf0-3ed644f8fd87 |  | checkpoint | Application - 200P Ultra Product TDS
label | c35bcc2b-d2c6-5a71-9171-5503c6eefcf3 |  | note | • 200P Ultra to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | 72bed02e-66cb-5d1f-99ce-e4f75c2f68f6 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | d6a7e0c9-e6e3-58dd-9f76-6851a73a9f4a |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | bb3368dd-909d-55ba-9d50-170be29a65eb |  | note | Records - Photograph
label | 03d891fd-a999-5883-a534-d74c9e84f0ee |  | note | Witness Point
checkpoint-group | 33b8e594-d8ca-4f6d-9255-5c2612e8a2ee |  | section | SECOND BASE COAT- EACH LOCATION
checkpoint-status | 5add17fc-afd1-4c91-948e-68787218e232 |  | checkpoint | Weather/RH - 200P Ultra Product TDS
label | c48bed4b-8bbd-5f39-8fde-1db04250de8b |  | note | Apply within 10-35°C RH must be 0-85%
label | 584fd6cd-a371-5a77-982e-d56ae4758367 |  | note | Screenshot - Temperature and weather forecast
label | 213d1898-6fed-566f-9aa5-da2be5ad571f |  | note | Surveillance point
checkpoint-status | fb0609aa-00c8-48f5-8867-074563143d23 |  | checkpoint | Mixing - 200P Ultra Product TDS
label | 61f7b4b1-6a85-5797-8a6b-bb8b8f7cacfe |  | note | • 200P Ultra should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 8c0a13ce-32db-5146-9a50-5230b46c6203 |  | note | Witness Point
checkpoint-status | 2135a7f8-7fc6-4716-bf3b-733083db7099 |  | checkpoint | Application - 200P Ultra Product TDS
label | 5b01bcd7-4742-5642-adc9-42045d5c40cd |  | note | • 200P Ultra to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | 8bf300f6-578a-59b1-a65c-8a5b31f5f56f |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 2d9c854c-7636-5500-8f02-ac4b051498e6 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 47dae2dd-e877-5c32-9881-b7e0bd54343c |  | note | Records - Photograph
label | ad60a143-2ea2-5852-8401-44b5307b3918 |  | note | Witness Point
checkpoint-group | 9d36b8b6-2f71-494a-9eb9-9653dfff4386 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | b7f687d3-b843-4a0a-af2c-0de80da96b3a |  | checkpoint | Inspection
label | 0af295ec-eb5d-56b1-bc9a-0de1a641c758 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | f2f4e0b4-b19f-5c72-946e-d1a913d52bf9 |  | note | Records - Photograph
label | 798a6739-8758-579a-8ab9-b70adff90ee3 |  | note | Witness Point
checkpoint-status | cedd5643-88ed-4b0e-a3e8-d0cf70313720 |  | checkpoint | Thickness Testing - Delfasco Positector
label | 6840c5a7-c080-56ea-8977-2a82fb942ccb |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | e5134ed3-f124-5e4a-87c8-7604a22983e0 |  | note | Records - Photograph
label | 1e5eb088-f42a-5a95-8bcc-f64ee8414b56 |  | note | Hold Point
checkpoint-status | 04292306-311d-4b4c-9644-72096401037d |  | checkpoint | Flood Testing
label | 908ccbb4-7982-5052-b900-2f736fd57715 |  | note | Mark water level and conduct a 24 hour flood test for internal wet areas
label | c5b13695-92e4-5fc9-942d-0b49ed231748 |  | note | Records - Photograph
label | 22db6a0d-83bf-5f52-8e88-6f9aaeeb52ec |  | note | Hold Point
checkpoint-group | d00c94ef-6af4-4689-9bce-b6962e2681f4 |  | section | SIGN OFFS
checkpoint-status | e072165f-a6b7-4738-838a-664d7b80d245 |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 1f20c224-2eeb-4702-8e93-0a3d160b73e3 |  | signoff | Subcontractor inspection sign off
checkpoint-status | 073c4cbb-5f5e-4957-b845-12df9b533296 |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | fbb50528-b765-41b5-9a47-f018fec57a2d |  | signoff | Site Engineer/foreman inspection sign off
checklist-flat | 9d0e735b-4bf1-4024-b37b-97e5aa1400f9 |  | checklist | Floors and hobs |  |  |  |  | Yes | zSYS - Floors and hobs | 655260d9-b33b-4b92-8b48-05916f3988e5
checkpoint-status | b6be3656-e2f2-483a-8c7b-8b049ba08ca9 |  | checkpoint | Relevant Australian Standards Checked
text | 88427353-ba64-5a30-b746-e876f33d59ab |  | textbox | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint-status | 08d906d5-8ca9-4659-9a1e-f5324ddc3075 |  | checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | a72a6890-9fd3-58cc-96c5-28b01745415d |  | note | Attach Photo
checkpoint-status | b5b9f00b-970e-41ec-ae18-ae49e24c09fa |  | checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X.
label | 208de54e-d549-5c4b-90a4-ca79e84c69ef |  | note | Attach Photo
checkpoint-status | b6a7e84c-fd28-4e0c-9923-610bc8da8c9c |  | checkpoint | Priming. Apply primer (Enviro Epoxy B-LV / Enviro Prime P2 / Enviro Shield) using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X.
label | 71a948c4-4f33-5532-bb2c-7d84bc2a6ff0 |  | note | Attach Photo
checkpoint-status | 2cb93640-4bb1-4e4e-ab8f-853d6ce53de7 |  | checkpoint | Mixing and Application. Enviro 700X should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT. (2 coats).
label | f94ede14-088d-5def-9d49-10a443024d52 |  | note | Attach Photo
checkpoint-status | 8c6d45da-f381-4c82-b169-574860a7fcb8 |  | checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed Enviro 700X to ensure the membrane is not damaged.
checkpoint-status | 46e9b3d0-0fc9-4890-8029-b62bb879d49c |  | checkpoint | Top Coat. Enviro 250NS should be thoroughly mixed using a mechanical mixer at low speed prior to application. Do not mix in air. APPLICATION: In exposed areas, do not apply if rain is expected within 6hours. Enviro 250 NS can be applied using a roller (6mmnap recommended). Apply 2 coats of Enviro 250 NS (each coat at a wet film thickness of 0.6mm), to achieve a 0.6mm Dry Film Thickness (DFT). Do not apply as one heavy coat. Preferably, apply at 90° to the direction of the previous coat. Ensure that all areas receive a sufficient coating thickness and are free of all defects such as pinholes. Allow each coat to sufficiently dry before proceeding to the next coat. Thicker coats will take longer to dry.
label | 47e97b81-c880-5f4b-9330-ae61527fe57f |  | note | Attach Photo
checkpoint-status | 6913e85c-52b0-4bce-b3e2-86d083e377cc |  | checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | 38d16da1-3356-525c-800f-3e06b3419942 |  | note | Attach Photo
checkpoint-status | 47eee39d-36ea-49d5-9714-73cdbef0c0f7 |  | checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | 3ce8483d-1ab3-4c6c-914c-8f9641037421 |  | signoff | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-sectioned | 51ee64d3-ab99-4c23-91fb-cc2dd9720365 |  | checklist | Pre Start Briefing Form V1.0 |  |  |  |  | Yes | Pre Start Briefing Form V1.0 | 7c086190-b1f9-4a22-83cb-dd5acabef41f
checkpoint-group | bc5c390a-120c-42f6-8de2-12e5af988acc |  | section | PRE-START DETAILS
checkpoint-status | efed7beb-30e6-4f28-8547-e67c6014fa46 |  | checkpoint | Attach any relevant documents or photos
date | 240c5141-196d-5cb9-80cc-f32015af66ad |  | date | Date:
text | 7aa72205-e208-5066-9208-6bb617beeb98 |  | textbox | Time:
text | cebc36c3-4442-50fd-b749-91c0d1b9b1e5 |  | textbox | Location:
text | 6467baba-a79d-5ac4-b3f2-151c50d11da9 |  | textbox | Works Supervisor:
text | ad9b1fdb-f9ac-57f3-91f2-ccbbda17d1cd |  | textbox | Client:
text | fc21b8b7-aafd-55f7-aa27-796467119132 |  | textbox | Representative conducting meeting:
checkpoint-group | 24d27f0b-db7a-4405-b551-b0c7b0a452a3 |  | section | LAST WEEKS ISSUES
checkpoint-status | b724f9ce-cbb9-4ee1-9182-cbb0518bd5f0 |  | checkpoint | Issues arising from previous day?
text | 4b7c4efe-cf64-54a7-92cc-b080aac1e8ef |  | textbox | Issues from Previous day:
checkpoint-group | 90eb79c5-88ca-44fb-a491-d7087f0955ce |  | section | PLANNED WORK ACTIVITIES - DAILY
checkpoint-status | b9f5dab4-9398-43ac-baa6-9423dfdf48dd |  | checkpoint | Work Activities
text | 24f32913-faa1-5e9e-a5e0-b473ef636fae |  | textbox | Activity 1
text | cc9c29d0-4891-5e02-9027-55231338209f |  | textbox | Activity 2
text | b8598ddf-9f53-5441-95c2-a542d80d4786 |  | textbox | Activity 3
text | f96fb439-859b-5067-961f-542fcfe9dbe6 |  | textbox | Activity 4
text | 8f192723-b827-5ab1-8c56-23a7c04803e8 |  | textbox | Activity 5
text | 96c63ec5-64ce-5657-b4f0-2b624b03a9e0 |  | textbox | Activity 6
text | a00932ad-8117-5a8a-b21c-9c5b9884eaf7 |  | textbox | Activity 7
text | beb1e468-192a-5eae-8ed0-01594b7c712c |  | textbox | Activity 8
text | 56b50cad-da18-56ca-9062-0fafde0beaaf |  | textbox | Activity 9
text | 9f7c61f3-02de-5266-84cd-fcc21b5af558 |  | textbox | Activity 10
button | eb1fcc6c-4d92-5fc9-84e9-8954ced6f593 |  | button | SWMS in place for all activities ? | Yes, No
checkpoint-group | 602ba57c-7273-48e6-b19d-f6038c347ef3 |  | section | SUBCONTRACTING
checkpoint-status | b0a96c3a-5535-46cc-a684-353b1c5f039e |  | checkpoint | Subcontractors on Site
button | 72c3ea14-9dd1-563e-af6d-2d9e9ea8a5d9 |  | button | Are you subcontracting out any works today will you be interacting with other trades? | Yes, No
checkpoint-group | 65581459-9f61-49f9-bf61-18230d53775c |  | section | ENVIRONMENTAL AND HAZARD CONTROL
checkpoint-status | 074bc3b7-847a-4a3a-9825-01b0a4b682f5 |  | checkpoint | Environmental Control
text | 0679a8f7-e34b-52b4-96f3-1ee0263d981f |  | textbox | What controls are in place to manage envionmental risk on site, specific for today?
checkpoint-status | 6dd777c5-e57e-4a33-884a-fe0ae53a1ac0 |  | checkpoint | Hazardous Substances
text | c9e37a58-9ea7-59f5-961d-9ad069c92dee |  | textbox | Are any hazardous substances being used or will be brought to / or stored on site today?
checkpoint-group | f54b93e0-b594-46a8-a653-546f3118dfb8 |  | section | ACTIVITY CHECKLISTS
checkpoint-status | 27cca62a-5604-4311-8a58-c6a2a13f1e0e |  | checkpoint | Daily Risk Assesment
select | a879f08b-1a5b-55f4-a747-379d911e7418 |  | dropdown | Work area inspected and safe for staff to enter and work in today? | Yes, No
text | 76b3ea05-6b3a-5ffe-a221-7214f0d35aec |  | textbox | Indicate number of people in your work group
checkpoint-status | bb7ed79c-2a3e-4fe5-89e4-4274016376e6 |  | checkpoint | Qualifications/training of staff adequate for work activities
select | 49b75400-2e1b-5f6f-b65f-1ac166fc0659 |  | dropdown | Appropriate and adequate PPE supplied to work teams? | Yes, No
text | 45c68fca-b4c7-5022-8849-585113713a6e |  | textbox | Indicate number of workers allocated for todays clean up after works completed
checkpoint-status | 4dbb9321-cadc-4ba6-8c82-75767c95b78f |  | checkpoint | Plant and equipment on/off site
select | b8612596-8972-5656-91b2-81f8111d9f31 |  | dropdown | Weather conditions for work to be conducted assessed | Yes,no
select | beccc4c4-151b-56c3-aeaa-c3f6e11fe520 |  | dropdown | Pre-start consulted to all work teams including subcontractors and Trade listed in section 4 | Yes,No
select | 372fcc76-3c5a-527e-8c25-bc6c9f4450eb |  | dropdown | Equipment safe to use | Yes,No
checkpoint-group | 44ace7cd-f6b2-4589-9920-65bb783a652b |  | section | BUILDERS BRIEFING NOTES AND GENERAL NOTES
checkpoint-status | 0f725f60-6052-438c-8323-51ed506c421d |  | checkpoint | Builders Briefing notes
text | c1c53609-39bd-5d96-8501-e8350c299ed4 |  | textbox | List builders notes if applicable
checkpoint-status | 665bebbc-b9b8-4bb3-917c-e5ccf161bd7d |  | checkpoint | General notes
text | ea79ff2c-c375-5e48-bb0c-99acd86c5163 |  | textbox | Today's general notes
checkpoint-group | df2d4db2-b26c-4fb8-a8fd-1d3b8383e9ab |  | section | ATTENDEES
checkpoint-status | 27814d65-5fc4-47b9-b1a6-36f57c7314bf |  | checkpoint | Pre Start attendees
text | 7d8d51fd-350c-57fe-8022-daf535d9d7e0 |  | textbox | Attendees
holdpoint | d72d15cc-9244-470f-bd1d-6e50102ef20a |  | signoff | Attendees sign off
checklist-sectioned | 1246b9db-dc36-437c-b790-7851a1d56948 |  | checklist | FATRA - V1.0 ITP |  |  |  |  | Yes | FATRA - V1.0 ITP | a107eebc-0352-4053-9bf6-b006a6b59831
checkpoint-group | 81526c65-6695-4df8-9e47-eb68218c3a40 |  | section | DETAILS
checkpoint-status | 630683d2-eff2-4ace-b568-06904e5b7933 |  | checkpoint | Attach any relevant documents or photos
text | 266b0e68-81b1-53c5-9012-d39210f77446 |  | textbox | ITP No.
text | 7437d6c6-0c47-5af7-8313-043d36ec5be4 |  | textbox | Revision No. & Date
text | a74d8be7-700b-5f92-801a-25e1aab56017 |  | textbox | Prepared By
text | 8b927b52-1eb5-5d61-81bc-557d58780a71 |  | textbox | Reviewed By
text | 79d9552b-193c-55ef-8181-0c87fbc35812 |  | textbox | Approved By
checkpoint-group | 90eb935e-c413-4250-9977-acf24ebeebab |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 9c1d51f3-9e8e-46b6-b5be-c441b1c31c77 |  | checkpoint | FatraBond Adhesive
label | f4eb9c3e-0347-5757-8ef2-562bcd2b691a |  | note | Records - Time stamped photograph
select | 6c93fe70-3084-5110-9199-16336ca9b7f3 |  | dropdown | Inspection | Surveillance point,Witness point
holdpoint | e31fe8cf-a04f-4382-910d-c1d25b2035bd |  | signoff | Subcontractor and Site Engineer/Foreman sign off
checkpoint-group | 2800c770-2fc0-4a43-8bec-81d7ed896683 |  | section | PRE COMMENCEMENT- EACH LOCATION
checkpoint-status | 8127976f-c3bd-4a19-9974-1a330720df24 |  | checkpoint | Samples Submitted
label | 81b5e898-c2da-588f-9e0c-a8c7893471bd |  | note | Submit samples for approval as per Specific Material Requirements.
label | 88dfd791-a17f-599a-b3d3-49713fcbeba2 |  | note | Sample Approval Ref.
checkpoint-status | 824f8306-11f4-40fa-9a8e-d84628a2c3a1 |  | checkpoint | First Of Type Inspection
label | a78e94e1-d5d3-5e45-860b-fbe7eb67960b |  | note | First of type of inspection conducted prior to commencment of works taking place.
label | b5132a29-c847-5019-bc7d-060534018eac |  | note | Document Ref.
holdpoint | 97be3a2b-aaa0-4b78-8d1b-0556a7dea4f5 |  | signoff | Sample Submission / First of type inspection - Site Engineer Sign Off
checkpoint-group | a96168f5-238d-4c64-9b3e-27e1d89c9187 |  | section | APPLICATION - EACH LOCATION
checkpoint-status | 5d1aa6a1-e227-45e0-9b11-5134639bb1cc |  | checkpoint | FatraBond Adhesive
label | ac2208b3-2aa2-56d5-a1bb-0386c4866bc1 |  | note | Apply adhesive consistently over required area using squeegee/rollers
label | cc305264-0071-5789-8803-72ae8a497661 |  | note | Adhesive is applied consistently and evenly across the surface to achieve correct adhesion
label | cc6cbb15-639d-5513-85ce-c04beb472da6 |  | note | Adhesive does not spill onto membrane, weldable laps or surrounding areas that can potentially contaminate welds
label | 30c41b9c-bd9e-52c5-add5-5c6aeef902a2 |  | note | Records - Time stamped photograph
select | 1453c71b-0860-5d04-86c3-c0bf1809fb37 |  | dropdown | Inspection | Surveillance point,Witness point
checkpoint-status | 7d700bbd-8856-4fb7-99ee-48aed30857d9 |  | checkpoint | Install Fatrafol PVC Membrane
label | f5314f82-9435-5226-ae22-4ae7f9149a8c |  | note | Install Fatrafol to coincide with the falls of the roof
label | afe50769-e6bf-590d-bbd0-00d5552f8ac4 |  | note | Ensure the membrane laps run with the fall of the roof to minimise negative laps on the roof
label | 27e04eca-8ff6-5940-b595-859e3cb8bbe1 |  | note | Records - Time stamped photograph
select | e5ebb07b-c368-5ae3-bf77-4b829c8ff45a |  | dropdown | Inspection | Surveillance point,Witness point
holdpoint | 3feaff41-f8c9-4036-bfcc-42d1d0ea60b9 |  | signoff | Subcontractor Inspection - Sign Off
checkpoint-status | 8b7550b2-d9af-4560-b820-9358d3733585 |  | checkpoint | Builders Application Review
holdpoint | f0e2dbb6-5f96-466c-999b-7ad0b5b11e38 |  | signoff | Site Engineer/ Foreman Inspection - Sign Off
checkpoint-group | 1ec3a443-18a8-434a-9aa1-b1fce0659f79 |  | section | DETAILING - EACH LOCATION
checkpoint-status | 88ab1e53-8fd8-4678-85e9-5334c9b68545 |  | checkpoint | Hot Air Fusion Welding of PVC membrane.
label | b0ffc153-1957-5a98-82d0-0b13aa9b8685 |  | note | Hot air fusion weld overlaps.
label | 59dda9e2-5955-5bd7-8748-e621ef680d70 |  | note | Achieve a minimum 40mm wide weld width on all hot air seam welds to achieve sufficient weld strength
label | f17c2d28-d14f-5b6a-b684-8142bcec3681 |  | note | Records - Time Stamped Photograph
select | fa7dbb91-c681-59f2-bdc8-392eb302765d |  | dropdown | Inspection | Surveillance point,Witness point
holdpoint | 1168b7a6-a213-4ba2-b419-931bd7da8cee |  | signoff | Subcontractor Inspection - Sign Off
checkpoint-status | f0fcf5aa-c043-47a7-aafa-45048f9c4694 |  | checkpoint | Installation of PVC Coated Angles
label | 9d80e734-218a-5dcc-966a-31f217d0be39 |  | note | Fixing Fatranyl PVC coated termination angles using relevant fixings
label | 1ee38694-9fa7-5d8f-8258-8f2baf53018f |  | note | All termination metals are aligned correctly and are not disjointed or protruding
label | d3ed1bdc-beb3-5347-8c78-53c4daccad02 |  | note | Fixings centres do not exceed 200mm centres
label | 5fcb45b5-0d6d-598b-9186-80d9e6272ca9 |  | note | PVC coated termination angles are installed with a minimum 2mm gap between each angle to allow for structural movement and expansion
label | f04af38e-402b-584f-9856-65f782da9ede |  | note | Records - Time Stamped Photograph
select | f29c6b4f-3b5a-53d9-b9e3-f5d4cafbacbe |  | dropdown | Inspection | Surveillance point,Witness point
checkpoint-status | 61712ba5-6697-4b09-9335-9e01e5080978 |  | checkpoint | Builders Detailing Review
holdpoint | 96a2065d-8a91-4956-a5ca-e46beed22f96 |  | signoff | Site Engineer/ Foreman Inspection - Sign Off
checkpoint-group | ddf6e1e1-1d06-4f01-9877-33ff7262dab5 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | dc0a6b26-93ad-41c0-8572-11df5231b972 |  | checkpoint | Inspection
label | 312cfd38-1fdb-59a2-a3bb-255ac75ab301 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | 82a2468b-448f-5c68-afbf-45e9d81f7981 |  | note | Records - time stamped photograph
select | ae8de0b5-83ac-5703-bfc4-9da619e43419 |  | dropdown | Inspection | Surveillance point,Witness point
checklist-flat | 51107eb1-43e4-4575-922d-4163df7c0ed2 |  | checklist | Attachment |  |  |  |  | Yes | Attachment Checklist | b1288afe-704c-4645-a9c5-e7e5216758e1
checkpoint-status | ac024ed1-4b6b-4564-ac26-681eb988b8af |  | checkpoint | Attach all relevant douments and Photos
checklist-sectioned | 647850a9-239f-48dd-a516-0fc8c9d46f2e |  | checklist | HP1200 v1.1 |  |  |  |  | Yes | HP1200 v1.1 | b18055f7-75d4-4848-9213-f049316276fe
checkpoint-group | 9e60da21-8c2b-4365-a9ea-41fd0d885fa2 |  | section | DETAILS
checkpoint-status | 3c8c03e1-055f-488b-9eea-d9af4d643fb3 |  | checkpoint | Attach any relevant documents or photos
text | bcb1673b-7f72-5034-8e38-fc5af6b3924a |  | textbox | ITP No.
text | 55762e25-329a-5d05-ac6a-62c3ae575517 |  | textbox | Revision No. & Date
text | 633b06c3-4cb4-568b-aa06-d99ee6570ca6 |  | textbox | Prepared By
text | f5b8638d-19ba-590f-a65a-216cab30fa2a |  | textbox | Reviewed By
text | c93197b7-35fa-5959-a41d-89a3670bd6f7 |  | textbox | Approved By
text | e7e4c0d8-f822-5668-8278-c185b2a7af4c |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 95225202-8eca-4dd4-94f2-96829b8ba376 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 5b7490a4-c8ac-44a4-b2db-29d91d2549b3 |  | checkpoint | Enviro B-LV
label | 3f3e8f28-cfa5-54e5-92a2-92a4c05235e7 |  | note | Records - Photograph
label | 3bea1d5c-c316-5e71-9885-4553a77eb228 |  | note | Surveillance point
checkpoint-status | 675644c6-8740-4360-be88-93b0e9be1c71 |  | checkpoint | Sika Flex FC/ Enviro Flex FC
label | 895794bd-94e1-56b1-9d19-c390f6efcc5e |  | note | Records - Photograph
label | c0645938-cb5a-5bc9-b90f-a6a49bf27736 |  | note | Surveillance point
checkpoint-status | a6b128d4-d45b-4aa8-8776-ee23da1e6fb1 |  | checkpoint | Enviro HP1200
label | 8e9da402-ead3-5241-9cd0-8295f1fdae37 |  | note | Records - Photograph
label | f4fea7f7-6dc4-5237-a6ed-b6c8983e68e4 |  | note | Surveillance point
checkpoint-group | 6451d256-4e94-42f0-8517-942b7e0ec6ef |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | a696cb36-8464-45f8-aa4b-8630d71af0ae |  | checkpoint | Sample Submissions
label | d5d8c761-ae56-5272-9e61-f948a008f4f3 |  | note | Submit samples for approval as per Specific Material Requirements.
label | 829cb9cb-91ac-5600-845f-e5036c4d7dd7 |  | note | Record Submissions
checkpoint-status | d23129d1-b651-4866-994d-7d00af016e72 |  | checkpoint | First Of Type Inspection
label | 2f9e561d-76b9-575b-a434-abfd346a9620 |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 5bbe2def-8157-566e-ac04-77d235a4334d |  | note | Record Submissions
checkpoint-status | 861df6f6-107e-450f-8d55-d4e807581d9f |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 63a6360f-561d-5922-82f4-201aee1574d7 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 178fb17c-05c0-59c8-910f-6a5efb3ae556 |  | note | Records - Photograph
label | 85ff2ab7-c8b0-51ba-a245-d1ceef0f80ba |  | note | Witness Point
checkpoint-status | b2359c17-5aec-42f3-ab91-904262e6c248 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | f6c4268b-ab7c-524c-80ce-0d8230681d2c |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | a039a111-b7ab-5d35-baf1-2a4e22216ace |  | note | Records - Photograph
label | 52ccd0a7-1fe9-568e-8318-db33a7b60096 |  | note | Witness Point
checkpoint-status | b4df6be4-0b30-4136-95fd-7221a5654521 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | dac3d465-c430-5385-8710-1c47f1d5850a |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | 04f68484-7c42-5f1e-891d-4e26757f076b |  | note | Hold Point
checkpoint-status | 25ee83b4-4664-49e5-99a6-8aadce1b758c |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | e08edd03-fe8d-5e9e-b8bf-05ac32c2ce27 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 0e536bbf-dd39-5676-999e-ba50065beeeb |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | d5b76478-5fc9-5e0a-b730-619babc072d9 |  | note | Records - Photograph
label | e2af1622-5892-5f5e-bf18-61636f8301c1 |  | note | Witness Point
checkpoint-group | 6f56dfdf-a760-42dc-8c08-2a9642c3abad |  | section | SUBSTRATE PREPARATION: AS 4654.2-2012
checkpoint-status | 89120858-8dc2-4a1a-89e2-c8508a82ffea |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | 645df80e-9c8d-5cee-8fbf-3fbc7d6ffa3d |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | f9e6dd1b-b071-59dc-8a4d-3ac47441a3f6 |  | note | Records - Photograph
label | cb59ad95-473b-52de-b281-1e203e62917b |  | note | Witness Point
checkpoint-group | 82bb80ca-998d-4c22-a280-84ca78f984c9 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | c327c48f-da9b-4c08-b158-b35a8db8d3ee |  | checkpoint | Moisture Content - Enviro Epoxy B-LV Product TDS
label | e905f63e-a5be-5a88-ae8f-673c803e9b7b |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 69ddb62a-3201-50f9-b43c-dff5ee36c94c |  | note | Records - Photograph
label | a9b80d17-36a6-534a-9f9b-b7c401b2d565 |  | note | Surveillance point
checkpoint-status | f7b354a2-992e-43fc-87e8-ec3f3bde178f |  | checkpoint | Weather/RH - Enviro Epoxy BL-V Product TDS
label | d8798454-777a-539a-8af2-2caa73a4dd0f |  | note | Apply within 5-35°C RH must be 0-85%
label | 6192267c-612e-5786-9011-5f534fe31b47 |  | note | Screenshot - Temperature and weather forecast
label | 83f36e34-83c8-59d9-b560-efa99e61bd8a |  | note | Witness Point
checkpoint-status | b0bbc677-34c0-4d21-a15f-12539c14437b |  | checkpoint | Product Mixing - Enviro Epoxy BL-V Product TDS
label | 528ab846-2ce7-55ac-b52e-965743ea9746 |  | note | Mix Part A (12L) and Part B (6L) separately add Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached. Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 6b223841-2643-574c-9cd1-bbe361b06266 |  | note | Witness Point
checkpoint-status | 0f88ed98-46df-4e0e-b253-4e068b368c33 |  | checkpoint | Application - Enviro Epoxy BL-V Product TDS
label | b583bd0e-0669-594a-84e3-0c5c987318e8 |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied. Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | bcb5bca4-4f51-5db8-8565-e3dcf26b71a9 |  | note | Records - Photograph
label | 99ad41d8-908a-5131-9964-9942f343d742 |  | note | Witness Point
checkpoint-group | 325500c3-5570-4b26-bce7-964b9ebd81f1 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 9af4872c-2c39-49d2-b4ad-01867a447ca2 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 45ef6657-ae76-5dfe-90f7-0b96af3d9f59 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | c2cdcd53-d088-573e-8488-59bc10aeb4fd |  | note | Records - Photograph
label | be120769-7381-5e5c-840d-0b7f4c056721 |  | note | Records - Thickness testing with fillet gauge
label | c81bfea3-dc9b-5d1b-8b2c-df0c89a59d21 |  | note | Witness Point
checkpoint-group | 23b54766-c51b-4bbe-89b4-fc8aaaaaf7c5 |  | section | BASE COAT - EACH LOCATION
checkpoint-status | c383a38a-f7f5-46ca-8579-2897851924ad |  | checkpoint | Weather/RH - HP1200 Product TDS
label | 1c6ec6e6-eb99-5d5e-8c1b-0980d6e2110f |  | note | Apply within 5-35°C RH must be 0-85%
label | 4b5bee34-d54b-587a-8a60-456d2fbd4a95 |  | note | Screenshot - Temperature and weather forecast
label | 9b7915b6-9fe8-5c5d-b2ca-55ce522fab40 |  | note | Surveillance point
checkpoint-status | 8d362141-dfc8-49c2-9335-17748cc18514 |  | checkpoint | Product Mixing - HP1200 Product TDS
label | 3c7f159d-bffd-51ff-ba6b-1325d08ff1c2 |  | note | Mixing by way of 1:1 mix ratio (by volume) in heated plural component. Mix Part B thoroughly with a mechanical power mixer before use
label | 2c9b5481-2006-5730-8cf4-1d1d79c1fadc |  | note | Witness Point
checkpoint-status | b2b54c87-1542-45fd-b7e6-60697a78301b |  | checkpoint | Application- HP1200 Product TDS
label | 4adb49ae-60ba-513c-851e-68fe1d8e30b7 |  | note | HP1200 must be sprayed using high pressure plural component dispensing equipment - Drums of component must be pre-heated to at least 25C prior to mixing or dispensing
label | 2138e4e9-cc88-5ae9-b14e-31689443c52d |  | note | Records - Photograph
label | 5edd1f3c-1b75-5097-b8e8-30e556e264f0 |  | note | Witness Point
checkpoint-group | 7441f360-c97d-40fe-9d55-99c406e35e6e |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 5bb879d9-8412-47f0-9c09-9c49be4bdd0d |  | checkpoint | Inspection
label | 0e0195d4-487c-5373-845a-e897de45b9e0 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | 61c87ce9-a4b7-5655-9dc0-a9dcd6f2e8a8 |  | note | Records - Photograph
label | b8124408-ed1f-568b-883f-cfbe65fbccd5 |  | note | Witness Point
checkpoint-status | efd19511-669b-401a-a14e-8b70378e99eb |  | checkpoint | Thickness Testing - Delfasco Positector
label | 15536a75-746b-5f77-9a95-4c750353314a |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | 11d0e056-edcc-5a40-9eb4-a7df54a3cc73 |  | note | Records - Photograph
label | 140c79eb-ee33-5b72-abf1-32fad5d6e231 |  | note | Witness Point
checkpoint-status | 167e59f9-eb25-41a1-8a29-2b4f9affb60d |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | 9d041e4e-afb8-58e4-8dc6-d327bcbe1662 |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | edca13bf-2624-5d63-bba5-7f1f8d00e740 |  | note | Records - Photograph
label | e93147f0-96ac-53f4-8f61-b3fb4d6a507c |  | note | Witness Point
checkpoint-group | 5aeda48f-d1ce-4087-8478-53d0faa620dc |  | section | DETAILING- EACH LOCATION
checkpoint-status | ccb230d1-982b-401b-ba78-33c92bd7469d |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | a543e2ac-ab39-51d3-95dd-54e1ff55fdb5 |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | 4df611bb-415a-542a-a24c-42a69f00361e |  | note | Records - Photograph
label | 1c7f6c5b-6cfc-5916-a1ab-bea74425a7e2 |  | note | Witness Point
checkpoint-group | 1f855787-79d6-4110-84f1-18b6d8819025 |  | section | SIGN OFFS
checkpoint-status | d7819dcf-acf9-44d0-9e99-61704f068d0c |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 65af2249-2ece-40e2-90e8-9bcf96f9bb43 |  | signoff | Subcontractor inspection sign off
checkpoint-status | b059399f-f122-4b40-a276-f343ef59355f |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | ecea4fe2-30de-4084-b997-0bfad3ccdcc3 |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 64da0051-ef61-4c2c-9895-014121c12e51 |  | checklist | WB Primer + Enviro 200P V1.1 |  |  |  |  | Yes | WB Primer + Enviro 200P V1.1 | be501a7d-59a9-40cd-aac9-bdaf0ef4cdd6
checkpoint-group | 59ad9cae-2e72-40bf-8ce2-676ef591d9d6 |  | section | DETAILS
checkpoint-status | 3903171a-d9d6-48d3-bf82-8d9514921e17 |  | checkpoint | Attach any relevant documents or photos
text | 12541abf-bc66-5a9a-988e-640ca61121af |  | textbox | ITP No.
text | abb7dfd0-5bce-524e-aa9d-98294bbb2ef4 |  | textbox | Revision No. & Date
text | 119660d3-3c24-5110-bf33-4d7836abb1e4 |  | textbox | Prepared By
text | 40c2ca93-cd9c-58dd-abc8-fa9d0508abe0 |  | textbox | Reviewed By
text | 6b18ddec-50d2-55d3-a578-a72dfee3b8f3 |  | textbox | Approved By
text | 07f6bb1e-9878-5952-8752-9dd047374c92 |  | textbox | Suppoting documentations - E.g location, CIDD alerts etc.
checkpoint-group | c6354295-3c32-4907-b96c-a3a1984f0b43 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 518b8a77-efd4-4572-bdbd-264efe8e83c4 |  | checkpoint | Enviro WB Primer
label | 0932162d-eac2-5219-a1f9-b624a96756b7 |  | note | Records - Photograph
label | 7e47ca44-5bdd-50fa-910f-52822e00b6d4 |  | note | surveillance point
checkpoint-status | af3a1e22-ae29-4236-afe0-95b86711e8b8 |  | checkpoint | Enviro Flex FC/ Sika Flex FC
label | e679d85c-9c83-5323-a7ea-6e33674a80aa |  | note | Records - Photograph
label | 2e274a1d-764b-5c10-8d48-7f870752db4d |  | note | surveillance point
checkpoint-status | cf580677-00f4-45c3-b48b-b60e8730f78f |  | checkpoint | Enviro 200P Ultra
label | 97e7d2c0-9609-5d29-9e04-e04e9d977588 |  | note | Records - Photograph
label | 827f15b8-a308-533c-95c3-f5ee3a93dad9 |  | note | surveillance point
checkpoint-group | 70a74fd0-05d8-4e18-87d2-406f1446af55 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 3aa4d963-e357-4f4e-9d94-b25c8314355b |  | checkpoint | Samples Submitted
label | 01bc0d82-d636-50f3-b818-b35be6384cfe |  | note | Submit samples for approval as per Specific Material Requirements.
label | e3eb8cf3-377e-5f11-a29c-24c86283476a |  | note | Record Submissions
checkpoint-status | e2a653af-6faa-4a07-ba27-487506c1945b |  | checkpoint | First Of Type Inspection
label | aef2bdd2-9901-59eb-a78d-3eebabb0a4b9 |  | note | First of type of inspection conducted by builder prior to commencment of works taking place.
label | db8cce78-8d4f-57a0-b79e-6df41ccd2b8c |  | note | Record Submissions
checkpoint-status | 1c205105-de3e-42b1-aa10-4a5a57d212b5 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | aebee83b-2193-568b-8ae3-7b57b5b08d29 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | e88c13cb-199f-5c02-a5ac-cd2d33559215 |  | note | Records - Photograph
label | 222eaa9d-8908-5b1b-afef-d41e442f5ba5 |  | note | Witness Point
checkpoint-status | fd84bd7e-aa45-45f7-8d6d-d2341e54dfde |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 153dd7c0-91ae-5359-9c36-1dce4a9f8748 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per PDS before applying the membrane.
label | 4369a212-cdd5-5df3-a707-e64ce08a937e |  | note | Records - Photograph
label | 03e02af0-b393-5e8a-a22b-f83f5143ddca |  | note | Witness Point
checkpoint-status | c014e395-3a11-41c3-a582-7cddc8f23d82 |  | checkpoint | Acceptance of Puddle Flanges - AS3740-2021 Section 4.3.1
label | b1850eee-83ae-54c2-9e3e-daddbe44850b |  | note | All Puddle flanges to be recessed into substrate to finish flush ready for waterproofing.
label | 4cbf4065-9f98-51b7-862c-37563ad5afe3 |  | note | Records - Photograph
label | bdc3c866-5eb8-5e4c-bf22-ae1cce4ef608 |  | note | Witness Point
checkpoint-status | c97e6002-1224-4e23-8d55-8c9a00dcc4fa |  | checkpoint | Acceptance of wall - AS3740- 2021 Section 4.4.4
label | 85df6c93-4bf6-5f9e-90bd-115f48faf8d5 |  | note | FC sheeting to have max 6mm gap at floor/wall junction. Sheets to be set with manufacturers base coat, including all nails, penetrations and corners. Mortar in block work needs to be a flush joint, smooth and level with the blocks, no blow outs of mortar.
label | 00ff07fb-fe9d-5a68-840c-3bf8f617c8a2 |  | note | Records - Photograph
label | b181e113-0276-524f-b853-ce4a0cb9daf7 |  | note | Witness Point
checkpoint-status | 677402ce-2f30-4fd2-942b-2a73b3655bb5 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3
label | 1e1db1e8-0f7f-59ae-aa8a-7997e36cfc40 |  | note | Builder to confirm compliant falls; minimum 1-100 falls and 1-80 in showers
label | 44cfdbb5-d77e-556c-aace-a1a90292696f |  | note | Hold Point
checkpoint-status | 298cdc00-24df-4c98-9be9-02264294dfb1 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | cbef9d38-dca9-50f9-b891-86040a190f1a |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 6fb53e9e-4b54-5c5e-a694-16a65d094791 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | d3909705-2284-5e3a-aebc-f1d701a7f0a8 |  | note | Records - Photograph
label | 3a22052b-7116-5793-9f41-035c116add6b |  | note | Witness Point
checkpoint-group | 2797092e-b87e-419e-b485-79f4ae863935 |  | section | SUBSTRATE PREPERATION - EACH LOCATION
checkpoint-status | 9346b2ed-c41a-4251-8a14-b176ba145d61 |  | checkpoint | Substrate Preperation - AS 4654.2-2012
label | 899cc33d-d2d5-589e-8102-0dbdf0906002 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 60988861-bce4-5114-ba41-21f7210db244 |  | note | Records - Photograph
label | d6a7bf60-295d-55c5-83dd-faf49565ba13 |  | note | Witness Point
checkpoint-group | 04a87f5e-6469-45bc-9369-a1a8df40e078 |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | b1cd3efc-6973-46e6-96aa-71272bf22cca |  | checkpoint | Moisture Content - Enviro prime WB product TDS
label | a192884f-63f7-52be-8ded-c7355aff0932 |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 65987e77-61ec-51fa-b8a3-21e0e197bab4 |  | note | Records - Photograph
label | dead629d-824b-5ca7-b82b-6e9330f9a0cc |  | note | surveillance point
checkpoint-status | 168eb529-ced4-4bfd-a3d5-b37281cb3d02 |  | checkpoint | Weather/RH - Enviro prime WB Product TDS
label | 8b0aee71-2153-535f-8fb8-b6e5c406c664 |  | note | Apply within 10-35°C RH must be 0-85%
label | 5cba8fb4-3fea-52ab-b62c-59b936084135 |  | note | Screenshot - Temperature and weather forecast
label | 2484c446-2c13-5219-82e5-8b741862b1c5 |  | note | Witness Point
checkpoint-status | a6303722-203a-43ea-aff2-f7863e9ad3c2 |  | checkpoint | Mixing - Enviro prime WB TDS
label | 698a9034-0d3f-5635-a02d-38e47513f4ed |  | note | Dilute 1 part Enviro Prime WB with 1 part water and brush/roll out over surface, ensuring a consistent coverage across entire area to be membrane. Allow to dry before proceeding with waterproofing membrane application.
label | 834cda7c-a6a8-51f8-99ae-e95e66f8d4cc |  | note | Witness Point
checkpoint-status | 5194efbf-adb6-4d26-a3b3-fd5cd5ab49cf |  | checkpoint | Application - Enviro prime WB TDS
label | cdc62a4b-a610-5985-862b-54efc1782481 |  | note | Apply primer using a brush or roller.
label | f8543899-3bbb-5c8b-8b4a-ddda61f42263 |  | note | Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface.
label | c1aa3fd6-0ce6-51fc-bc0a-a1432230fcad |  | note | Ensure Primer is dry and tack free prior to next coat.
label | 1b8e4879-de34-5dc3-8a84-1fcb75908cab |  | note | Records - Photograph
label | 7724b66b-f48a-550e-b6ec-14eec176fd5a |  | note | Witness Point
checkpoint-group | c157ad5c-406a-46c4-9db6-d6b872b7eff0 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 66baa523-0cf5-498e-88c5-181329f65f47 |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | 393716c8-67ca-5e75-96f5-7b34a297a079 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | c342e971-f05e-5c4c-bb6c-788871e2a212 |  | note | Records - Photograph
label | 8460649e-a7a0-5437-aa37-245f8bbffc60 |  | note | Records - Thickness testing with fillet gauge
label | 19a512e5-cef5-53fc-8f17-95b598e4b67e |  | note | Witness Point
checkpoint-group | 98ee6b51-572a-4f77-a469-e8379fe1a520 |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | 19d1eeb6-f00c-4099-a7f0-393e114d51ef |  | checkpoint | Weather/RH - 200P Ultra Product TDS
label | 16b6eb75-eff1-5d20-b934-b94a947253d0 |  | note | Apply within 10-35°C RH must be 0-85%
label | 83da55e6-f34c-5322-8a83-ccd1f44948e5 |  | note | Screenshot - Temperature and weather forecast
label | ae92c010-e6a2-5b4f-bc27-a280be4477e8 |  | note | surveillance point
checkpoint-status | 9d43874c-f304-4f3b-bc9a-eda49dc3f414 |  | checkpoint | Mixing - 200P Ultra Product TDS
label | 75b06ecf-52c5-51c4-b3cd-c36e38453ddd |  | note | • 200P Ultra should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 2b369691-8ad5-5656-8867-f79091164779 |  | note | Witness Point
checkpoint-status | 6430490a-cba7-4c64-aaf4-07389ac14d39 |  | checkpoint | Application - 200P Ultra Product TDS
label | 7db57ae1-6145-5843-895b-3df8c833e0eb |  | note | • 200P Ultra to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | 663000d8-d761-5534-9c3d-26851958cd4b |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | c6b7f526-fe94-5de7-927c-17be9269318f |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | afbc16dd-2e96-548f-9e80-1e1f6323ffb3 |  | note | Records - Photograph
label | 555c896c-5661-575e-9633-7dbde0caf511 |  | note | Witness Point
checkpoint-group | 12789446-60bd-4f73-aed2-8866d9ff6d73 |  | section | SECOND BASE COAT- EACH LOCATION
checkpoint-status | c4beddb0-81dc-4d9c-b7bc-8630d5c2eb12 |  | checkpoint | Weather/RH - 200P Ultra Product TDS
label | 22049567-77bc-5484-8a51-06d32b5c06b0 |  | note | Apply within 10-35°C RH must be 0-85%
label | b42a5b98-1758-511f-879f-927246920a19 |  | note | Screenshot - Temperature and weather forecast
label | 2c91de5f-6574-5486-94a0-8bd7e70ae940 |  | note | surveillance point
checkpoint-status | 81685f4b-0d35-4134-8a1f-9796e27fbb3b |  | checkpoint | Mixing - 200P Ultra Product TDS
label | 83dc8da3-241f-5a65-ba13-bac08f4dca3c |  | note | • 200P Ultra should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 21fff5e6-746e-5266-83ac-ebcdde2aeb07 |  | note | Witness Point
checkpoint-status | a17fd63f-7cf2-4f5c-a4b0-90499fc6a5f3 |  | checkpoint | Application - 200P Ultra Product TDS
label | ec413e04-eebf-5c68-b228-3a6f8ee4cc5a |  | note | • 200P Ultra to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | ac12d9a3-1175-59e5-a3c0-e7cccde9c57e |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 3cfcef39-087f-56b9-b649-bb4a3b4e75c0 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 7d7204bc-f12c-5e13-9010-63e80007ac4f |  | note | Records - Photograph
label | 051f744d-f6f7-595f-b7cc-dbe282199409 |  | note | Witness Point
checkpoint-group | 96e01518-f838-44b3-9c70-92a7efe36937 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | bdd06dca-43b0-46b8-810c-687fc20cf08c |  | checkpoint | Inspection
label | d7f0bf9d-e624-5c01-9b22-e64304a61e62 |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | b9d0531b-6304-5b83-9c71-5b4d4ff1f79a |  | note | Records - Photograph
label | 447b345c-09a9-5fdd-9b80-43ab2b87d9b2 |  | note | Witness Point
checkpoint-status | dd415471-5cea-4820-93c0-4799739ad57d |  | checkpoint | Thickness Testing - Delfasco Positector
label | 4cddce7e-be0a-57e0-afad-326f1880a44c |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | e34bf64e-a5e5-5dab-a9b9-1597be17b520 |  | note | Records - Photograph
label | fdbc3aee-acec-5540-ba22-5c011ab7883f |  | note | Hold Point
checkpoint-status | 95627faa-e144-4748-8928-408a734c5024 |  | checkpoint | Flood Testing
label | 4d933779-e5d4-5c89-8ddd-c676f6cefe90 |  | note | Mark water level and conduct a 24 hour flood test for internal wet areas
label | 79cd2c18-843a-5b55-9dd1-228b9cbf8cb8 |  | note | Records - Photograph
label | 42251bf3-9eba-53e9-93f4-fa3ee8c70821 |  | note | Hold Point
checkpoint-group | 6afd4467-f6a1-4aa7-9cba-5afd868b4d3a |  | section | SIGN OFFS
checkpoint-status | 4bfc2da2-5634-4060-8aa3-08f8d2583271 |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 3af722b9-490d-4f9f-97d7-76bacd33462a |  | signoff | Subcontractor inspection sign off
checkpoint-status | 5f214a03-4f1a-40a1-b5dd-984662e1ff43 |  | checkpoint | Site Engineer/foreman ITP accceptance Sign off
holdpoint | 7baba8e8-68c4-42d2-ae52-6b57a7c6adc8 |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 913b0894-9e35-4c86-9eba-12017a898e7a |  | checklist | HP1200+ 800TC V1.1 |  |  |  |  | Yes | ZSYS - HP1200+ 800TC V1.1 (old version) | d536524d-632e-4498-85aa-4c6ad38275f3
checkpoint-group | a2b374dd-c3ea-4344-a710-40a124718b6f |  | section | DETAILS
checkpoint-status | 8ea8c904-ba2f-4799-92ca-771519f4458b |  | checkpoint | Attach any relevant documents or photos
text | c677fd9e-90ec-5597-b7c4-f7081676c739 |  | textbox | ITP No.
text | 5f10f0e2-db3a-56cc-bcdf-7a1d24e6282d |  | textbox | Revision No. & Date
text | 3bc64dc0-e763-5373-93ae-ab69060aafe0 |  | textbox | Prepared By
text | 9b53ab5f-6988-54a5-a096-ae2055d130b9 |  | textbox | Reviewed By
text | 33dcb105-0204-5dd6-8c1c-f62cc8af67d4 |  | textbox | Approved By
text | aa19baa0-0d02-5d9b-97d1-1ff7fc258e24 |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 204b7ca4-2d9f-46b1-8f76-f118ccad2ef0 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 98789f39-c8d3-43c8-98d9-591facfbf082 |  | checkpoint | Enviro B-LV
label | b5d25066-dfb7-56a5-9d34-9d9990cf0933 |  | note | Records - Photograph
label | 272ffa94-8cb5-5d3d-a97c-653e156d2e8c |  | note | Surveillance point
checkpoint-status | a19e8de9-bb3f-4010-968d-17b0848d437f |  | checkpoint | Sika Flex FC/ Enviro Flex FC
label | 2bb85d31-6ed3-543d-a25f-f2bb31249b3e |  | note | Records - Photograph
label | 0db88856-b3b9-5814-9363-dc982c3073e7 |  | note | Surveillance point
checkpoint-status | 428a27d0-3b2e-4ea6-a699-8e211f39b5de |  | checkpoint | Enviro HP1200
label | 4a490768-f6d5-579f-814e-1e2ae129a78b |  | note | Records - Photograph
label | fee8f00e-7f52-5815-b1bb-bd22d4a5c13a |  | note | Surveillance point
checkpoint-group | 86a5b5f0-fe8c-4454-b3a1-bd746e6eaca8 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 05bfde05-f935-4466-a64b-627def9a37d9 |  | checkpoint | Sample Submissions
label | 8939434a-e48a-5e15-bfdb-7722b15ab2aa |  | note | Submit samples for approval as per Specific Material Requirements.
label | c7666abc-aba1-519c-b5d7-b1e5ec12a981 |  | note | Record Submissions
checkpoint-status | 79cebcc4-e90a-46a2-933c-2c53c7c916b7 |  | checkpoint | First Of Type Inspection
label | 9a63f344-55c0-592f-a9a9-32de8db1a4f6 |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | ae3319ff-53bf-56e0-9d07-1e1b2fe84890 |  | note | Record Submissions
checkpoint-status | 414c515b-bd63-4346-b86f-0da97c9d372a |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 5f9d5147-3b25-5761-8e48-d0e97c1d2cac |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 119b56f0-bb68-5a5a-8e47-144217990b66 |  | note | Records - Photograph
label | 684ff4d0-1611-5b87-8286-5fc8cd421495 |  | note | Witness Point
checkpoint-status | 95a99b8d-f554-4189-a546-1feb844467db |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | 07a6ddfc-3d06-5280-9748-a4f91787d861 |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | ab2a9768-db7f-5df6-baf2-2ba60c137ac7 |  | note | Records - Photograph
label | 2a6f4170-d745-5d59-865d-187a9ef72613 |  | note | Witness Point
checkpoint-status | f9cb70ba-c850-4e80-92e0-44d7da03c654 |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3 and AS 4654.2
label | e36bdd84-66bb-547c-8fb3-23fe47a6941e |  | note | Builder to confirm compliant falls; minimum 1-100 falls
label | a0a8e474-0537-583a-99cb-d3df63428057 |  | note | Hold Point
checkpoint-status | 9aeaad4b-2c13-43ba-8d47-b6b7ee31de10 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | 8a2cb75e-51fc-5967-8b2a-0833338c5634 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | 9b09a529-e4df-5c85-a0c0-098e3c58442a |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | 5dff9fa3-57ee-50d5-a683-7b5c2d7c3038 |  | note | Records - Photograph
label | 69024259-7c46-5ca8-adee-c2cd4af2bdea |  | note | Witness Point
checkpoint-group | 81407b2e-16cd-45e6-b794-e73e396c880d |  | section | SUBSTRATE PREPARATION: AS 4654.2-2012
checkpoint-status | 0794f92d-96b6-4ef5-9977-fd882ec43bb5 |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | 6ae8cafe-e07e-50c1-9296-0c62d67c29e3 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | ee858f76-beeb-5e11-ba06-8048feb0210e |  | note | Records - Photograph
label | b7b30b3a-2bd7-5752-b59a-5cf263a0d31e |  | note | Witness Point
checkpoint-group | 60982656-ca58-486d-b95a-18346e9d7feb |  | section | PRIME COAT- EACH LOCATION
checkpoint-status | acfb936d-efdc-40c0-8881-bacbcda4956e |  | checkpoint | Moisture Content - Enviro Epoxy B-LV Product TDS
label | a636acbc-5ef4-56e7-824a-f1e37966dcc3 |  | note | Check moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
label | 8c80ae45-ee51-5ad8-a986-b80fc5d4dcf5 |  | note | Records - Photograph
label | d8b6e68c-c8cc-5a50-aaa9-b45395c9d430 |  | note | Surveillance point
checkpoint-status | 4694476f-f033-4043-83e4-12e58b59289a |  | checkpoint | Weather/RH - Enviro Epoxy BL-V Product TDS
label | e432c76f-83dd-5401-93b7-b6b1b3ec2ab5 |  | note | Apply within 5-35°C RH must be 0-85%
label | 66c114d9-4017-5c36-85c6-1fb454f64c28 |  | note | Screenshot - Temperature and weather forecast
label | 35e6c472-fe8a-51c7-b9c1-9096a3ce6be4 |  | note | Witness Point
checkpoint-status | 1fa76620-c1ff-47c8-911f-2ffc054c9c8d |  | checkpoint | Product Mixing - Enviro Epoxy BL-V Product TDS
label | 2dc4e77b-4f67-587c-be0d-bc3cb9ed8dba |  | note | Mix Part A (12L) and Part B (6L) separately add Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed with a suitable mixing paddle attached. Mix for 3 minutes or until uniform with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 8e8c57fa-7311-5295-8462-b835a12819a8 |  | note | Witness Point
checkpoint-status | 654c949f-6181-4d2f-8385-b36c3bc6fdd9 |  | checkpoint | Application - Enviro Epoxy BL-V Product TDS
label | 0c48b623-c736-5b8a-8032-d0748983cf30 |  | note | Apply primer using a brush or roller and casting aggregate for every 5 m2 applied. Applications of excessive build should be avoided, and material must not be allowed to pool on the substrate surface Ensure Primer is dry and tack free (within 24 hours) prior to next coat.
label | 64d3a866-0441-5f56-8d9b-c7d7c9b0cccf |  | note | Records - Photograph
label | aa1a7c40-1b23-53ed-acb5-c1fff1f8c432 |  | note | Witness Point
checkpoint-group | 666fb335-3b43-4a9e-ad1b-1384a2db4341 |  | section | BOND BREAKER- EACH LOCATION
checkpoint-status | 42ffc3bf-5a78-4ca6-8fa7-284dffd83aed |  | checkpoint | Caulking - AS 3740 2021 & AS 4654.1
label | c1a7221c-db53-5655-98d8-a4b2fb4d4676 |  | note | Apply compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. Bond breaker to be tack free prior to coating.
label | dceddac6-4424-5631-99eb-89a05c82bb1a |  | note | Records - Photograph
label | a348a0c6-c412-5a1a-adfd-a28651796f1d |  | note | Records - Thickness testing with fillet gauge
label | d3f696d8-c600-5041-9713-581da2fb5940 |  | note | Witness Point
checkpoint-group | 06f7dc72-e870-4cb2-9fd7-6784f65d2975 |  | section | BASE COAT - EACH LOCATION
checkpoint-status | bb9dc769-9e6d-4665-bc90-e9fbf63df044 |  | checkpoint | Weather/RH - HP1200 Product TDS
label | c8ab3e88-ab4b-5636-9a57-d959a13fc264 |  | note | Apply within 5-35°C RH must be 0-85%
label | 574fd48f-77a7-5744-9ba4-726d0a92e79e |  | note | Screenshot - Temperature and weather forecast
label | 94b8a445-4a7b-5ea2-8526-a5b9d3b6bd97 |  | note | Surveillance point
checkpoint-status | a62e26a8-befd-4a45-afb2-04fad6778123 |  | checkpoint | Product Mixing - HP1200 Product TDS
label | 6acad224-2013-593a-9e6a-940504d6be50 |  | note | Mixing by way of 1:1 mix ratio (by volume) in heated plural component. Mix Part B thoroughly with a mechanical power mixer before use
label | 5ae0f0cd-77df-530b-8dc7-45efb472832c |  | note | Witness Point
checkpoint-status | 7b5ea44b-dd0d-4fd7-9f57-32079ad39726 |  | checkpoint | Application- HP1200 Product TDS
label | f1d8ed66-1a2a-5a93-9833-86c3b82ea116 |  | note | HP1200 must be sprayed using high pressure plural component dispensing equipment - Drums of component must be pre-heated to at least 25C prior to mixing or dispensing
label | 2e30e5ff-a094-5b16-b49c-45550e017c4a |  | note | Records - Photograph
label | 3861fa7b-7eea-5221-8eea-636dbb0bf18b |  | note | Witness Point
checkpoint-group | 9399998a-35c2-4aaf-9fc6-1b0ac3617e46 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 88507454-dc82-4998-b223-88d9d89dcf20 |  | checkpoint | Inspection
label | 6a75d709-2657-5844-b85e-0fdc8e23452d |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | b129beeb-bdc1-5ec8-8c6d-4d8738cccc33 |  | note | Records - Photograph
label | f1797d7d-554b-59fa-abf6-63289f6ecb80 |  | note | Witness Point
checkpoint-status | b7c8448a-59c1-435a-8604-f07fa508e5b3 |  | checkpoint | Thickness Testing - Delfasco Positector
label | e1216d9f-1f1b-568e-a1f7-f81f2ee9dfce |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | bcc6ad48-3f1e-5724-9608-3501f0daf7fc |  | note | Records - Photograph
label | 6aa02cc4-cefe-52c4-9b35-ca8613326fa6 |  | note | Hold Point
checkpoint-status | 6fbfd5b4-2d33-46cf-ae09-2f59ba289b0a |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | 6e88f907-ac27-58cf-b771-324c07f52bd4 |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | 8c82b116-fc47-5d6c-ba59-2a3de936b8bf |  | note | Records - Photograph
label | c04bf167-cdde-5ff9-89b4-6bc80a070fff |  | note | Hold point
checkpoint-group | 642b9643-96fa-445a-8f6a-854411bc662a |  | section | WEAR COAT- EACH LOCATION
checkpoint-status | ab254dde-6cc4-4ff8-95c7-7ca637f05499 |  | checkpoint | Weather/RH - Enviro 900 product TDS
label | 76c675fe-4188-51bd-9d30-b9246b5c9a23 |  | note | Apply within 5-35°C RH must be 0-85%
label | a9399f27-eb28-5f44-bf19-4aca3fb202b9 |  | note | Screenshot - Temperature and weather forecast
label | 43dbebd8-cdcd-51e5-ab62-dc60080c9e37 |  | note | Surveillance point
checkpoint-status | ecbd072d-7a99-4fb2-a6ae-b4201aa426d2 |  | checkpoint | Mixing of Product - Enviro 900 product TDS
label | 88a17ac7-ce54-5797-aad6-e1e5ca8b3f79 |  | note | Mix Part A and Part B separately, before combining. Enviro 900 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) for a minimum of thirty seconds prior to application.
label | 2921df1c-2e56-506b-a65f-fa6cdb164675 |  | note | Witness Point
checkpoint-status | 843f25ff-e3ff-4a88-b80d-f753825cd6a5 |  | checkpoint | Application - Enviro 900 product TDS
label | e94c1c7a-79e9-5bca-a0f0-ea95ab8d1a78 |  | note | Enviro 900 to be applied by squeegee, roller or brush to finished membrane. Aggregate should be uniformly broadcasted to the wet Enviro 900 within 10 minutes.
label | b4ddc7c3-79f3-5c04-b23b-dd89be83ff96 |  | note | Records - Photograph
label | 7cc62c06-a04e-5900-a04d-6f799985a093 |  | note | Witness Point
checkpoint-group | 5024a2ce-917d-4111-9dab-34a20c6f4a30 |  | section | FIRST TOP COAT - EACH LOCATION
checkpoint-status | 7bcc80a9-45bb-49fa-b761-cc4089d69ee6 |  | checkpoint | Weather/RH - Enviro 800 product TDS
label | 40967c25-d278-5f4a-8170-0d30b028c31a |  | note | Apply within 10-35°C RH must be 0-85%
label | aa3553e4-8470-51ef-8723-5deee1ff2285 |  | note | Screenshot - Temperature and weather forecast
label | e7a63d4d-f36d-5199-908d-e432209299b6 |  | note | Surveillance point
checkpoint-status | 6d7aeb72-e392-4609-9aeb-d379ac107fdf |  | checkpoint | Mixing - Enviro 800 product TDS
label | 33308bc0-d421-5d93-aae7-af8eda69ac45 |  | note | Mixing by way of 4:1 mix ratio (A:B) by volume. Enviro 800 TC should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Add Part B to Part A and mix to a uniform colour and consistency of a minimum 3 minutes - allow to react for 10 minutes before application.
label | 7d9bed4d-d929-55b0-8be2-bc5d876473af |  | note | Witness Point
checkpoint-status | eecc30b3-c12b-415b-b6c3-fb39588d8fea |  | checkpoint | Application - Enviro 800 product TDS
label | 3e1f9b9b-55c1-586d-9f93-52f20b09c4ed |  | note | Enviro 800TC to be applied by roller or brush to finished membrane. Allow coat to sufficiently dry ( 24H) before proceeding to the next coat.
label | 3bf406d5-6c09-5ad5-bc54-608d7cc1a8b1 |  | note | Records - Photograph
label | 63616f22-51c9-57ba-a25d-1c90e3056993 |  | note | Witness Point
checkpoint-group | d4da6ab8-b445-4e66-ae05-c2859acf6afd |  | section | SECOND TOP COAT - EACH LOCATION
checkpoint-status | b207f8cc-e1f1-47d1-9a38-8fd91ff730a6 |  | checkpoint | Weather/RH - Enviro 800 product TDS
label | 47d038ba-a91a-5890-be44-cafcda003103 |  | note | Apply within 10-35°C RH must be 0-85%
label | afc382b3-1e2a-55c6-af8b-3e2af3a546e7 |  | note | Screenshot - Temperature and weather forecast
label | 729a8217-a70d-56f7-9bbb-e8e7a3910e10 |  | note | Surveillance point
checkpoint-status | 48f1801f-9caa-4f76-83a6-73eac5efdecd |  | checkpoint | Mixing - Enviro 800 product TDS
label | f1ed70b0-7fa9-5258-a9ee-1f3055ce4139 |  | note | Mixing by way of 4:1 mix ratio (A:B) by volume. Enviro 800 TC should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Add Part B to Part A and mix to a uniform colour and consistency of a minimum 3 minutes - allow to react for 10 minutes before application.
label | 021301e8-d2e3-5528-8b24-60d1a1b5ec7a |  | note | Witness Point
checkpoint-status | 9dc66e77-f363-4c88-b9fe-16fffe0b2d69 |  | checkpoint | Application - Enviro 800 product TDS
label | 2af53c40-9d8e-55c0-b155-e889302b2825 |  | note | Enviro 800TC to be applied by roller or brush to finished membrane. Allow coat to sufficiently dry ( 24H) before proceeding to the next coat.
label | b78c9e40-cabf-543b-ae3e-9cd5a8adfc94 |  | note | Records - Photograph
label | 880b6898-8315-551c-828f-e1d03125a7f8 |  | note | Witness Point
checkpoint-group | 52815233-c701-464f-a2c1-c16bf3c989ab |  | section | DETAILING- EACH LOCATION
checkpoint-status | 05434783-0d90-48ef-be72-bfa5dacde8e7 |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | c0fc4738-fcaf-5335-aa14-1b24857e81ff |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | 65dac52f-de21-52a3-9a6f-41acf1be340d |  | note | Records - Photograph
label | 66093da3-6d12-5223-8850-dc25197ff6b1 |  | note | Witness Point
checkpoint-group | e7f752af-4ef7-4d9a-af28-c7e06ab47012 |  | section | SIGN OFFS
checkpoint-status | aa034768-d5ea-49f7-8d47-ccc9cdb6429f |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | dea3d4e6-df23-414f-ad3c-629ceadfdc5f |  | signoff | Subcontractor inspection sign off
checkpoint-status | 42a903f2-3044-473b-b1a9-d28c4633380b |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | b8ec0511-6539-4e5e-bcca-b7d732e49f7f |  | signoff | Site Engineer/foreman inspection sign off
checklist-flat | 27fd61e7-93f1-4977-bcfb-f92029a8c743 |  | checklist | Spoon drain floor, Upturns and Bandage |  |  |  |  | Yes | zSYS - Spoon drain floor, Upturns and Bandage | e1ab6611-aea8-409a-b3ed-e301a36e0add
checkpoint-status | 7ed004ed-ffe0-4585-ab49-b12558f2c016 |  | checkpoint | Relevant Australian Standards Checked
text | a03edb63-0f6a-5d68-855b-a45ed9a5166b |  | textbox | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint-status | 3d7e6480-0d06-4816-a70b-15a7f2591d89 |  | checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | 3c0f9505-c2c7-52d7-8331-00d53cb71b43 |  | note | Attach Photo
checkpoint-status | 5ff02a41-7843-4347-b6eb-955f765e3da6 |  | checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | b7de31b5-05e9-5140-9ede-12817f391800 |  | note | Attach Photo
checkpoint-status | 66e3f1e2-b5f4-4db0-8329-210c8a90ff3f |  | checkpoint | Moisture Content Test
label | cefab425-53f4-5d6a-bae8-46e6a14bfc1f |  | note | Attach Photo
checkpoint-status | b8fc14f4-4504-4802-b88e-068a788738bc |  | checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | dac7aa62-9ca9-55d2-bc28-d872a0dfa401 |  | note | Attach Photo
checkpoint-status | ecf1f10e-5665-4c05-bdf3-b65fb7c94334 |  | checkpoint | Apply primer using a brush or roller
label | 727b8534-0f6d-5e2d-ac44-6afde01e1d32 |  | note | Attach Photo
checkpoint-status | f4d09dad-9e9c-4b52-90aa-79ae94fdae83 |  | checkpoint | Membrane Application (1st coat) - Apply Enviro 700X using a brush or roller
checkpoint-status | 556a603f-3f6d-4616-9373-d731080bbb04 |  | checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint-status | bdcdef67-05ca-40c2-bd28-e30ed6d366fb |  | checkpoint | Membrane Application (2nd coat) - Apply Enviro 700X using a brush or roller
checkpoint-status | 7fc84f68-7eae-4857-9c4d-7a747afb2dc1 |  | checkpoint | Flood Testing (if required)
label | 6dc5dcab-8e74-5e69-9862-e1beda390f7c |  | note | Attach Photo
checkpoint-status | 6c425d57-94de-4112-9ab5-a103dd68cf20 |  | checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | 242a70eb-491b-42ae-a529-9a97a5eeb063 |  | signoff | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-sectioned | 90a62a6e-9c73-44b9-a100-8ff3d10a6f26 |  | checklist | Sealer V1.1 |  |  |  |  | Yes | Sealer V1.1 | ea2365bb-fd4b-4c80-883d-b8a755d87d1d
checkpoint-group | c83637c9-9347-4d58-a935-ff8e0fc45850 |  | section | DETAILS
checkpoint-status | 5c0677dc-bc89-477b-a107-ee08a4b6f310 |  | checkpoint | Attach any relevant documents or photos
text | 7ec800bf-b2b2-51a3-8843-33a35e2b272a |  | textbox | ITP No.
text | c6551cfb-478d-5a93-881e-1588bbe96f36 |  | textbox | Revision No. & Date
text | 4c8c3232-536b-55be-8377-548b21d9a259 |  | textbox | Prepared By
text | b832cd95-9401-54e2-aa76-8050c535182a |  | textbox | Reviewed By
text | e201e3de-253f-55f9-85b6-98bdd9ae8733 |  | textbox | Approved By
text | bed55091-3e7a-5f29-9afe-63474003509e |  | textbox | Supporting documentations - e.g location, CIDD alerts etc.
checkpoint-group | 5262bb2f-881d-4646-8ae7-0e598960c9eb |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | bd91d28d-ad82-422f-8e33-bc248314ccb2 |  | checkpoint | Enviro Seal WB
label | 54beb843-8a39-5dba-9055-a0e9c6073cbb |  | note | Records - Photograph
label | 51444ccb-b473-580d-885e-9bee680ae344 |  | note | Surveillance point
checkpoint-status | 6d060757-fc2a-41e1-b87a-a66a8ee835e8 |  | checkpoint | Enviro CSH
label | 291b7de9-19f1-54de-9b1f-f835564a76ec |  | note | Records - Photograph
label | ef18c6dd-322d-576e-ab05-7b020d8816f2 |  | note | Surveillance point
checkpoint-group | d760eb08-01c0-4d19-b207-6f4bab47d8f6 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 1e466df4-16b8-4a10-92a4-b39302cb6162 |  | checkpoint | Sample Submissions
label | 4c85ef76-d4e0-577c-8e28-ab2fc4fff6da |  | note | Submit samples for approval as per Specific Material Requirements.
label | 2c28286e-6a41-5341-9cae-068568374daf |  | note | Record Submissions
checkpoint-status | a903351b-14a9-4d3d-bb21-9683c1249e33 |  | checkpoint | First Of Type Inspection
label | 88eebd3a-a4f4-5d8a-8bfa-79a3c6d14890 |  | note | First of type of inspection conducted by builder prior to commencement of works taking place.
label | 587c648f-ade7-5029-b1c4-ef9e42e6a436 |  | note | Record Submissions
checkpoint-status | ce5aa3c1-fa9d-441b-8151-97336e7c3e80 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | e7830ad6-194a-5690-9f71-4db93045a076 |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | 7c115b9e-a94a-5dcc-9547-4b31ea8627a3 |  | note | Records - Photograph
label | cbced163-243f-51c9-9e1f-4cf081a49412 |  | note | Witness Point
checkpoint-status | 612d4df0-f7de-4fb5-bca2-7a860e0e4d78 |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | c33873bb-c033-5ce3-b43b-9576089c3a1f |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per TDS prior to application
label | 768d4519-4c95-5df4-bd70-52b8c035b327 |  | note | Records - Photograph
label | 5d7efb68-5942-5e3d-a1ad-e4d17716b261 |  | note | Witness Point
checkpoint-status | 34acb82c-6a95-4cf3-b797-85fd311cb693 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | 583c1779-53cb-59b9-9b8c-d600c581df2d |  | note | Ensure no substrate cracks greater than 1.6mm.
label | e97f1e70-2d5c-58b2-8f39-d3213da03ed5 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | fbea3d4a-4041-5c90-8724-023235c4754f |  | note | Records - Photograph
label | 0549b0b0-77a6-5ed7-bd6b-7bcba0395ab4 |  | note | Witness Point
select | 97006e57-d98c-5641-b070-b436b144e281 |  | dropdown | Inspection | Surveillance point, Witness point
checkpoint-group | 320015c5-3144-48e0-8cd6-81e3ba511653 |  | section | SUBSTRATE PREPARATION - EACH LOCATION
checkpoint-status | aea39e02-ad01-4b07-9e5b-8504a1567899 |  | checkpoint | Substrate PREPARATION - AS 4654.2-2012
label | 0833596c-8ecc-5173-a882-f545a2dda497 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish profile. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 839eff0a-fea3-532f-ba7b-3d89cf947969 |  | note | Records - Photograph
label | 4df6cdf4-e2fd-5059-b753-43950d214201 |  | note | Witness Point
checkpoint-group | 04c85976-f37e-4144-9af1-a543ddefaabc |  | section | FIRST SEALER COAT - EACH LOCATION
checkpoint-status | 7e133eed-c025-44c5-8fc3-a6c7809951be |  | checkpoint | Application
label | 5173a499-e430-5688-a472-217b6edbac22 |  | note | Spray or roll concrete Sealer on substrate
label | d500855d-0124-5fc0-b4de-46e5b28ab42f |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 1665a09a-383b-52b0-afe6-69b488069a0d |  | note | Records - Photograph
label | f17f9984-a479-5c4b-97f7-e6c4c5d4a790 |  | note | Witness Point
checkpoint-group | 77258b38-63d8-416d-92f1-9ae7783fb563 |  | section | SECOND SEALER COAT - EACH LOCATION
checkpoint-status | e6d33c20-00f5-49d8-8757-2f18b719d568 |  | checkpoint | Application
label | 76b819e3-1e44-5ef7-980c-2924212e34d4 |  | note | Spray or roll concrete Sealer on substrate
label | c410b295-ff04-5489-a116-f22f54486fff |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | db09c422-8612-5277-b02e-9bddb73c91fc |  | note | Records - Photograph
label | 443afa2a-b126-5ef5-8eea-bf204f424b69 |  | note | Witness Point
checkpoint-group | 0e46c44b-0a41-4978-abec-3bea48b60fad |  | section | SIGN OFFS
checkpoint-status | 6ac53e7d-e40d-48f1-96ff-f6e70d5f3f0f |  | checkpoint | Polyseal ITP acceptance Sign off
holdpoint | 2a2f8054-f688-43ff-9b2e-9df030c9d3cf |  | signoff | Subcontractor inspection sign off
checkpoint-status | 7816fbaa-1a82-462e-8294-0317d13786a0 |  | checkpoint | Site Engineer/foreman ITP acceptance Sign off
holdpoint | 7d3f0468-33e8-4803-a3a1-fbef57afc6c0 |  | signoff | Site Engineer/foreman inspection sign off
checklist-sectioned | 783b7258-f366-47a9-9f44-39ce7fff8e5e |  | checklist | Toolbox Talk V1.0 |  |  |  |  | Yes | Toolbox Talk V1.0 | f2b079a0-957e-4b24-a3f9-9aba8544c83e
checkpoint-group | b7b4be9a-393b-44a3-93ed-3de26e0be07f |  | section | TOOLBOX DETAILS
checkpoint-status | 740de648-58d5-43ca-9440-79f7b749aadd |  | checkpoint | Attach any relevant documents or photos
text | fc8badd7-34b9-5194-adf2-abd34e692e3a |  | textbox | Date:
text | 79f03c83-5960-5826-ac55-959edbca2a2c |  | textbox | Time:
text | 4ad620b9-5aa5-5337-a818-8aa39f436d9e |  | textbox | Location:
text | 30158eec-bf6d-52cf-995a-987cf296e0b4 |  | textbox | Works Supervisor:
text | c43851de-7979-56d5-8794-988af176ab19 |  | textbox | Client:
text | 3ee60aa5-97de-52d8-aa9a-99a94cb0392c |  | textbox | Representative conducting meeting:
checkpoint-group | b94bfc78-a1d5-4f65-931c-5bca2a2d9fe8 |  | section | LAST WEEK INCIDENTS
checkpoint-status | 6472c304-0c63-40cc-b955-1bb204f43018 |  | checkpoint | Attach any relevant documents or photos
text | 275b6634-c79d-54e6-bd77-f79b1b5f60cd |  | textbox | Injuries last week
text | 55bc4314-e15c-5390-8a8b-e0d930c8e0fd |  | textbox | Near misses last week
text | 6af4705e-1f5e-5d77-a975-a5bf51fb3a0d |  | textbox | Hazards last week
text | 337c5b6c-2cd0-5548-a62b-22951d152433 |  | textbox | Environmental damages and personal injury last week
checkpoint-group | aba327d1-a294-499e-a9ef-7b6669143306 |  | section | FEEDBACK ON LAST WEEK AND NEW ISSUES
checkpoint-status | a66fa500-3ebc-4fb3-9805-343df996be3a |  | checkpoint | Feedback on issues raised by Work Crews on Previous Day/shift
text | 81cc141e-aaea-5640-b691-48b5a8bf1a2f |  | textbox | Issues
text | 32e0b4ee-8b2e-5767-a9b0-28b9e3fd3e06 |  | textbox | Action
checkpoint-status | b44c6c46-938c-40f3-867d-89ab3101fbe7 |  | checkpoint | New Issues Raised
text | 074a1265-174e-522b-b335-24be21b82405 |  | textbox | Issues
text | 56b768af-3042-5523-a4e1-40ad3ecd9644 |  | textbox | Actions
checkpoint-group | f65d085d-aee3-416a-be61-c1582add914c |  | section | ATTENDANCE RECORD
checkpoint-status | 3cb24e58-5794-4b49-96fb-7e93e615bdd1 |  | checkpoint | Toolbox talk attendees
text | 0af714cd-e529-5354-a047-ecf4bfe461d0 |  | textbox | Attendees
holdpoint | 82ded4d2-ee34-4937-a62f-db840bf798de |  | signoff | Attendees sign off
checkpoint-group | f99e174f-26ec-42f3-b957-823290518795 |  | section | DIARY
checkpoint-status | 804b6e4d-3497-4c10-8a8c-562252f1881d |  | checkpoint | Diary Report
text | ebb7a6ff-1561-59de-a1e3-aed9a2cf820a |  | textbox | Diary report database
checklist-sectioned | d073174c-9abb-4f7b-873b-da75dc766147 |  | checklist | Enviro Shield+700X+250NS |  |  |  |  | Yes | Enviro Shield+700X+250NS | fc827235-59d5-4c07-81cc-9ca8c179b53c
checkpoint-group | d9e50859-9ffc-4269-8c6e-416ec282f0d3 |  | section | DETAILS
checkpoint-status | 9b493975-6489-412b-9021-9badcce5fe61 |  | checkpoint | Attach any relevant documents or photos
text | 2b0c4c47-8c63-5a5b-8086-bf9bf4b16e11 |  | textbox | ITP No.
text | fba97ef3-74ae-5a94-8245-b6281a62186d |  | textbox | Revision No. & Date
text | 7f60d9b4-c9ba-503f-acb2-a6915a15e959 |  | textbox | Prepared By
text | 69f00166-0b44-5ec2-855f-ae1e52e0250a |  | textbox | Reviewed By
text | 47c5cdfe-904e-5fd0-b574-84be2620b7c0 |  | textbox | Approved By
text | 56ac05ec-482f-50ee-a3ff-d70327692656 |  | textbox | CIDD Alerts
checkpoint-group | 06dfad36-933a-4c61-bea9-02d0e24faff7 |  | section | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
checkpoint-status | 2357b9fd-0624-4566-bc47-5b6eb2bccc6e |  | checkpoint | Enviro Shield
label | 63dca091-7e53-5f5d-b070-054f91497cd4 |  | note | Records - Time stamped photograph
checkpoint-status | 55964aab-9e41-4ae9-997d-c0ddd8487cf0 |  | checkpoint | Enviro Flex FC/ Sika Flex Pro
label | 34072947-012d-5051-98d3-79048a2de2dd |  | note | Records - Time stamped photograph
checkpoint-status | b555c834-548e-4b96-865b-5a723a8b90b0 |  | checkpoint | Enviro 700X
label | c3bae4da-bd16-5e91-b7cc-ede5f839c299 |  | note | Records - Time stamped photograph
checkpoint-status | 49e6a864-baeb-4eb1-bf85-504edf1124e4 |  | checkpoint | Enviro 250NS
label | 5a923d05-32d3-5621-a8b5-ce379741c928 |  | note | Records - Time stamped photograph
checkpoint-group | 22018c46-aa69-490e-8211-8564dad06301 |  | section | PRE COMMENCEMENT - EACH LOCATION
checkpoint-status | 5a3670a2-df18-4284-a613-be608ea14bb1 |  | checkpoint | Samples Submitted
label | 5822f18e-2726-5481-be70-a0d6b48027f3 |  | note | Submit samples for approval as per Specific Material Requirements.
label | c73a042d-af94-5bfa-97d0-73b2eb5d36e0 |  | note | Records - Subcontractor Contracts Admin Confirmation
label | e94b261d-4cf3-56bc-b7c4-b1ea8ea80d89 |  | note | Sample Approval Ref.
checkpoint-status | b241c8b5-63fc-4c40-865c-06e278260992 |  | checkpoint | First Of Type Inspection
label | f5b79c3e-91d9-5ba7-a335-c2b85341ff5b |  | note | First of type of inspection conducted by builder prior to commencment of works taking place.
label | 2f7cb740-1639-5397-9b4e-2ad8281a75cd |  | note | Records - Site Engineer/ Foreman Confirmation
checkpoint-status | cca9962f-7932-44f1-afd6-3605060e0170 |  | checkpoint | Material Management & Storage - Envirosystems TDS
label | 7049bf4c-0705-53b1-bc06-836dd1ef3bcf |  | note | Store materials in a dry, clean place away from direct sunlight as per TDS
label | dff930e6-22bd-5bdf-8669-68f3c8fdc776 |  | note | Records - Time stamped photograph
checkpoint-status | 3ff87df4-0282-4396-bd3a-5dc3cb25697d |  | checkpoint | Acceptance of Substrate - AS 4654 .2.2012 Section 2.5
label | a8ece500-cfdb-5047-b1bf-8458ebe246dc |  | note | Obtain clearance for work initiation. Ensure a smooth substrate without protrusions, voids, or formwork distortions. The substrate should be free of honeycombing/bug holes. Patching products must be fully cured as per PDS before applying the membrane.
label | 5f0e2fd5-c631-5914-8a88-057dbc60cf96 |  | note | Records - Time stamped photograph
checkpoint-status | 28f4cab8-d57d-444c-b0ff-45eeac1b7286 |  | checkpoint | Acceptance of Puddle Flanges - AS3740-2021 Section 4.3.1
label | 9b8258df-31e3-578b-83ae-30349ffc9c56 |  | note | All Puddle flanges to be recessed into substrate to finish flush ready for waterproofing.
label | 978e451b-5cbf-5a1f-b548-0875595d04c3 |  | note | Records - Time stamped photograph
checkpoint-status | 0919d79f-5886-4b91-bec2-1b7bb0c1e61d |  | checkpoint | Acceptance of wall - AS3740- 2021 Section 4.4.4
label | ade8689c-825f-5331-a145-e1becd1e0a70 |  | note | FC sheeting to have max 6mm gap at floor/wall junction. Sheets to be set with manufacturers base coat, including all nails, penetrations and corners. Mortar in block work needs to be a flush joint, smooth and level with the blocks, no blow outs of mortar.
label | 7e746a64-ec86-56f0-8e30-b19743aa1aa7 |  | note | Records - Time stamped photograph
checkpoint-status | 5b6c1971-2b8d-49b0-b5b3-a8eda0139afe |  | checkpoint | Falls in Substrate- AS3740- 2021 Section 2.3
label | c91cfb91-b1af-566e-b9ef-9c234608077d |  | note | Builder to confirm compliant falls; minimum 1-100 falls and 1-80 in Showers
label | 483d5d2a-2eb6-5ef5-8905-d7524987c1b6 |  | note | Records - Site Engineer/ Foreman Confirmation
checkpoint-status | 650b3ebc-b537-41ad-bcb1-87e6a1335766 |  | checkpoint | Cracks in Substrate - AS2870 Table 2.10
label | dee66601-3f27-5b3b-afe5-acdf3a50ed22 |  | note | Ensure no substrate cracks greater than 1.6mm.
label | ea6abe6e-8f2e-5a34-9118-1ef76bf322b7 |  | note | Cracks of 1.6mm and over, movement structural joints, cold joints and Live cracks are to be referred to engineers for treatment methodology.
label | 9d355b54-21e3-5b56-b276-00683d4479fc |  | note | Records - Time stamped photograph
checkpoint-group | a7ce829d-0b32-431b-99c8-654373cf3e61 |  | section | SUBSTRATE PREPERATION: AS 4654.2-2012
checkpoint-status | 85fb51fc-44c1-4300-8031-cf902c3594ac |  | checkpoint | Substrate Preperation - AS 4654.2-2012
label | 2ff43137-6f35-5ef1-a62f-fc77a28d1763 |  | note | Ensure Surface is prepared to receive primer application. Clean substrate so that it is free of mould, paint, sealers, coatings, curing agents, loose particles and other contamination or foreign matter that may interfere with the adhesion. Achieve CSP2 and CSP3 Concrete finish. Remove all sharp edges including screws, nails and concrete/mortar projection. Steel surfaces should be treated with appropriate degreasers, then grit blasted and/or wire brushed where necessary.
label | 5d269a90-4cf6-5754-b34a-2cd3a0edd599 |  | note | Records - Time stamped photograph
checkpoint-group | 36d9fa6a-826b-44df-a75a-1180b3183bc1 |  | section | ENVIRO SHIELD- PRIME COAT
checkpoint-status | f542016b-5ba5-406a-b0c3-9675fd654fce |  | checkpoint | Moisture Content
label | d864d720-1235-52ca-a3c6-1a9499c74105 |  | note | Check Moisture content of substrate, not to exceed 6% (Min.1 test per 10m2).
checkpoint-status | 7afd1cc4-751a-48b7-b9c2-945159f90486 |  | checkpoint | Weather/RH
label | a3c8ca93-01ce-55c4-b7a7-81c5c42c92fd |  | note | Apply within 10-35°C RH must be 0-85%
checkpoint-status | ac59bc4e-5101-4bd0-a895-93b8d96066af |  | checkpoint | Application
label | d785c595-cf71-53db-b2b6-9471821edf3c |  | note | Add Enviro Shield Part B (grey liquid hardener) to the Enviro Shield Part A (base Thoroughly mix with a mechanical mixer at low speed (less than 400 RPM) prior to application. Mix for 5 minutes or until uniform. Allow to stand 5 minutes after mixing and then mix again for a minute.
checkpoint-group | 82bc7ab7-5963-438b-8b3d-d90c9c05c8f5 |  | section | BOND BREAKER
checkpoint-status | ad5eeb04-23e8-471f-8fc3-872a31a7012a |  | checkpoint | • Apply Enviro Flex FC/compatible sealant to form smooth flexible cove to all internal corners, penetrations and joints. • This is to be a 12mm x 12mm coved fillet as per AS3740 class III membrane requirements for internal areas and 15mm x 15mm coved fillet as per AS4654.1 class III membrane requirements for external areas. • Allow to cure prior to over coating with membrane coats.
checkpoint-group | 77ebb579-eda4-43fe-b117-9be8442841fb |  | section | FIRST BASE COAT - EACH LOCATION
checkpoint-status | 0ee4d453-c46d-4f73-8f52-b68a40280a25 |  | checkpoint | Weather/RH - 700X Product TDS
label | f5933eea-fc81-54d0-adc6-eacf96982f8c |  | note | Apply within 5-35°C RH must be 0-85%
label | b6f04574-511c-56dd-8244-ac6f84c2291d |  | note | Screenshot - Temperature and weather forecast
checkpoint-status | 16770b98-a0b9-4636-bf42-169e40a861e4 |  | checkpoint | Product Mixing - 700X Product TDS
label | 33c40811-5b9a-5b0e-b1f3-8a301916e104 |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 85fb9bab-b2a8-57fd-8164-cb18c78a2391 |  | note | Records - Time stamped photograph
checkpoint-status | c42c8690-ec61-4209-aa3d-27b87c9a5ad3 |  | checkpoint | Application- 700X Product TDS
label | 48474e39-c72a-5368-af87-36479c2e00bd |  | note | • 700X to be applied by roller vertically on substrate and terminating min 150mm with brush.
label | c5730736-00ee-59ae-a2e1-17ca897a6978 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | c5d80e8d-ec35-57fa-bfcc-43aa3d383c8c |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 8d4310e1-0723-5bdb-ac55-27c6725846a7 |  | note | Records - time stamped photograph
checkpoint-group | bb004a31-c217-4f23-997b-a7ea04e422ef |  | section | ENVIRO 700X - SECOND COAT
checkpoint-status | 1193148d-6048-4167-b987-38723e05effe |  | checkpoint | Weather/RH - 700X Product TDS
label | f39bad85-c959-52a2-8ed6-2f77a99f781e |  | note | Apply within 5-35°C RH must be 0-85%
label | 6c6a625d-6a13-5984-9a8d-8bd88d108bbe |  | note | Screenshot - Temperature and weather forecast
checkpoint-status | 6be50a19-f1da-4c7f-a415-55d21a2cce62 |  | checkpoint | Product Mixing - 700X Product TDS
label | 100ffef3-d652-5d85-a99e-27e40b89f593 |  | note | • Product should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application.
label | 963f40a1-d15c-527f-b542-a2b16bdbf493 |  | note | Records - Time stamped photograph
checkpoint-status | 40a2ab62-f765-45cd-903c-c8281c7574d2 |  | checkpoint | Application- 700X Product TDS
label | 13fc08b7-5acd-5ca8-89a8-451167d64921 |  | note | • 700X to be applied by roller Horizontally on substrate and terminating min 150mm with brush.
label | c53cf857-312b-57cb-be16-f08714f5d596 |  | note | Minimum application requirements set forth relevant Australian Standards to be followed
label | 87fcf22a-8bcf-549e-a3c8-a213d787a641 |  | note | Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | f39b992b-31cd-5093-97b1-d958699d9125 |  | note | Records - time stamped photograph
checkpoint-group | 41f7f3be-7529-45b5-a48c-94de22c329d7 |  | section | QA TESTING - EACH LOCATION
checkpoint-status | 632ecc73-824f-4a63-9b09-aeea79bbcd06 |  | checkpoint | Inspection
label | 0ddba977-931c-5136-ab1f-667cce0ca24f |  | note | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
label | bd9e0186-f148-5060-b6ac-b2ab4a399b8b |  | note | Records - time stamped photograph
checkpoint-status | a4f24abd-61c3-4641-8784-786daa425d0b |  | checkpoint | Thickness Testing - Delfasco Positector
label | 5db19938-63a7-5cf8-b120-12f7d5750b4d |  | note | Thickness testing of application to the recommended DFT of 1.0mm to manufacturers instructions.( 1 test per 10m2)
label | 31a4c59c-64c7-5ad0-b3c8-d108798a6f2e |  | note | Records - time stamped photograph
checkpoint-status | 64c5b459-d2b1-4f2c-a332-74577ce69d87 |  | checkpoint | ELT Testing - Delfasco Holiday Tester
label | 46333504-cd72-5303-8705-abf1029db12a |  | note | Conduct Electronic Leak Testing ( ELT) on area membraned
label | 9a19a2ae-2bc6-5d82-b804-b10076159939 |  | note | Records - time stamped photograph
checkpoint-group | 39ff003d-acf4-47ac-a08e-7b3352716966 |  | section | 250NS - FIRST BASE COAT
checkpoint-status | 38ea6856-bbf1-48c0-9015-7f9b28962209 |  | checkpoint | Weather/RH
label | 8dccba15-6a74-5446-976e-43a0962a59d5 |  | note | Apply within 10-35°C RH must be 0-85%
checkpoint-status | 83d34542-6e0b-46fa-87b9-302b6a72604e |  | checkpoint | Mixing
label | 37c2c3a8-6f55-50c1-a368-453ebacab474 |  | note | • Enviro 250NS should be thoroughly mixed with a mechanical mixer at low speed (less that 400 RPM) prior to application.
checkpoint-status | 6b2366c1-14ac-4a5b-bd77-3dda0f25d6ec |  | checkpoint | 250NS Application
label | c5656a2d-7b2b-5479-bb72-2fd017c3b291 |  | note | • Enviro 250NS to be applied by roller vertically on substrate and cut in with brush on terminations. • Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | d6185143-7c37-54f1-bdfe-85101eaac804 |  | note | Records - time stamped photograph
checkpoint-group | 0c6ae081-ab5b-4eb4-a0cd-d9979881ed1c |  | section | 250NS SECOND BASE COAT
checkpoint-status | 973f4568-cfaf-47a0-b56e-f29a667f0747 |  | checkpoint | Weather/RH
label | 6c008a51-e18c-5914-97a9-4f5a6b8dae47 |  | note | Apply within 10-35°C RH must be 0-85%
checkpoint-status | ba220a3b-5184-4e20-bd62-790229d372ce |  | checkpoint | Mixing
label | f3632f78-ae6a-5d09-a32b-841ee4dfce3f |  | note | • Enviro 250NS should be thoroughly mixed with a mechanical mixer at low speed (less that 400 RPM) prior to application.
checkpoint-status | f4b79dcb-409e-4299-9cb9-91210e348df6 |  | checkpoint | 250NS Application
label | e2d6b4e7-e11f-5891-a6a4-12735a194e26 |  | note | • Enviro 250NS to be applied by roller horizontally on substrate and cut in with brush on terminations. • Allow membrane to dry for 24 Hours before proceeding to the second coat.
label | 5b9f1d50-788f-5254-be84-cfc881e5a1d6 |  | note | Records - time stamped photograph
checkpoint-group | 88c12b46-0d30-4968-8783-832d980664a7 |  | section | DETAILING- EACH LOCATION
checkpoint-status | 5816550b-9388-4897-a607-cec060d31b23 |  | checkpoint | Vertical Termination Detailing - AS 4654.2
label | e1bd67f1-a868-5799-987c-08f1108ece90 |  | note | Ensure Vertical terminations of membrane on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge.
label | b4530b24-4d26-5af3-a173-fb55fd0a2ec2 |  | note | Records - time stamped photograph
holdpoint | d638a0fc-57f1-4336-a308-5080561b1b55 |  | signoff | Subcontractor inspection sign off
checkpoint-status | ceb30b8a-9221-4111-a0e9-f56a02242d7d |  | checkpoint | Site Engineer/foreman Detailing inspection review
holdpoint | 6bf32ff7-abe6-433c-a98d-4a0845b4bac7 |  | signoff | Site Engineer/foreman inspection sign off