## Project Structure
Folder Structure |  |  |  |  | Checklists
Site QA
Decks
Stairs
Stair Core (Tower)
|  |  |  | Basement 2 | In Decks
|  |  |  | Basement 1 | In Decks
|  |  |  | Lower Ground | In Decks
|  |  |  | Upper Ground | In Decks
|  |  |  | Level 1 | In Decks
|  |  |  | Level 2 | In Decks
|  |  |  | Level 3 | In Decks
|  |  |  | Level 4 | In Decks
|  |  |  | Level 5 | In Decks
|  |  |  | Level 6 | In Decks
|  |  |  | Level 7 | In Decks
|  |  |  | Level 8 | In Decks
|  |  |  | Level 9 | In Decks
|  |  |  | Level 10 | In Decks
|  |  |  | Level 11 | In Decks
|  |  |  | Level 12 | In Decks
|  |  |  | Level 13 | In Decks
|  |  |  | Level 14 | In Decks
|  |  |  | Level 15 | In Decks
|  |  |  | Level 16 | In Decks
|  |  |  | Level 17 | In Decks
|  |  |  | Level 18 | In Decks
|  |  |  | Level 19 | In Decks
|  |  |  | Level 20 | In Decks
|  |  |  | Level 21 | In Decks
|  |  |  | Level 22 | In Decks
|  |  |  | Level 23 | In Decks
|  |  |  | Level 24 | In Decks
|  |  |  | Level 25 | In Decks
|  |  |  | Level 26 | In Decks
|  |  |  | Level 27 | In Decks
|  |  |  | Level 28 | In Decks
|  |  |  | Level 29 | In Decks
Stair 04 (South West Stair)
|  |  |  | Basement 2 | In Decks
|  |  |  | Basement 1 | In Decks
|  |  |  | Lower Ground | In Decks
|  |  |  | Upper Ground | In Decks
Stair 05 (RAC Western Egress)
|  |  |  | Lower Ground | In Decks
|  |  |  | Upper Ground | In Decks
|  |  |  | Level 1 | In Decks
|  |  |  | Level 2 | In Decks
|  |  |  | Level 3 | In Decks
|  |  |  | Level 4 | In Decks
Stair 06
|  |  |  | Basement 2 | In Decks
|  |  |  | Basement 1 | In Decks
|  |  |  | Lower Ground | In Decks
|  |  |  | Upper Ground | In Decks
|  |  |  | Level 1 | In Decks
|  |  |  | Level 2 | In Decks
|  |  |  | Level 3 | In Decks
|  |  |  | Level 4 | In Decks
Stair 07 (Parish Core)
|  |  |  | Lower Ground Mezzanine | In Decks
|  |  |  | Upper Ground Mezzanine | In Decks
|  |  |  | Level 1 | In Decks
|  |  |  | Level 2 | In Decks
|  |  |  | Level 3 | In Decks
|  |  |  | Level 4 | In Decks
Stair 08 (School Core)
|  |  |  | Upper Ground | In Decks
|  |  |  | Level 1 | In Decks
|  |  |  | Level 2 | In Decks
|  |  |  | Level 3 | In Decks
|  |  |  | Level 4 | In Decks
External Stair 01
|  |  |  | Pour 1 | In Decks
External Stair 02
|  |  |  | Pour 1 | In Decks
External Stair 03
|  |  |  | Pour 1 | In Decks
Miscellaneous Stairs
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
|  |  |  | Pour 3 | In Decks
|  |  |  | Pour 4 | In Decks
|  |  |  | Pour 5 | In Decks
|  |  |  | Pour 6 | In Decks
|  |  |  | Pour 7 | In Decks
|  |  |  | Pour 8 | In Decks
Basement 2
|  |  | Pour 1 |  | In Decks
|  |  | Pour 2 |  | In Decks
|  |  | Pour 3 |  | In Decks
|  |  | Pour 4 |  | In Decks
|  |  | Pour 5 |  | In Decks
|  |  | Pour 6 |  | In Decks
|  |  | Pour 7 |  | In Decks
|  |  | Pour 8 |  | In Decks
|  |  | Pour 9 |  | In Decks
|  |  | Pour 10 |  | In Decks
|  |  | Pour 11 |  | In Decks
|  |  | Pour 12 |  | In Decks
|  |  | Pour 13 |  | In Decks
Basement 1
|  |  | Pour 1 |  | In Decks
|  |  | Pour 2 |  | In Decks
|  |  | Pour 3 |  | In Decks
|  |  | Pour 4 |  | In Decks
Lower Ground
|  |  | Pour 1 |  | In Decks
|  |  | Pour 2 |  | In Decks
|  |  | Pour 3 |  | In Decks
|  |  | Pour 4 |  | In Decks
Upper Ground
|  |  | Pour 1 |  | In Decks
|  |  | Pour 2 |  | In Decks
|  |  | Pour 3 |  | In Decks
|  |  | Pour 4 |  | In Decks
School
|  |  | Upper Ground |  | In Decks
Level 1
|  |  |  | Pour 1 | In Decks
Level 2
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 3
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 4
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Parish Hall
|  |  | Lower Ground |  | In Decks
|  |  | Upper Ground |  | In Decks
Level 1
|  |  |  | Pour 1 | In Decks
Level 2
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 3
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 4
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
RAC (Residential Aged Care)
Level 1
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 2
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 3
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 4
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
RL (Retired Living)
Level 5
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 6
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 7
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 8
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 9
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 10
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 11
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 12
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 13
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 14
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 15
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 16
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 17
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 18
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 19
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 20
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 21
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 22
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 23
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 24
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 25
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 26
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 27
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 28
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Level 29
|  |  |  | Pour 1 | In Decks
|  |  |  | Pour 2 | In Decks
Sprinkler Pipe Installation Rough In
|  | Basement 2 |  |  | Sprinkler System Installation ITP
|  | Basement 1 |  |  | Sprinkler System Installation ITP
|  | Lower Ground |  |  | Sprinkler System Installation ITP
|  | Upper Ground |  |  | Sprinkler System Installation ITP
School
|  |  | Upper Ground |  | Sprinkler System Installation ITP
|  |  | Level 1 |  | Sprinkler System Installation ITP
|  |  | Level 2 |  | Sprinkler System Installation ITP
|  |  | Level 3 |  | Sprinkler System Installation ITP
|  |  | Level 4 |  | Sprinkler System Installation ITP
Parish Hall
|  |  | Lower Ground |  | Sprinkler System Installation ITP
|  |  | Upper Ground |  | Sprinkler System Installation ITP
|  |  | Level 1 |  | Sprinkler System Installation ITP
|  |  | Level 2 |  | Sprinkler System Installation ITP
|  |  | Level 3 |  | Sprinkler System Installation ITP
|  |  | Level 4 |  | Sprinkler System Installation ITP
RAC (Residential Aged Care)
|  |  | Level 1 |  | Sprinkler System Installation ITP
|  |  | Level 2 |  | Sprinkler System Installation ITP
|  |  | Level 3 |  | Sprinkler System Installation ITP
|  |  | Level 4 |  | Sprinkler System Installation ITP
RL (Retired Living)
|  |  | Level 5 |  | Sprinkler System Installation ITP
|  |  | Level 6 |  | Sprinkler System Installation ITP
|  |  | Level 7 |  | Sprinkler System Installation ITP
|  |  | Level 8 |  | Sprinkler System Installation ITP
|  |  | Level 9 |  | Sprinkler System Installation ITP
|  |  | Level 10 |  | Sprinkler System Installation ITP
|  |  | Level 11 |  | Sprinkler System Installation ITP
|  |  | Level 12 |  | Sprinkler System Installation ITP
|  |  | Level 13 |  | Sprinkler System Installation ITP
|  |  | Level 14 |  | Sprinkler System Installation ITP
|  |  | Level 15 |  | Sprinkler System Installation ITP
|  |  | Level 16 |  | Sprinkler System Installation ITP
|  |  | Level 17 |  | Sprinkler System Installation ITP
|  |  | Level 18 |  | Sprinkler System Installation ITP
|  |  | Level 19 |  | Sprinkler System Installation ITP
|  |  | Level 20 |  | Sprinkler System Installation ITP
|  |  | Level 21 |  | Sprinkler System Installation ITP
|  |  | Level 22 |  | Sprinkler System Installation ITP
|  |  | Level 23 |  | Sprinkler System Installation ITP
|  |  | Level 24 |  | Sprinkler System Installation ITP
|  |  | Level 25 |  | Sprinkler System Installation ITP
|  |  | Level 26 |  | Sprinkler System Installation ITP
|  |  | Level 27 |  | Sprinkler System Installation ITP
|  |  | Level 28 |  | Sprinkler System Installation ITP
|  |  | Level 29 |  | Sprinkler System Installation ITP
Sprinkler Pipe Installation Fit Off
Basement 2
|  |  | Cooling Pit |  | Sprinkler System Installation Fit Off ITP
Grease Arrestor
RL Parking
RL Waste Room
Basement 1
ACC WC C0306
Chute Room C0305
Cleaner C0391
Clean Laundry C0303
Consumables Store 2 C0394
Consumable Store 1 C0393
Continence Pad Store C0392
Corridor C0340
Corridor (plant) C0341
Dirty Laundry C0305
Dry Store C0302
Female Locker C0309
Female WCs C0310
Kitchen C0301
Male Locker C0307
Male WCs C0308
Medical C0395
Plenum C0381
RL Parking
Small Bulk Waste C0396
Staff Lobby C0397
Lower Ground
Parish Waste Room
School Waste Room
ACC WC C0508
ACC WC C05212
Admin C05214
Admin & CSM Office C0507
Air Lock C0501
Bike Room C0594
Bin Holding Room C0590
Booster C0581
Building Manager C0509
Bulky Waste C0595
Cafe BOH C0515
Cafe C0503
Cafe C0516
Cafe Seating C0502
DB C0684
Fan Room C0681
Fire Control Room C0582
Fire Pump Room C0580
Foyer C0505
Hair Salon C0506
Hoist Lift C0570
Holding Bay C0581
Lobby C0640
Mail Room C0511
Meeting C0513
Office C0517
Plenum C0586
Plenum C0680
Pump Room - 1 C0682
Pump Room - 2 C0683
RAC Lift Lobby C0540
Reception C0504
RL Lobby C0510
Site Comms Room C0584
Store C0692
Switch Room C0585
Upper Ground
Parish Hall Storage & Comms
ACC WC C0708
Admin Hot Desk C0703
Airlock C0707
CM & CCO C0702
Comms Room C0780
DB C0786
Fan Room C0784
Fan Room C0880
GM Office C0705
Interview Room B0706
Lifestyle Office C0709
Lift Lobby C0763
Lobby C0841
Plant Room C0781
Plenum C0881
Printer C0704
Retail C0711
Retail Waste C0790
Substation C0782
Team Room C0710
Wellness Centre C0701
School
Lower Ground
Level 1
ACC S0109
ACC S0115
Administration S102
Circulation S0108
FS S0183
Interview Room S0104
Principal's Office S0105
Reception S0103
Services S0180
Sick Bay S0110
Staff & Student Entry S0111
Store S0190
Uni S0106
Uni S0107
Uni S0112
Uni S0113
Waiting S0101
Level 2
ACC S0203
Circulation S0241
Cleaner S0290
Exploration Lab S0217
Fem S0202
Games & Construction S0206
Home Base Grade 2 S0207
Home Base Kinder S0212
Kinder Outdoor Learning S0214
Male S0201
Media Hub S0205
Media Hub S0216
Nook S0204
Outdoor Learning S0209
Services S0280
ST S0291
Studio Lab & Learning Commons S0208
Uni S0215
Level 3
ACC S0303
Circulation S0341
Circulation S0342
Circulation S0343
Cleaner S0390
Exploration Lab S0321
Fem S0302
FS S0383
Games & Construction S0306
Games & Construction S0317
Home Base Grade 3 S0307
Home Base Grade 4 S0310
Home Base Grade 5 S0312
Home Base Grade 6 S0316
Incubator S0320
Incubator S0322
Male S0301
Media Hub S0305
Media Hub S0318
Nook S0304
Nook S0311
Nook S0319
Outdoor Learning S0309
Outdoor Learning S0315
Services S0380
Studio Lab & Learning Commons S0308
Studio Lab & Learning Commons S0314
Level 4
ACC S0403
ACC S0404
Covered Area S0402
Outdoor Learning S0401
Plant S0405
Lifts
Lift S-L1 C0871
Lift S-L1 S0170
Lift S-L1 S0270
Lift S-L1 S0370
Lift S-L1 S0470
Stairs
Stair 8 S0360
Stair 9 S0261
Stair 9 S0361
Stair C0850
Upper Ground
School Comms Room C0783
School Lobby UG C0741
School Lobby UG Mezz C0640
|  | Parish Hall |  | School Storage C0791
Lower Ground
Upper Ground
Level 1
ACC P0102
Airlock P0141
CLNR P0108
FEM P0103
Lettable Space P0101
Lobby P0140
Male P0104
Meter Room RB146
Level 2
ACC P0203
AV Store P0292
Elec P0293
Family Room P0205
Foyer P0209
Foyer P0240
Hall P206
Kitchen & Servery P0208
Lobby P0241
Meeting P0202
Reception P0201
Stage P0207
ST P0290
ST P0291
Level 3
ACC P0302
Assistant Priest's Office P0303
Elec/Comms
Meeting Room P0305
Priest's Office P0304
Level 4
Plant P0484
RAC (Residential Aged Care)
Level 1
ACC WC B0142
Bed B0101
Bed B0102
Bed B0103
Bed B0104
Bed B0105
Bed B0106
Bed B0107
Bed B0108
Bed B0109
Bed B0110
Bed B0111
Bed B0112
Bed B0113
Bed B0114
Bed B0115
Bed B0116
Bed B0117
Bed B0118
Bed B0119
Bed B0120
Bed B0121
Bed B0122
Bed B0123
Bed B0124
Bed B0125
Bed B0126
Bed B0127
Bed B0128
Bed B0129
Bed B0130
BOH B0134
Chute Room B0190
Cleaners B0193
Comms Room B0181
Corridor - 1 B0140
Corridor - 2 B0141
Corridor - 3 B0144
Dining B0145
DU B0194
Elec B0180
EQ Store B0191
Medication B0132
MPR Cup'd B0150
MPR Store B0195
Multi Purpose Room B0150
Nurse Station B0131
RL Corridor B0143
Servery B0133
Trolley Store B0192
WC B0147
Level 2
Airlock B0224.1
Balcony B0243
Balcony B0247
Bed B0201
Bed B0202
Bed B0203
Bed B0204
Bed B0205
Bed B0206
Bed B0207
Bed B0208
Bed B0209
Bed B0210
Bed B0211
Bed B0212
Bed B0213
Bed B0214
Bed B0215
Bed B0216
Bed B0217
Bed B0218
Bed B0219
Bed B0220
Bed B0221
Bed B0222
Bed B0223
Bed B0224
Bed B0225
Bed B0226
Bed B0227
Bed B0228
Bed B0229
Bed B0230
Bed B0231
Bed B0232
Bed B0233
Bed B0234
BOH B0238
Chute Room B0290
Cleaner B0293
Comms & Elec B0280
Corridor - 1 B0240
Corridor - 2 B0241
Corridor - 3 B0245
Corridor - 4 B0249
Dining B0247
DU B0292
Equipment ST - 1 B0291
Equipment Store - 2 B0294
Nurse Station B0235
Servery B0237
WC B0248
WCC B0244
Level 3
Airlock B0324.1
Balcony B0343
Balcony B0347
Bed B0301
Bed B0302
Bed B0303
Bed B0304
Bed B0305
Bed B0306
Bed B0307
Bed B0308
Bed B0309
Bed B0310
Bed B0311
Bed B0312
Bed B0313
Bed B0314
Bed B0315
Bed B0316
Bed B0317
Bed B0318
Bed B0319
Bed B0320
Bed B0321
Bed B0322
Bed B0323
Bed B0324
Bed B0325
Bed B0326
Bed B0327
Bed B0328
Bed B0329
Bed B0330
Bed B0331
Bed B0332
Bed B0333
Bed B0334
BOH B0338
Chute Room B0390
Cleaner B0393
Comms & Elec B0380
Corridor - 1 B0340
Corridor - 2 B0341
Corridor - 3 B0345
Corridor - 4 B0349
Dining B0347
DU B0392
Equipment ST - 1 B0391
Equipment Store - 2 B0394
Medication B0336
Nurse Station B0335
Servery B0337
WC B0348
WCC B0344
Level 4
Airlock B0424.1
Balcony B0443
Balcony B0447
Bed B0401
Bed B0402
Bed B0403
Bed B0404
Bed B0405
Bed B0406
Bed B0407
Bed B0408
Bed B0409
Bed B0410
Bed B0411
Bed B0412
Bed B0413
Bed B0414
Bed B0415
Bed B0416
Bed B0417
Bed B0418
Bed B0419
Bed B0420
Bed B0421
Bed B0422
Bed B0423
Bed B0424
Bed B0425
Bed B0426
Bed B0427
Bed B0428
Bed B0429
Bed B0430
Bed B0431
Bed B0432
Bed B0433
Bed B0434
BOH B0438
Chute Room B0490
Cleaner B0493
Comms & Elec B0480
Corridor - 1 B0440
Corridor - 2 B0441
Corridor - 3 B0445
Corridor - 4 B0449
Dining B0447
DU B0492
Equipment ST - 1 B0491
Equipment Store - 2 B0494
Medication B0436
Nurse Station B0435
Servery B0437
WC B0448
WCC B0444
RL (Retired Living)
Level 5
ACC WC A0517
Bar A0511
Billiards A0508
Cinemas A0507
Circulation A0504
Cleaner A0514
Comms Room A513
Condensers L1-L4 A0523
Condensers L1-L4 A0524
Craft Room A0506
Dining A0510
Female WC A0515
Furniture Store A0519
Garbage A0503
Hot Water Plant A0521
Kitchen A0512
Lounge A0509
Male WC A0516
Meeting Room A0505
Outdoor Craft A0522
Plant A0518
Planter A0525
Pool A0520
Level 6
ACC WC / SHR A0607.9
CH A0607.10
CH A0607.11
Circulation A0608.0
Comms Cupboard
Electrical Cupboard
Gym A0607.1
Hydrant/Meter Cupboard
Lobby / CH A0607.8
Lobby / Waiting area A0607.0
Mech Plant A0607.7
Plant A0608.1
Pool A0607.5
Pool Store A0607.6
Store A0607.3
Waiting Room A0600.0
WC A0600.1
WC A0607.4
Yoga A0607.2
Unit 0601
Unit 0602
Unit 0603
Unit 0604 (Communal Lounge)
Unit 0605
Unit 0606
Level 7
Comms
Elec
HYD/MTR
Unit 0701
Unit 0702
Unit 0703
Unit 0704
Unit 0705
Unit 0706
Unit 0707
Unit 0708
Level 8
Comms
Elec
HYD/MTR
Unit 0801
Unit 0802
Unit 0803
Unit 0804
Unit 0805
Unit 0806
Unit 0807
Unit 0808
Level 9
Comms
Elec
HYD/MTR
Unit 0901
Unit 0902
Unit 0903
Unit 0904
Unit 0905
Unit 0906
Unit 0907
Unit 0908
Level 10
Comms
Elec
HYD/MTR
Unit 1001
Unit 1002
Unit 1003
Unit 1004
Unit 1005
Unit 1006
Unit 1007
Unit 1008
Level 11
Comms
Elec
HYD/MTR
Unit 1101
Unit 1102
Unit 1103
Unit 1104
Unit 1105
Unit 1106
Unit 1107
Unit 1108
Level 12
Comms
Elec
HYD/MTR
Unit 1201
Unit 1202
Unit 1203
Unit 1204
Unit 1205
Unit 1206
Unit 1207
Unit 1208
Level 13
Comms
Elec
HYD/MTR
Unit 1301
Unit 1302
Unit 1303
Unit 1304
Unit 1305
Unit 1306
Unit 1307
Unit 1308
Level 14
Comms
Elec
HYD/MTR
Unit 1401
Unit 1402
Unit 1403
Unit 1404
Unit 1405
Unit 1406
Unit 1407
Unit 1408
Level 15
Comms
Elec
HYD/MTR
Unit 1501
Unit 1502
Unit 1503
Unit 1504
Unit 1505
Unit 1506
Unit 1507
Unit 1508
Level 16
Comms
Elec
HYD/MTR
Unit 1601
Unit 1602
Unit 1603
Unit 1604
Unit 1605
Unit 1606
Unit 1607
Unit 1608
Level 17
Comms
Elec
HYD/MTR
Unit 1701
Unit 1702
Unit 1703
Unit 1704
Unit 1705
Unit 1706
Unit 1707
Unit 1708
Level 18
Comms
Elec
HYD/MTR
Unit 1801
Unit 1802
Unit 1803
Unit 1804
Unit 1805
Unit 1806
Unit 1807
Unit 1808
Level 19
Comms
Elec
HYD/MTR
Unit 1901
Unit 1902
Unit 1903
Unit 1904
Unit 1905
Unit 1906
Unit 1907
Unit 1908
Level 20
Comms
Elec
HYD/MTR
Unit 2001
Unit 2002
Unit 2003
Unit 2004
Unit 2005
Unit 2006
Unit 2007
Unit 2008
Level 21
Comms
Elec
HYD/MTR
Unit 2101
Unit 2102
Unit 2103
Unit 2104
Unit 2105
Unit 2106
Unit 2107
Unit 2108
Level 22
Comms
Elec
HYD/MTR
Unit 2201
Unit 2202
Unit 2203
Unit 2204
Unit 2205
Unit 2206
Unit 2207
Unit 2208
Level 23
Comms
Elec
HYD/MTR
Unit 2301
Unit 2302
Unit 2303
Unit 2304
Unit 2305
Unit 2306
Unit 2307
Unit 2308
Level 24
Comms
Elec
HYD/MTR
Unit 2401
Unit 2402
Unit 2403
Unit 2404
Unit 2405
Unit 2406
Unit 2407
Unit 2408
Level 25
Comms
Elec
HYD/MTR
Unit 2501
Unit 2502
Unit 2503
Unit 2504
Unit 2505
Unit 2506
Unit 2507
Unit 2508
Level 26
Comms
Elec
HYD/MTR
Unit 2601
Unit 2602
Unit 2603
Unit 2604
Unit 2605
Unit 2606
Unit 2607
Unit 2608
Level 27
Comms
Elec
HYD/MTR
Unit 2701
Unit 2702
Unit 2703
Unit 2704
Unit 2705
Unit 2706
Level 28
Comms
Elec
HYD/MTR
Unit 2801
Unit 2802
Unit 2803
Unit 2804
Kitchen A2807
ACC A2820
Outdoor Lounge A2805
Private Dining A2806
Level 29
PV Cells
Plant
Sprinkler System Commissioning
|  | Basement 2 |  |  | Sprinkler System Commissioning
|  | Basement 1 |  |  | Sprinkler System Commissioning
|  | Lower Ground |  |  | Sprinkler System Commissioning
|  | Upper Ground |  |  | Sprinkler System Commissioning
School
|  |  | Upper Ground |  | Sprinkler System Commissioning
|  |  | Level 1 |  | Sprinkler System Commissioning
|  |  | Level 2 |  | Sprinkler System Commissioning
|  |  | Level 3 |  | Sprinkler System Commissioning
|  |  | Level 4 |  | Sprinkler System Commissioning
Parish Hall
|  |  | Lower Ground |  | Sprinkler System Commissioning
|  |  | Upper Ground |  | Sprinkler System Commissioning
|  |  | Level 1 |  | Sprinkler System Commissioning
|  |  | Level 2 |  | Sprinkler System Commissioning
|  |  | Level 3 |  | Sprinkler System Commissioning
|  |  | Level 4 |  | Sprinkler System Commissioning
RAC (Residential Aged Care)
|  |  | Level 1 |  | Sprinkler System Commissioning
|  |  | Level 2 |  | Sprinkler System Commissioning
|  |  | Level 3 |  | Sprinkler System Commissioning
|  |  | Level 4 |  | Sprinkler System Commissioning
RL (Retired Living)
|  |  | Level 5 |  | Sprinkler System Commissioning
|  |  | Level 6 |  | Sprinkler System Commissioning
|  |  | Level 7 |  | Sprinkler System Commissioning
|  |  | Level 8 |  | Sprinkler System Commissioning
|  |  | Level 9 |  | Sprinkler System Commissioning
|  |  | Level 10 |  | Sprinkler System Commissioning
|  |  | Level 11 |  | Sprinkler System Commissioning
|  |  | Level 12 |  | Sprinkler System Commissioning
|  |  | Level 13 |  | Sprinkler System Commissioning
|  |  | Level 14 |  | Sprinkler System Commissioning
|  |  | Level 15 |  | Sprinkler System Commissioning
|  |  | Level 16 |  | Sprinkler System Commissioning
|  |  | Level 17 |  | Sprinkler System Commissioning
|  |  | Level 18 |  | Sprinkler System Commissioning
|  |  | Level 19 |  | Sprinkler System Commissioning
|  |  | Level 20 |  | Sprinkler System Commissioning
|  |  | Level 21 |  | Sprinkler System Commissioning
|  |  | Level 22 |  | Sprinkler System Commissioning
|  |  | Level 23 |  | Sprinkler System Commissioning
|  |  | Level 24 |  | Sprinkler System Commissioning
|  |  | Level 25 |  | Sprinkler System Commissioning
|  |  | Level 26 |  | Sprinkler System Commissioning
|  |  | Level 27 |  | Sprinkler System Commissioning
|  |  | Level 28 |  | Sprinkler System Commissioning
|  |  | Level 29 |  | Sprinkler System Commissioning
Fire Detection Installation Rough In
|  | Basement 2 |  |  | Fire Detection Installation ITP
|  | Basement 1 |  |  | Fire Detection Installation ITP
|  | Lower Ground |  |  | Fire Detection Installation ITP
|  | Upper Ground |  |  | Fire Detection Installation ITP
School
|  |  | Upper Ground |  | Fire Detection Installation ITP
|  |  | Level 1 |  | Fire Detection Installation ITP
|  |  | Level 2 |  | Fire Detection Installation ITP
|  |  | Level 3 |  | Fire Detection Installation ITP
|  |  | Level 4 |  | Fire Detection Installation ITP
Parish Hall
|  |  | Lower Ground |  | Fire Detection Installation ITP
|  |  | Upper Ground |  | Fire Detection Installation ITP
|  |  | Level 1 |  | Fire Detection Installation ITP
|  |  | Level 2 |  | Fire Detection Installation ITP
|  |  | Level 3 |  | Fire Detection Installation ITP
|  |  | Level 4 |  | Fire Detection Installation ITP
RAC (Residential Aged Care)
|  |  | Level 1 |  | Fire Detection Installation ITP
|  |  | Level 2 |  | Fire Detection Installation ITP
|  |  | Level 3 |  | Fire Detection Installation ITP
|  |  | Level 4 |  | Fire Detection Installation ITP
RL (Retired Living)
|  |  | Level 5 |  | Fire Detection Installation ITP
|  |  | Level 6 |  | Fire Detection Installation ITP
|  |  | Level 7 |  | Fire Detection Installation ITP
|  |  | Level 8 |  | Fire Detection Installation ITP
|  |  | Level 9 |  | Fire Detection Installation ITP
|  |  | Level 10 |  | Fire Detection Installation ITP
|  |  | Level 11 |  | Fire Detection Installation ITP
|  |  | Level 12 |  | Fire Detection Installation ITP
|  |  | Level 13 |  | Fire Detection Installation ITP
|  |  | Level 14 |  | Fire Detection Installation ITP
|  |  | Level 15 |  | Fire Detection Installation ITP
|  |  | Level 16 |  | Fire Detection Installation ITP
|  |  | Level 17 |  | Fire Detection Installation ITP
|  |  | Level 18 |  | Fire Detection Installation ITP
|  |  | Level 19 |  | Fire Detection Installation ITP
|  |  | Level 20 |  | Fire Detection Installation ITP
|  |  | Level 21 |  | Fire Detection Installation ITP
|  |  | Level 22 |  | Fire Detection Installation ITP
|  |  | Level 23 |  | Fire Detection Installation ITP
|  |  | Level 24 |  | Fire Detection Installation ITP
|  |  | Level 25 |  | Fire Detection Installation ITP
|  |  | Level 26 |  | Fire Detection Installation ITP
|  |  | Level 27 |  | Fire Detection Installation ITP
|  |  | Level 28 |  | Fire Detection Installation ITP
|  |  | Level 29 |  | Fire Detection Installation ITP
Fire Detection Installation Fit Off
Basement 2
|  |  | Cooling Pit |  | Smoke Detection & EWIS/OWS Fit Off
Grease Arrestor
RL Parking
RL Waste Room
Basement 1
ACC WC C0306
Chute Room C0305
Cleaner C0391
Clean Laundry C0303
Consumables Store 2 C0394
Consumable Store 1 C0393
Continence Pad Store C0392
Corridor C0340
Corridor (plant) C0341
Dirty Laundry C0305
Dry Store C0302
Female Locker C0309
Female WCs C0310
Kitchen C0301
Male Locker C0307
Male WCs C0308
Medical C0395
Plenum C0381
RL Parking
Small Bulk Waste C0396
Staff Lobby C0397
Lower Ground
Parish Waste Room
School Waste Room
ACC WC C0508
ACC WC C05212
Admin C05214
Admin & CSM Office C0507
Air Lock C0501
Bike Room C0594
Bin Holding Room C0590
Booster C0581
Building Manager C0509
Bulky Waste C0595
Cafe BOH C0515
Cafe C0503
Cafe C0516
Cafe Seating C0502
DB C0684
Fan Room C0681
Fire Control Room C0582
Fire Pump Room C0580
Foyer C0505
Hair Salon C0506
Hoist Lift C0570
Holding Bay C0581
Lobby C0640
Mail Room C0511
Meeting C0513
Office C0517
Plenum C0586
Plenum C0680
Pump Room - 1 C0682
Pump Room - 2 C0683
RAC Lift Lobby C0540
Reception C0504
RL Lobby C0510
Site Comms Room C0584
Store C0692
Switch Room C0585
Upper Ground
Parish Hall Storage & Comms
ACC WC C0708
Admin Hot Desk C0703
Airlock C0707
CM & CCO C0702
Comms Room C0780
DB C0786
Fan Room C0784
Fan Room C0880
GM Office C0705
Interview Room B0706
Lifestyle Office C0709
Lift Lobby C0763
Lobby C0841
Plant Room C0781
Plenum C0881
Printer C0704
Retail C0711
Retail Waste C0790
Substation C0782
Team Room C0710
Wellness Centre C0701
School
Upper Ground
Level 1
ACC S0109
ACC S0115
Administration S102
Circulation S0108
FS S0183
Interview Room S0104
Principal's Office S0105
Reception S0103
Services S0180
Sick Bay S0110
Staff & Student Entry S0111
Store S0190
Uni S0106
Uni S0107
Uni S0112
Uni S0113
Waiting S0101
Level 2
ACC S0203
Circulation S0241
Cleaner S0290
Exploration Lab S0217
Fem S0202
Games & Construction S0206
Home Base Grade 2 S0207
Home Base Kinder S0212
Kinder Outdoor Learning S0214
Male S0201
Media Hub S0205
Media Hub S0216
Nook S0204
Outdoor Learning S0209
Services S0280
ST S0291
Studio Lab & Learning Commons S0208
Uni S0215
Level 3
ACC S0303
Circulation S0341
Circulation S0342
Circulation S0343
Cleaner S0390
Exploration Lab S0321
Fem S0302
FS S0383
Games & Construction S0306
Games & Construction S0317
Home Base Grade 3 S0307
Home Base Grade 4 S0310
Home Base Grade 5 S0312
Home Base Grade 6 S0316
Incubator S0320
Incubator S0322
Male S0301
Media Hub S0305
Media Hub S0318
Nook S0304
Nook S0311
Nook S0319
Outdoor Learning S0309
Outdoor Learning S0315
Services S0380
Studio Lab & Learning Commons S0308
Studio Lab & Learning Commons S0314
Level 4
ACC S0403
ACC S0404
Covered Area S0402
Outdoor Learning S0401
Plant S0405
Lifts
Lift S-L1 C0871
Lift S-L1 S0170
Lift S-L1 S0270
Lift S-L1 S0370
Lift S-L1 S0470
Stairs
Stair 8 S0360
Stair 9 S0261
Stair 9 S0361
Stair C0850
Upper Ground
School Comms Room C0783
School Lobby UG C0741
School Lobby UG Mezz C0640
|  | Parish Hall |  | School Storage C0791
Lower Ground
Upper Ground
Level 1
ACC P0102
Airlock P0141
CLNR P0108
FEM P0103
Lettable Space P0101
Lobby P0140
Male P0104
Meter Room RB146
Level 2
ACC P0203
AV Store P0292
Elec P0293
Family Room P0205
Foyer P0209
Foyer P0240
Hall P206
Kitchen & Servery P0208
Lobby P0241
Meeting P0202
Reception P0201
Stage P0207
ST P0290
ST P0291
Level 3
ACC P0302
Assistant Priest's Office P0303
Elec/Comms
Meeting Room P0305
Priest's Office P0304
Level 4
Plant P0484
RAC (Residential Aged Care)
Level 1
ACC WC B0142
Bed B0101
Bed B0102
Bed B0103
Bed B0104
Bed B0105
Bed B0106
Bed B0107
Bed B0108
Bed B0109
Bed B0110
Bed B0111
Bed B0112
Bed B0113
Bed B0114
Bed B0115
Bed B0116
Bed B0117
Bed B0118
Bed B0119
Bed B0120
Bed B0121
Bed B0122
Bed B0123
Bed B0124
Bed B0125
Bed B0126
Bed B0127
Bed B0128
Bed B0129
Bed B0130
BOH B0134
Chute Room B0190
Cleaners B0193
Comms Room B0181
Corridor - 1 B0140
Corridor - 2 B0141
Corridor - 3 B0144
Dining B0145
DU B0194
Elec B0180
EQ Store B0191
Medication B0132
MPR Cup'd B0150
MPR Store B0195
Multi Purpose Room B0150
Nurse Station B0131
RL Corridor B0143
Servery B0133
Trolley Store B0192
WC B0147
Level 2
Airlock B0224.1
Balcony B0243
Balcony B0247
Bed B0201
Bed B0202
Bed B0203
Bed B0204
Bed B0205
Bed B0206
Bed B0207
Bed B0208
Bed B0209
Bed B0210
Bed B0211
Bed B0212
Bed B0213
Bed B0214
Bed B0215
Bed B0216
Bed B0217
Bed B0218
Bed B0219
Bed B0220
Bed B0221
Bed B0222
Bed B0223
Bed B0224
Bed B0225
Bed B0226
Bed B0227
Bed B0228
Bed B0229
Bed B0230
Bed B0231
Bed B0232
Bed B0233
Bed B0234
BOH B0238
Chute Room B0290
Cleaner B0293
Comms & Elec B0280
Corridor - 1 B0240
Corridor - 2 B0241
Corridor - 3 B0245
Corridor - 4 B0249
Dining B0247
DU B0292
Equipment ST - 1 B0291
Equipment Store - 2 B0294
Nurse Station B0235
Servery B0237
WC B0248
WCC B0244
Level 3
Airlock B0324.1
Balcony B0343
Balcony B0347
Bed B0301
Bed B0302
Bed B0303
Bed B0304
Bed B0305
Bed B0306
Bed B0307
Bed B0308
Bed B0309
Bed B0310
Bed B0311
Bed B0312
Bed B0313
Bed B0314
Bed B0315
Bed B0316
Bed B0317
Bed B0318
Bed B0319
Bed B0320
Bed B0321
Bed B0322
Bed B0323
Bed B0324
Bed B0325
Bed B0326
Bed B0327
Bed B0328
Bed B0329
Bed B0330
Bed B0331
Bed B0332
Bed B0333
Bed B0334
BOH B0338
Chute Room B0390
Cleaner B0393
Comms & Elec B0380
Corridor - 1 B0340
Corridor - 2 B0341
Corridor - 3 B0345
Corridor - 4 B0349
Dining B0347
DU B0392
Equipment ST - 1 B0391
Equipment Store - 2 B0394
Medication B0336
Nurse Station B0335
Servery B0337
WC B0348
WCC B0344
Level 4
Airlock B0424.1
Balcony B0443
Balcony B0447
Bed B0401
Bed B0402
Bed B0403
Bed B0404
Bed B0405
Bed B0406
Bed B0407
Bed B0408
Bed B0409
Bed B0410
Bed B0411
Bed B0412
Bed B0413
Bed B0414
Bed B0415
Bed B0416
Bed B0417
Bed B0418
Bed B0419
Bed B0420
Bed B0421
Bed B0422
Bed B0423
Bed B0424
Bed B0425
Bed B0426
Bed B0427
Bed B0428
Bed B0429
Bed B0430
Bed B0431
Bed B0432
Bed B0433
Bed B0434
BOH B0438
Chute Room B0490
Cleaner B0493
Comms & Elec B0480
Corridor - 1 B0440
Corridor - 2 B0441
Corridor - 3 B0445
Corridor - 4 B0449
Dining B0447
DU B0492
Equipment ST - 1 B0491
Equipment Store - 2 B0494
Medication B0436
Nurse Station B0435
Servery B0437
WC B0448
WCC B0444
RL (Retired Living)
Level 5
ACC WC A0517
Bar A0511
Billiards A0508
Cinemas A0507
Circulation A0504
Cleaner A0514
Comms Room A513
Condensers L1-L4 A0523
Condensers L1-L4 A0524
Craft Room A0506
Dining A0510
Female WC A0515
Furniture Store A0519
Garbage A0503
Hot Water Plant A0521
Kitchen A0512
Lounge A0509
Male WC A0516
Meeting Room A0505
Outdoor Craft A0522
Plant A0518
Planter A0525
Pool A0520
Level 6
ACC WC / SHR A0607.9
CH A0607.10
CH A0607.11
Circulation A0608.0
Comms Cupboard
Electrical Cupboard
Gym A0607.1
Hydrant/Meter Cupboard
Lobby / CH A0607.8
Lobby / Waiting area A0607.0
Mech Plant A0607.7
Plant A0608.1
Pool A0607.5
Pool Store A0607.6
Store A0607.3
Waiting Room A0600.0
WC A0600.1
WC A0607.4
Yoga A0607.2
Unit 0601
Unit 0602
Unit 0603
Unit 0604 (Communal Lounge)
Unit 0605
Unit 0606
Level 7
Comms
Elec
HYD/MTR
Unit 0701
Unit 0702
Unit 0703
Unit 0704
Unit 0705
Unit 0706
Unit 0707
Unit 0708
Level 8
Comms
Elec
HYD/MTR
Unit 0801
Unit 0802
Unit 0803
Unit 0804
Unit 0805
Unit 0806
Unit 0807
Unit 0808
Level 9
Comms
Elec
HYD/MTR
Unit 0901
Unit 0902
Unit 0903
Unit 0904
Unit 0905
Unit 0906
Unit 0907
Unit 0908
Level 10
Comms
Elec
HYD/MTR
Unit 1001
Unit 1002
Unit 1003
Unit 1004
Unit 1005
Unit 1006
Unit 1007
Unit 1008
Level 11
Comms
Elec
HYD/MTR
Unit 1101
Unit 1102
Unit 1103
Unit 1104
Unit 1105
Unit 1106
Unit 1107
Unit 1108
Level 12
Comms
Elec
HYD/MTR
Unit 1201
Unit 1202
Unit 1203
Unit 1204
Unit 1205
Unit 1206
Unit 1207
Unit 1208
Level 13
Comms
Elec
HYD/MTR
Unit 1301
Unit 1302
Unit 1303
Unit 1304
Unit 1305
Unit 1306
Unit 1307
Unit 1308
Level 14
Comms
Elec
HYD/MTR
Unit 1401
Unit 1402
Unit 1403
Unit 1404
Unit 1405
Unit 1406
Unit 1407
Unit 1408
Level 15
Comms
Elec
HYD/MTR
Unit 1501
Unit 1502
Unit 1503
Unit 1504
Unit 1505
Unit 1506
Unit 1507
Unit 1508
Level 16
Comms
Elec
HYD/MTR
Unit 1601
Unit 1602
Unit 1603
Unit 1604
Unit 1605
Unit 1606
Unit 1607
Unit 1608
Level 17
Comms
Elec
HYD/MTR
Unit 1701
Unit 1702
Unit 1703
Unit 1704
Unit 1705
Unit 1706
Unit 1707
Unit 1708
Level 18
Comms
Elec
HYD/MTR
Unit 1801
Unit 1802
Unit 1803
Unit 1804
Unit 1805
Unit 1806
Unit 1807
Unit 1808
Level 19
Comms
Elec
HYD/MTR
Unit 1901
Unit 1902
Unit 1903
Unit 1904
Unit 1905
Unit 1906
Unit 1907
Unit 1908
Level 20
Comms
Elec
HYD/MTR
Unit 2001
Unit 2002
Unit 2003
Unit 2004
Unit 2005
Unit 2006
Unit 2007
Unit 2008
Level 21
Comms
Elec
HYD/MTR
Unit 2101
Unit 2102
Unit 2103
Unit 2104
Unit 2105
Unit 2106
Unit 2107
Unit 2108
Level 22
Comms
Elec
HYD/MTR
Unit 2201
Unit 2202
Unit 2203
Unit 2204
Unit 2205
Unit 2206
Unit 2207
Unit 2208
Level 23
Comms
Elec
HYD/MTR
Unit 2301
Unit 2302
Unit 2303
Unit 2304
Unit 2305
Unit 2306
Unit 2307
Unit 2308
Level 24
Comms
Elec
HYD/MTR
Unit 2401
Unit 2402
Unit 2403
Unit 2404
Unit 2405
Unit 2406
Unit 2407
Unit 2408
Level 25
Comms
Elec
HYD/MTR
Unit 2501
Unit 2502
Unit 2503
Unit 2504
Unit 2505
Unit 2506
Unit 2507
Unit 2508
Level 26
Comms
Elec
HYD/MTR
Unit 2601
Unit 2602
Unit 2603
Unit 2604
Unit 2605
Unit 2606
Unit 2607
Unit 2608
Level 27
Comms
Elec
HYD/MTR
Unit 2701
Unit 2702
Unit 2703
Unit 2704
Unit 2705
Unit 2706
Level 28
Comms
Elec
HYD/MTR
Unit 2801
Unit 2802
Unit 2803
Unit 2804
Kitchen A2807
ACC A2820
Outdoor Lounge A2805
Private Dining A2806
Level 29
PV Cells
Plant
Fire Detection System Commissioning
|  | Basement 2 |  |  | Fire Detection System Commissioning
|  | Basement 1 |  |  | Fire Detection System Commissioning
|  | Lower Ground |  |  | Fire Detection System Commissioning
|  | Upper Ground |  |  | Fire Detection System Commissioning
School
|  |  | Upper Ground |  | Fire Detection System Commissioning
|  |  | Level 1 |  | Fire Detection System Commissioning
|  |  | Level 2 |  | Fire Detection System Commissioning
|  |  | Level 3 |  | Fire Detection System Commissioning
|  |  | Level 4 |  | Fire Detection System Commissioning
Parish Hall
|  |  | Lower Ground |  | Fire Detection System Commissioning
|  |  | Upper Ground |  | Fire Detection System Commissioning
|  |  | Level 1 |  | Fire Detection System Commissioning
|  |  | Level 2 |  | Fire Detection System Commissioning
|  |  | Level 3 |  | Fire Detection System Commissioning
|  |  | Level 4 |  | Fire Detection System Commissioning
RAC (Residential Aged Care)
|  |  | Level 1 |  | Fire Detection System Commissioning
|  |  | Level 2 |  | Fire Detection System Commissioning
|  |  | Level 3 |  | Fire Detection System Commissioning
|  |  | Level 4 |  | Fire Detection System Commissioning
RL (Retired Living)
|  |  | Level 5 |  | Fire Detection System Commissioning
|  |  | Level 6 |  | Fire Detection System Commissioning
|  |  | Level 7 |  | Fire Detection System Commissioning
|  |  | Level 8 |  | Fire Detection System Commissioning
|  |  | Level 9 |  | Fire Detection System Commissioning
|  |  | Level 10 |  | Fire Detection System Commissioning
|  |  | Level 11 |  | Fire Detection System Commissioning
|  |  | Level 12 |  | Fire Detection System Commissioning
|  |  | Level 13 |  | Fire Detection System Commissioning
|  |  | Level 14 |  | Fire Detection System Commissioning
|  |  | Level 15 |  | Fire Detection System Commissioning
|  |  | Level 16 |  | Fire Detection System Commissioning
|  |  | Level 17 |  | Fire Detection System Commissioning
|  |  | Level 18 |  | Fire Detection System Commissioning
|  |  | Level 19 |  | Fire Detection System Commissioning
|  |  | Level 20 |  | Fire Detection System Commissioning
|  |  | Level 21 |  | Fire Detection System Commissioning
|  |  | Level 22 |  | Fire Detection System Commissioning
|  |  | Level 23 |  | Fire Detection System Commissioning
|  |  | Level 24 |  | Fire Detection System Commissioning
|  |  | Level 25 |  | Fire Detection System Commissioning
|  |  | Level 26 |  | Fire Detection System Commissioning
|  |  | Level 27 |  | Fire Detection System Commissioning
|  |  | Level 28 |  | Fire Detection System Commissioning
|  |  | Level 29 |  | Fire Detection System Commissioning
| Extinguishers |  |  |  | Ability to Add
| Pumps |  |  |  | Ability to Add
Drawings |  |  |  |  | Document Attachment
Variation |  |  |  |  | Ability to Add
Injury Form |  |  |  |  | Ability to Add
Toolbox Meeting
| June |  |  |  | Ability to Add
| July |  |  |  | Ability to Add
| August |  |  |  | Ability to Add
| September |  |  |  | Ability to Add
| October |  |  |  | Ability to Add
| November |  |  |  | Ability to Add
| December |  |  |  | Ability to Add
Site Induction |  |  |  |  | Ability to Add
Daily Pre Start/Works
| June |  |  |  | Ability to Add
| July |  |  |  | Ability to Add
| August |  |  |  | Ability to Add
| September |  |  |  | Ability to Add
| October |  |  |  | Ability to Add
| November |  |  |  | Ability to Add
| December |  |  |  | Ability to Add
Test & Tag |  |  |  |  | Ability to Add

## Checklists
type | name | values
checklist | Sprinkler System Installation ITP
section | Initial Floor/Area Establishment
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint | Does the delivery/delivery docket match the order?
checkpoint | Piping & weld quality reviewed?
checkpoint | Fabrication sheets match the pipe delivered to site? (Take a photo of the fabrication check sheet)
checkpoint | Have the correct sprinklers been delivered? (Take a photo of all sprinklers required for area of installation)
section | Initial Installation
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Check sprinkler heads for damage/scratches to paint finish (Take a photo of sprinklers required for area of installation)
checkpoint | Flexi compliant to AS2118 and FM approved? (take a photo of the data sheet)
checkpoint | Sprinklers neatly hemped and soaped (with inner escutcheon plates installed, if required)? (take a photo)
checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint | Grid lines marked out and confirmed with the assistance of building team? (Take a photo/signature from both parties required)
checkpoint | Pipework installed as per the ISSUED FOR CONSTRUCTION drawings? (correct heights, measurements off grid lines)
checkpoint | Pipework hangers/supports installed correctly? (take multiple photos)
checkpoint | Concealed space sprinklers installed as per AS2118 with no obstructions? (Take multiple photos)
checkpoint | Flexi installed to manufacturers specs and tied up away from possible damage? (Take multiple photos)
checkpoint | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish) (take photos)
checkpoint | Riser pipework installed as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint | Riser hangers/supports installed correctly? (take photos)
checkpoint | Fire sprinkler control valve installed and connected to system, riser and drain pipework? (take a photo when installation complete)
checkpoint | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? (Take a photo of each sealed penetration back and front)
checkpoint | Fire Rating/acoustic sealing of riser penetrations completed? (Take a photo of each sealed penetration above and below)
checkpoint | Exposed fire sprinkler pipework completely painted to required colour? (Take multiple photos)
checkpoint | Any changes to installation recorded for AS BUILT DRAWINGS (Mark up most recent plans and take a photo of each change)(make a note as why the change was made)
checklist | Sprinkler System Installation Fit Off ITP
section | Fit Off - Part 1
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Check Sprinkler Heads for damage/scratches to paint finish (Take a photo of all damaged sprinklers with room/area reference)
checkpoint | Check Flexi for damage/kinks (take a photo of any damaged Flexi with room/area reference)
checkpoint | Check the water is drained the water out of the system (take a photo)
checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint | Laser used to fit off to accurate measurements? (Take a photo of each sprinkler in final position)
checkpoint | Sprinklers installed as per AS2118 with no obstructions? (Take multiple photos)
checkpoint | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish) (take photos)
checkpoint | Check the water is reinstated into the system at the completion of fit off (take a photo)
section | Fit Off - Part 2
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Check sprinkler heads for damage/scratches to paint finish (Take a photo of all sprinklers required for area of installation)
checkpoint | Check sprinkler heads are straight and parallel to finished surface (Take a photo of each sprinkler in final position with room/area reference if moved or damaged)
Checkpoint | Check there is no paint or gyprock setting on sprinkler head (Take a photo of each sprinkler in final position with room/area reference if damaged)
checkpoint | Outer escutcheon plates installed
checkpoint | Check there is no gaps between the outer escutcheon plate and the finished ceiling
checkpoint | Sprinklers installed as per AS2118 with no obstructions? (Take multiple photos)
checklist | Fire Detection Installation ITP
section | Initial Site Establishment
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint | Does the delivery/delivery docket match the order?
section | Dry Fire Cable Rough In
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint | Room/area layout set out and confirmed with the assistance of building team? (Take a photo/signature from both parties required)
checkpoint | Cable installed to device locations as per the most recent ISSUED FOR CONSTRUCTION drawings?
checkpoint | Cable supports installed correctly? (take multiple photos)
checkpoint | Sufficient slack in cable to reach required fit off location?
checkpoint | Cable tray installed as per AS 3000? (take photos of installed tray)
checkpoint | Fire Detection cable has compliant spacing between Detection, EWIS/OWS and electrical power cable? (take multiple photos)
checkpoint | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? (Take a photo of each sealed penetration back and front)
checkpoint | Are wires clearly drawn and submitted for AS BUILTS/AS CONSTRUCTED drawings (take a photo of the drawing with line diagram clearly shown)
checkpoint | Are all devices numbered on drawing for AS BUILTS/AS CONSTRUCTED drawings? (take a photo of the drawing with device number clearly shown)
checkpoint | Riser Cable Tray Installation & cables installed in a neat order? (take a photo)
checkpoint | Cable supported to tray
checkpoint | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? (Take a photo of each sealed penetration top and bottom)
checklist | Smoke Detection & EWIS/OWS Fit Off
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint | Excess slack in cable removed?
checkpoint | Smoke and Thermal Detectors are installed in correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint | Check Thermal and Smoke Detectors installed in accordance with AS1670, AS1668, BCA (take photo of data sheet for devices being installed)
checkpoint | EWIS/OWS speaker are installed in the correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint | Laser used to fit off to accurate measurements? (Take a photo of each detector/speaker in final position)
checkpoint | WIP/MCP installed as per AS1670 & BCA (take photo of each device after installation)
checkpoint | All devices are numbered correctly using labels (NO MARKERS) and in correct location as per the AS BUILT DEVICE numbering markup?
checkpoint | All devices are fit off as per ISSUED FOR CONSTRUCTION drawings and clear of any obstructions? (Take a photo of all damaged/obstructed devices with room/area reference)
checkpoint | Cable joints and terminations correctly completed with no tension on the terminals?
checkpoint | All traffolyte labels are installed to each WIP/MCP and field module?
checklist | Sprinkler System Commissioning
section | Visual inspection
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Check Sprinkler Heads & escutcheons for damage/scratches to paint finish (Take a photo of all damaged sprinklers with room/area reference)
checkpoint | Floor inspection to confirm all system works are complete?
checkpoint | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish)
checkpoint | Escutcheon plates installed
checkpoint | Joints, connections,position & spacing / obstruction correct
checkpoint | Shields/guards provided (where specified)
checkpoint | Fixings and supports in accordance with AS2118
checkpoint | Sprinkler Support Systems are installed to not impede other services installed
checkpoint | Ancillary equipment installed? (monitored isolation valve, flow switch, pressure switch)
checkpoint | Block Plans installed and reviewed? (take a photo)
checkpoint | Signage & Labelling, Locks & Straps installed (take a photo)
checkpoint | Seismic Restraints & paint assessed
checkpoint | Is the fire sprinkler valve set drain connected to the drain riser? (take a photo)
checkpoint | Is the fire sprinkler drain riser ran into the hydraulic waste drain? (take a photo)
section | Commissioning
checkpoint | Check operation of the monitored isolation valve and record FIP interface (take a photo of both items at the same time)
checkpoint | Inspect and test gauge operation (record a video of the drop in pressure and the pressure re-stabilising to static working pressure)
checkpoint | Check operation of manual test drain confirm flow switch activation to FIP (record a video and take a photo of the FIP when alarm is activated) (note the time delay)
checkpoint | Check operation of the water pressure switch activation to FIP (record a video and take a photo of the FIP when alarm is activated)
checkpoint | Check operation of solenoid test drain confirm FSW activation to FIP (record a video and take a photo of the FIP when alarm is activated)
checkpoint | Check the operation of the water motor alarm (record a video)
section | Hydrostatic Pressure Test
checkpoint | 1.6MPa or 400 kpa in excess of the maximum static working pressure (whichever is greater) for a period of 2 hours, with no loss of pressure duration the 2 hour duration.
checkpoint | Are the pipework Joints, connections, position & spacing correct?
checkpoint | Are all open ends plugged off to close up the piping network?
text | Start Time:
text | Test Pressure:
checkpoint | Attach picture of pressure test gauge:
text | Finish Time:
text | Test Pressure:
checkpoint | Attach picture of pressure test gauge:
checkpoint | Any pressure loss during test?
checkpoint | Summit Fire Representative & Builder Representative to sign prior to closing out
signoff | Summit Fire Representative & Builder Representative to sign off
checklist | Fire Detection System Commissioning
section | Visual Inspection
checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint | Floor inspect to confirm all system works are complete
checkpoint | All faults and isolations cleared for area
checkpoint | Smoke and Thermal Detectors are installed in correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint | EWIS/OWS speaker are installed in the correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint | WIP/MCP installed as per AS1670 & BCA
checkpoint | Cable joints and terminations correctly completed with no tension on the terminals?
checkpoint | Compliance with AS1670, AS1668, BCA 2015
checkpoint | All devices are fit off as per ISSUED FOR CONSTRUCTION drawings and clear of any obstructions? (Take a photo of all damaged/obstructed devices with room/area reference)
checkpoint | All devices are numbered correctly using labels (NO MARKERS) and in correct location as per the AS BUILT DEVICE numbering markup?
checkpoint | All traffolyte labels are installed to each WIP/MCP and field module?
checkpoint | Smoke detection & EWIS/OWS block plans installed as per AS1670?
section | Commissioning
checkpoint | Test each Smoke Detector in accordance with AS1670, AS1668, BCA using smoke can and record FIP alarm. (take a photo of the device & panel at the same time)
checkpoint | Test each thermal Detector in accordance with AS1670, AS1668, BCA using a heat detector tester kit can and record FIP alarm. (take a photo of the device & panel at the same time)
checkpoint | Test Speakers in accordance with AS1670 & BCA under general fire alarm and record results using a sound probe meter (record video)
checkpoint | Test Visual Alarm Devices in accordance with AS1670 & BCA under general fire alarm (record video)
checkpoint | Test WIP phones in accordance AS1670, BCA (record video)
checkpoint | Test Manual Call Points in accordance with AS1670, BCA and record FIP/EWIS alarm (record video)
checkpoint | Test Field Module Interfaces in accordance with AS1670, AS1668, BCA and record FIP alarm (take a photo of the Interface and FIP the the same time)
checkpoint | Test the activation of smoke/fire door magnetic hold open devices under local fire alarm (record video)
checkpoint | test the activation of mechanical fire trips under general fire alarm (take a photo of the mechanical GFA trip and FIP in alarm at the same time)
checkpoint | Test the activation of security fire trips under general fire alarm (take a photo of the mechanical GFA trip and FIP in alarm at the same time)
checkpoint | Test the EWIS/OWS time delay for cascading and changing from ALERT to EVAC (record a video of the EWIS/OWS Panel)
checkpoint | Test the activation of network monitoring during latching FIP alarm (attach monitoring company report and photos of the alarm on FIP & Monitoring Device)
checkpoint | Test the activation of the external bell under fire trip mode in accordance AS1670, BCA (record video)
checkpoint | Test the activation of the external strobe under fire trip mode in accordance AS1670, BCA (record video)
checklist | Fire Pump Commissioning
checkpoint | Floor inspect to confirm all system works are complete
checkpoint | Confirm schematic design reference & pump room design drawings reference
checkpoint | Installation of only approved sample equipment & to approved drawing
checkpoint | Confirm factory acceptance testing documents from supplier
checkpoint | Complete pump room hydrostatic test
checkpoint | Confirm/witness Axis Hydrostatic testing of pipework system
checkpoint | Check pump area for obstructions
checkpoint | Check pump discharge drains
checkpoint | Check signage and ID plates on engine & pump
text | Check and record number of water supply valves are secured
text | Record and verify pressure gauge readings suction kPa
checkpoint | Check general condition of Pump
checkpoint | Check Pump controller
checkpoint | Check monitor and engine start batteries and record
checkpoint | Check controller safety functions, alarms, set point validation and measurement of fuel consumption
checkpoint | Pump Run Operation, Run for 10 mins @ 0 flow (record)
label | Check Pump Starting devices and record
text | Starting pressure (kpa)
text | Run time
text | Hour meter
label | Check and verify pump operation and record in comments
text | Suction (kPa)
text | Discharge (kPa)
text | Charger Voltage (V)
text | Oil Pressure (kPa)
text | Engine Temp (C)
checkpoint | Pump Run Operation, Run for 10 mins @ 130% flow (record)
label | Check Pump Starting devices and record
text | Starting pressure (kpa)
text | Run time
text | Hour meter
label | Check and verify pump operation and record in comments
text | Suction (kPa)
text | Discharge (kPa)
text | Charger Voltage (V)
text | Oil Pressure (kPa)
text | Engine Temp (C)
checkpoint | Pump Run Operation, Run for 10 mins @ reduce flow to duty (record)
label | Check Pump Starting devices and record
text | Starting pressure (kpa)
text | Run time
text | Hour meter
label | Check and verify pump operation and record in comments
text | Suction (kPa)
text | Discharge (kPa)
text | Charger Voltage (V)
text | Oil Pressure (kPa)
text | Engine Temp (C)
checkpoint | Pump Run Operation, Run for 10 mins @ 0 flow until the pump has run for 30 mins
label | Check Pump Starting devices and record
text | Starting pressure (kpa)
text | Run time
text | Hour meter
label | Check and verify pump operation and record in comments
text | Suction (kPa)
text | Discharge (kPa)
text | Charger Voltage (V)
text | Oil Pressure (kPa)
text | Engine Temp (C)
label | Basement & Podium
label | Pressure Zone / Level Reference of Test
checklist | Document Attachment
checkpoints | Attach relevant documents
checklist | Variation
checkpoint | Variation / SI Details Entered
label | Please take before photos
radio | Work type:
text | Attention:
text | Area/Location
text | Date
text | Scope of work
text | Normal Hours
text | Overtime Hours
text | Material to complete task
checkpoint | Reference/SI Number Entered
text | Reference/SI Number
checkpoint | Variation / SI Work Completed
checkpoint | Values added (Office use only)
text | Labour Value
text | Material Value
text | Measured Items
text | Total Variation Value
checklist | Injury Form
checkpoint | Injury form completed
text | Date of incident
text | Time
text | Site location of the accident / incident (take multiple photo of area of incident)
text | Detail of how the accident / incident happened
label | Details of injured person
text | First name
text | Last name
text | DOB
text | Contact No
text | Address
text | Company
text | Trade
text | Date Inducted
select | Type of injury | Electrocution, Amputation, Bruise, Burn, Concussion, Deafness, Dislocation, Foreign Body, Fracture, Hernia, Inflammation / Infection, Internal Injury, Laceration / Cut, Occupational Illness, Open Wound, Poisoning / Toxic Effect, Strain / Sprain Twist
select | Location on body | Front, Back, Head, Neck, Torso, Left Hand, Left Arm, Right Hand, Right Arm, Left Leg, Left Foot, Right Leg, Right Foot, Other
select | Treatment | No First Aid Treatment, First Aid Treatment, Medical Treatment , Lost Time Injury, Fatal Injury
text | Initial treatment given
text | Was follow up treatment provided
text | Medical centre / Doctor / Hospital attended
text | Date / time attended
label | Witness details
text | Witness name & contact details
text | Witness name & contact details
select | Event details / cause | Falls from height, Fall from same level, Hitting objects with body part, Exposure to mechanical vibration, Being hit by moving objects, Exposure to sharp sudden noise / long term noise, Exposure to extreme temps, Exposure to radiation, Exposure to biological factors, Exposure to mental stress factors, Vehicle accident, Muscular single / repetitive movement, Contact with electricity, Contact with toxic chemicals / substance, Other & multiple mechanisms of injury
text | Other
checkpoint | Signature of injured worker
checkpoint | Person completing this form
checkpoint | Signature of person completing this form
checkpoint | Builder Representative Witness
checkpoint | Signature of Builder Representative Witness
checklist | Toolbox Meeting
checkpoint | Toolbox signed off - Attach an forms
text | Toolbox Talk Location
text | Person Conducting Toolbox Talk
text | Date
text | Time am / pm
text | Actions from last meeting
text | Injuries last week
text | Near misses last week
text | Safety Items discussed
text | Comments from the floor
text | Upcoming works for the week
text | New Business items to discuss
text | Attendees
checkpoint | Attendance verified
type | name
checklist | Site Induction
checkpoint | Summit Fire Employee - Attach document and photos where required
text | Name
text | Contact Number
text | Date of Induction
label | Tick if the following are understood:
bool | How to report to the site and who you report to
bool | The working hours on site
bool | Who the managers and supervisors are on site
bool | The correct minimum PPE for site
bool | How safety is communicated on site
bool | Where to have lunch and where the toilets are
bool | Where the First Aid Kit is kept and who is the First Aider
bool | The Emergency Plan and the Assembly Area for Emergency Evacuation
bool | What the high risk activities and hazards are on site
bool | How to report WHS & Environmental hazards & issues
bool | How to report a safety or environmental accident or incident
bool | Housekeeping responsibilities
checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
checkpoint | Summit Fire Employee Signature
checkpoint | Summit Fire Supervisor Signature
checklist-flat | Daily Pre Start/Works Checklist
checkpoint | Daily pre start meeting completed
text | Date
text | Time
text | Location of work being performed
checkpoint | Is the area clear, tidy, dry, accessible and well lit? (take multiple photos of installation area)
checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint | Does the delivery/delivery docket match the order placed? (*note: list all items not delivered)
checkpoint | Are the correct tools ready for today's tasks?
checkpoint | Are Power tool batteries on charge?
Checkpoint | Is the threading machine, drop saw and pipestand set up and ready for use?
checkpoint | Are all leads suspended off the ground, plugged into an RCD and test & tagged in date?
checkpoint | Are the correct height ladders being used for today's tasks?
checkpoint | Do you have the correct mandatory PPE on? (Hard Hat, Hi Vis shirt/jumper/jacket, Steel toe Boots, Safety Glasses, Safety gloves and Ear Plugs?
text | Project Manager
text | Any issues from the previous day
text | Any unfinished works from the previous day in the area of works?
text | First aiders on site today
text | Who are you working with today?
text | today's tasks / jobs
text | Any unfinished tasks / jobs from today's items? (list the items unfinished & explain why the tasks were not finished)
text | Attendees
checkpoint | Summit Fire Supervisor Signature
checklist | In Decks
checkpoint | Detection services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | EWIS services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Strobe services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | WIP services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | MCP services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Sprinkler System Interface conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Mech Services Interface conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Hydrant sleeves have been installed in accordance with design and as per drawings.
checkpoint | Sprinkler sleeves have been installed in accordance with design and as per drawings.
checkpoint | All Penetrations have been installed in accordance with design and as per drawings.
checklist | Extinghuser Checklist |  | x 50
checkpoint | Attach any relevant photos or documents
text | Item Number
text | Location
text | Man Date
text | Test Date
text | Serial Number
text | Type
checkpoint | Tested
checklist | Inspect and Test Register |  | x 50
checkpoint | Attach any relevant photos or documents
text | Equipment
text | Description
text | Manufacturer
text | Item Number
text | Date of Inspection and Test
checkpoint | Result
text | Action to be taken
signoff | Signature of person undertaking the work
text | Certificate number (if appropriate)
text | Date for next inspection and test

## Sheet3
type | name | values
checklist-flat | In Decks
checkpoint | Lighting services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Power services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Communication services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | Security services conduits and cast in boxes have been installed in accordance with design and as per drawings.
checkpoint | All Penetrations have been installed in accordance with design and as per drawings.