## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-008 Conduit and Pit Installation & Checklist - Rev.5 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-008 Conduit and Pit Installation & Checklist - Rev.5
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 1.2 - Lot Traceability
label | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Lot map
checkpoint | 1.3 - Underlying Lot Conformance
label | Ref docs - Underlying Lot ITP
label | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | ○ Refer underlying lot ITP(s)
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 1.4 - Set Out
label | Ref docs - Drawings
label | Acceptance Criteria - Peg location of proposed underground services with levels from pit to pit. Peg property boundaries
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 2.0 Material Conformance
checkpoint | 2.1 - Conduit Supply
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7]
label | Acceptance Criteria - Conduit system shall be a Category A wiring enclosure for an underground wiring system to AS/NZS3000 and AS/NZS 3013.
label | ○ No corrugated conduit or similar shall be used under any circumstances.
label | ○ HV & LV Conduits: Shall be orange heavy-duty uPVC, sizes as per drawings otherwise min 150mm (HV) and 100mm (LV) to be used.
label | ○ Comms Conduits: Shall be white heavy-duty uPVC, sizes as per drawings otherwise min 100mm to be used.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material certification
checkpoint | 2.2 - Pit Supply
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11]
label | Acceptance Criteria - All pits are to be reinforced concrete complete with concrete lids. All lids shall be gatic with min load classification of Class D in accordance with AS 3996.
label | ○ Pits lids shall be fixed to prevent unauthorised access.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material certification
checkpoint | 2.3 - Embedment material
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6, 6.11]
label | Acceptance Criteria - All conduits shall be surrounded by a min of 100mm compacted sand unless shown otherwise on the drawings. For power conduits, this compacted sand must have a min thermal rating of 1.2°C.m/W.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material certifications
section | 3.0 Excavation, Installation and Backfill - Conduits
checkpoint | 3.1 - Excavation
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | Acceptance Criteria - All trenches unless otherwise directed by Snowy Hydro shall be excavated as per Drawings.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 3.2 - Place Bedding
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | Acceptance Criteria - Pits shall be installed on a compacted sand base of not less than 100mm.
label | ○ Bedding layer to be compacted for the full width of the trench to a depth of 100mm for Comms & 150mm for Power Conduits.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 3.3 - Conduit Installation
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11, Cl.17.1], Drawings
label | Acceptance Criteria - Conduits to be installed as per the drawings in a straight line where possible and with no changes in diameter between pits. Joints to be sealed with a solvent cement or glue as per manufacturer recommendations.
label | Minimum separation to be 150mm for DN150 conduits and 100mm for all other sizes unless shown otherwise on the drawings
label | Minimum depth of cover to conduits to be:
label | – 300mm for COMMS
label | – 500mm for LV
label | – 900mm for MV
label | WITNESS POINT – Prior to Backfilling
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
checkpoint | 3.4 - Conduit bends
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7]
label | Acceptance Criteria - All conduit bends shall be long sweep bends with a maximum 90-degree angle.
label | Min bend radius shall suit the min cable bending radius of the largest cable in the conduit and generally not be less than 1000mm.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 3.5 - Marker tape
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.9]
label | Acceptance Criteria - Orange Polyethylene marker tapes, 150mm wide and 0.1mm deep, shall be laid in the trench directly over all underground conduits at approximately 50% of the depth of cover. The tape shall be marked with the warning:
label | “WARNING BURIED POWER CABLES”
label | or similar in black letters that will not fade.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 3.6 - Backfill - Conduits
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6]
label | Acceptance Criteria - Backfill the full width of trench with compacted sand to above the level specified for compacted sand, back to natural surface level.
label | ○ Layers not to exceed 150mm compacted thickness.
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 3.7 - Compaction
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
label | – 95% for foundations
label | – 70% for conduit encasement
label | – 97% for select fill areas
label | – 92% for general fill areas
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 3.8 - Cable Markers
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.10]
label | Acceptance Criteria - Install Concrete Cable markers on the surface of all underground cable joints, at every change in direction, and on straight runs at least every 30m.
label | ○ Markers to be a 400mm square and 100mm deep concrete block with a brass label attached. Label to identify conduit type and direction.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 4.0 Excavation, Installation and Backfill - Pits
checkpoint | 4.1 - Excavation
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | Acceptance Criteria - All trenches unless otherwise directed by Snowy Hydro shall be excavated as per Drawings.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.2 - Place Bedding
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | Acceptance Criteria - Pits shall be installed on a compacted sand base of not less than 100mm.
label | ○ Bedding layer to be compacted for the full width of the trench to a depth of 100mm for Comms & 150mm for Power Conduits.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.3 - Pit Installation
label | Ref docs - Drawings
label | Acceptance Criteria - Pits to be installed as per drawings and manufacturers specifications.
label | ○ All conduit entries are to be fitted with proprietary bell-mouths installed flush with the pit wall.
label | ○ All pit joints and bell-mouths are to be mastic sealed or glued as per manufacturer recommendations.
label | WITNESS POINT – Prior to Backfilling
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
checkpoint | 4.4 - Pit Drainage
label | Ref docs - Drawings
label | Acceptance Criteria - Pits to be installed with a drainage system as per the drawings to prevent pooling of water
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.5 - Step Irons
label | Ref docs - Drawings
label | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.6 - Access Covers
label | Ref docs - Drawings
label | Acceptance Criteria - Pits to be fitted with Class D Concrete Infill Gatic Lids to AS 3996.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.7 - Brass Marker Plates
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11], Drawings
label | Acceptance Criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.8 - Backfill - Pits
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6]
label | Acceptance Criteria - Backfill the full width of trench with compacted sand to above the level specified for compacted sand, back to natural surface level.
label | ○ Layers not to exceed 150mm compacted thickness.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.9 - Compaction
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
label | – 95% for pit and conduit bedding
label | – 97% for select fill areas
label | – 92% for general fill areas
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 4.10 - Rope and Mandrel
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7.5]
label | Acceptance Criteria - Draw ropes or wires to be installed in all conduits that will require further cabling.
label | ○ All conduits to be mandrel inspected prior to cabling to check for blockages.
label | WITNESS POINT – Prior to Cabling
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
section | 5.0 Conformance Check
checkpoint | 5.1 - Survey Report
label | Acceptance Criteria - An as-built survey of the conduit and pit system has been completed to ensure all structures are within construction tolerances.
button | Acceptance | Yes,No,N/A
label | Key - R
label | UGL Key - R
label | SHL Key - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey report
checkpoint | 5.2 - Acceptance and closure of non-conforming items
label | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
holdpoint | AUTHORITY HOLDPOINT