## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-018 Conduit Pits (In-situ) - Rev.2 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-018 Conduit Pits (In-situ) - Rev.2
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 1.2 - Lot Traceability
label | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Lot map
checkpoint | 1.3 - Underlying Lot Conformance
label | Ref docs - Underlying Lot ITP
label | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
button | Acceptance | Yes,No,N/A
checkpoint | 1.4 - Set out
label | Ref docs - Drawings
label | Acceptance Criteria - Setout pits to the location and levels on the drawings
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 2.0 Excavation and Bedding
checkpoint | 3.102.1 - Excavation
label | Ref docs - Spec. 0002 General Electrical [Cl 6.6]
label | Acceptance Criteria - Excavate to the depths and widths of the design drawings
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 2.2 - Place Bedding
label | Ref docs - Spec. 0002 General Electrical [Cl 6.11] Drawings
label | Acceptance Criteria - Pits to be installed on a 100mm thick compacted sand base.
label | ○ Alternatively, a 150mm thick 20mm crushed rock layer can be used if the pit floor is below the water table.'
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Dockets
checkpoint | 2.3 - Blinding
label | Ref docs - Drawings
label | Acceptance Criteria - Blinding (15MPa) for Pit Bases to be a 50mm thick mass concrete layer.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 3.0 Cast in-situ structures
checkpoint | 3.1 - Formwork (Base)
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
label | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | HOLD POINT
label | Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Steel reinforcement (Base)
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
label | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | ○ Concrete pre-pour inspection complete.
label | HOLD POINT
label | Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Formwork (Walls)
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
label | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | HOLD POINT
label | Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Steel reinforcement (Walls)
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
label | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | ○ Concrete pre-pour inspection complete.
label | HOLD POINT
label | Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Bell-mouths
label | Ref docs - Spec. 0002 General Electrical [Cl 6.11]
label | Acceptance Criteria - All conduit entries are to be fitted with proprietary bell-mouths installed flush with the pit wall as per manufacturer specifications
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 3.73.6 - Concrete supply and placement
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11], Drawings
label | Acceptance Criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
label | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | – – – – – – – – – – – – – – – –
label | Concrete temp at discharge (°C) ¦¦ Max elapsed time (hours)
label | 10-24 ¦¦ 2.00
label | 24-27 ¦¦ 1.50
label | 27-30 ¦¦ 1.00
label | 30-32 ¦¦ 0.75
label | – – – – – – – – – – – – – – – –
label | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Delivery dockets
checkpoint | 3.7 - Concrete sampling
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | Acceptance Criteria - The nominal rate of sampling shall be taken:
label | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
label | (b) Slump: One per batch of concrete
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete pour record
checkpoint | 3.8 - Concrete testing
label | Ref docs - Drawings
label | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements. Slump within tolerances specified in AS 1379
label | – – – – – – – – – – – – – – – –
label | Table 5.1 PERMISSIBLE TOLERANCE ON SLUMP
label | – – – – – – – – – – – – – – – –
label | Specified Slump (mm) ¦¦ Tolerance (mm)
label | – – – – – – – – – – – – – – – –
label | <60 ¦¦ ± 10
label | ≥60 ≤80 ¦¦ ± 15
label | >80 ≤110 ¦¦ ± 20
label | >110 ≤150 ¦¦ ± 30
label | >150 ¦¦ ± 40
label | – – – – – – – – – – – – – – – –
label | Testing to be in a NATA accredited test facility
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 3.9 - Curing
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
label | Acceptance Criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention for a min period of 7 days or as directed by the Superintendent.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 4.0 Finishing Works and Backfilling
checkpoint | 4.1 - Pit Backfill
label | Ref docs - Spec. 1354 Earthworks [Cl 3.7]
label | Acceptance Criteria - Pits to be backfilled in 150mm thick layers for a horizontal distance of 300mm as per RFI-069
label | ○ Backfill to be with a thermally rated compacted sand as per the design drawings up until the top of the conduit bank. The remaining backfill above the conduits to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
label | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
label | ○ Backfill shall not commence until concrete compressive strength reaches 15MPa unless approved otherwise by superintendent
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Test Report
checkpoint | 4.2 - Compaction - Backfill
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks [Cl 4.13]
label | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
label | 95% for pit bedding and conduit embedment
label | 97% for select fill areas
label | 92% for general fill areas
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 4.3 - Access Covers & Grates
label | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.4 - Step Irons
label | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 4.5 - Brass Marker Plates
label | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11], Drawings
label | Acceptance Criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 5.0 Conformance check
checkpoint | 5.1 - Survey Report
label | Ref docs - Spec. 0161 Quality [Cl 3.13]
label | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | Plan: +/- 200mm
label | Level: +/- 20mm
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey report
checkpoint | 5.2 - Acceptance and closure of non-conforming items
label | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
holdpoint | AUTHORITY HOLDPOINT