## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-019 HDPE Pipe Installation - Rev.2 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-019 HDPE Pipe Installation - Rev.2
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 1.2 - Lot Traceability
label | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Lot map
checkpoint | 1.3 - Pipe Material
label | Ref docs - Drawings
label | Acceptance Criteria - Has the correct class & type of drainage pipe been supplied. Has the pipe been inspected to be clean and free of defects?
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material conformance certificate
checkpoint | 1.4 - Embedment material
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | Acceptance Criteria - Embedment Material to be a cohesionless material with a plasticity index less than 6.
label | – – – – – – – – – – – – – – – –
label | Table 5.1 Embedment material grading
label | – – – – – – – – – – – – – – – –
label | Sieve size (mm) ¦¦ Weight passing (%)
label | – – – – – – – – – – – – – – – –
label | 19.0 ¦¦ 100
label | 2.36 ¦¦ 50-100
label | 0.6 ¦¦ 20-90
label | 0.3 ¦¦ 10-60
label | 0.15 ¦¦ 0-25
label | 0.075 ¦¦ 0-10
label | (Table taken from AS/NZS 2566.2, Table 5.5)
label | – – – – – – – – – – – – – – – –
label | Alternatively, embedment material may be a drainage aggregate (10,14 or 20mm) as specified in AS/NZS 2566.2
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Delivery dockets
bool | Test reports
checkpoint | 1.5 - Welder Qualifications
label | Ref docs - PIPA TP003
label | Acceptance Criteria - Have the workers involved in welding of HDPE pipes been trained by a Registered Training Organisation?
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Welders Qualifications
checkpoint | 1.6 - Underlying Lot Conformance
label | Ref docs - Underlying Lot ITP
label | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 1.7 - Set out
label | Ref docs - Drawings
label | Acceptance Criteria - Setout of water line alignment and level. This shall be presented for inspection by the superintendent, if requested.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 2.0 Excavation & Backfill
checkpoint | 2.1 - Excavation
label | Ref docs - Spec. 1352. Pipe Drainage [Cl 5.1], Drawings
label | Acceptance Criteria - Has the Trench been excavated to the correct width and depth to allow for the pipe size being installed?
label | PE Pipes:
label | – – – – – – – – – – – – – – – –
label | Table 5.2 Trench and embedment dimensions
label | – – – – – – – – – – – – – – – –
label | Extreme external ¦¦ Minimum dimensions (mm)
label | Dia (De)mm ¦¦ x : s : o : y
label | – – – – – – – – – – – – – – – –
label | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
label | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
label | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
label | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
label | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
label | – – – – – – – – – – – – – – – –
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 2.2 - Compaction –Bedding
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | Acceptance Criteria - Bedding:
label | ○ Has the correct thickness nominal of bedding been placed and adequately compacted below the pipe to achieve 70% Standard Compaction? (Compaction test N/A if drainage aggregate is used as bedding)
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.3 - Pipe & Fittings Installation
label | Ref docs - Drawings Manufacturer Specifications Spec. 1352 Pipe Drainage
label | Acceptance Criteria - Have correct pipes (size and type), bends, risers, valves & junctions been welded and installed as per manufacturer specifications? All weld records to be recorded daily on the HDPE butt fusion checklist
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | HDPE Butt Welding Checklist
checkpoint | 2.4 - Destructive Testing
label | Ref docs - PIPA TP003, PIPA POP014
label | Acceptance Criteria - Destructive Testing to be carried out as per PIPA guidelines using the Tensile Test Method at a NATA accredited laboratory. Frequency of testing will be one test every 100 welds. If a test fails the frequency to be dropped to one test every 10 welds until at least 5 consecutive conforming tests are received.
label | WITNESS POINT
button | Acceptance | Yes,No,N/A
label | Key - W
label | UGL Key - W
label | SHL Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.5 - Flanged Joint Installation
label | Ref docs - AS/NZS 2033 Cl 4.5
label | Acceptance Criteria - Flanged joints to be installed as per the drawings and manufacturer specifications. All flange joints to have a gasket or backing ring as nominated in the drawings.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 2.6 - Backfill
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | Acceptance Criteria - The pipe must be backfilled with the correct material and nominal thickness as per the project drawings and specifications
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
checkpoint | 2.7 - Compaction – Embedment material
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | Acceptance Criteria - PE Pipe:
label | ○ Side and Overlay: Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
label | ○ Layers not to exceed 150mm compacted thickness.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.8 - Compaction – General Fill
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
label | ○ Minimum relative compaction to be 92%
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.9 - Compaction – Select Fill
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
label | ○ Minimum relative compaction to be 97%
label | ○ Layers not to exceed 150mm compacted thickness.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.10 - Moisture Content
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 2.11 - Marker Tape
label | Ref docs - Design Drawings
label | Acceptance Criteria - Detectable Marker Tape to be installed a minimum of 300mm above the pipe. Tape to be red and labelled “Danger – Buried Fire Main Below”
label | Key - S
label | UGL Key - S
label | SHL Key - S
section | 3.0 Testing, Commissioning and Conformance
checkpoint | 3.1 - Preliminary Pressure Test
label | Ref docs - AS/NZS 3500 Cl 17.3.1.
label | Acceptance Criteria - Subjecting the pipe to 1500kPa for 30 minutes and checking for any leak.
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - W
label | SHL Key - W
checkpoint | 3.2 - Hydrostatic Pressure Test
label | Ref docs - AS/NZS 2033 Cl 7.2
label | Acceptance Criteria - Has the line undertaken a hydrostatic pressure test in accordance with AS/NZS 2033 Clause 7.2 achieving at least 1.25 times the maximum working pressure of the pipeline?
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Survey Report
label | Ref docs - Spec. 0161 Quality [Cl 3.13] RFI-026
label | Acceptance Criteria - Has an as-built survey of the system been completed to ensure all pipes are within construction tolerances.
label | Plan: +/- 200mm
label | Level: +/- 50mm
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Acceptance and closure of non-conforming items
label | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
holdpoint | AUTHORITY HOLDPOINT