## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-020 Screw Piling Load Testing. REV 4. | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-020 Screw Piling Load Testing. REV 4.
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks. UGL to confirm current IFC Drawings & Spec
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - R
checkpoint | 1.2 - Determine lot size
label | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - R
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Lot map
checkpoint | 1.3 - Material Certification
label | Acceptance Criteria - All Materials Certificate for all materials that are part of this works to be submitted to the client and approved
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - R
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Material Certification
checkpoint | 1.4 - Geotechnical Engineer
label | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience to provide Screw Pile design.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - R
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Bore Hole Log
section | 2.0 Materials & Equipment
checkpoint | 2.1 - Screw Piles Shop Drawing
label | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | Acceptance Criteria - Shop Drawings based on BH-308 to be submitted, reviewed, and approved by UGL.
label | Shop Drawings to include.
label | ○ Dimensional Requirement including tolerances if applicable.
label | ○ Sections designation and material grade
label | ○ All Welds and weld procedure
label | ○ Corrosion protection requirements
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Bore Hole Log
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Manufacturing of Steel Screw.
label | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | Acceptance Criteria - Fabrications
label | ○ Where CHS is cut using a mechanical saw, cuts to be straight and at an angle as the drawings, ±1%. The height difference does not exceed 5mm. There is to be no excessive gapping.
label | Welding
label | ○ All welding to be in accordance with AS/NZA 1554. Welding procedure specification to be submitted, reviewed, and approved by UGL.
label | Helices.
label | ○ Pitch at the inside of the helix must be equal, (±4% and no greater than 10mm). Gradients of the helices to be constant. Any radial measurements of helices should be perpendicular (±4% and no greater than 10mm).
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Material Certification
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Piling Machine
label | Ref docs - Drawings
label | Acceptance Criteria - Details and calibration records of the Piling machine and any other tools that may be required shall be provided for approval by the Superintendent.
label | ○ Calibration records for piling rig monitoring instruments to be submitted to Superintendent
button | Acceptance | Yes,No,N/A
label | Key - R
label | UGL Key - H
label | SHL Key - W
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Calibration Records
section | 3.0 Piling
checkpoint | 3.1 - Survey Setout
label | Acceptance Criteria - Pile locations shall be set-out at locations shown on the drawings and specifications – 3 test/ centre piles to be located as per the markup.
label | ○ Each pile is pegged by the surveyor and identified with a unique pile number.
label | ○ Static Load Test Compression: 4 Reaction piles to be marked out as per the dimensions of the I beam that is to be used
label | ○ Static Load Test Tension: 2 Reaction piles to be marked out as per the dimensions of the I beam that is to be used
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Survey Report
bool | Test Setout Plan
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Screw Pile Installation
label | Ref docs - Spec. 0003 Piling [Cl 3.4]
label | Acceptance Criteria - Each screw piles shall be inspected as the works proceeds.
label | ○ Rate of penetration to be monitored, if one helix pitch per revolution, it needs to be recorded and designer notified.
label | ○ Screw piles installed as per design and with min driving torque of 48,000NM
label | ○ Rate of penetration and torque vs depth to be recorded.
label | ○ Each piles finish height is to be checked.
label | ○ Testing piles to be 300 mm off the ground level, Reactive Piles to be made to suit ground level.
label | Notice: 2 working days prior to excavation of test pile
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Geotechnical Engineer Sign Off Sheet
bool | Pile Log Sheet
holdpoint | AUTHORITY HOLDPOINT
section | 4.0 Static Load Testing
checkpoint | 4.1 - Static Load Testing Set up
label | Acceptance Criteria - Australian piling Experts Static Load test Method Statement for set up of both Compression test & Tension test configuration.
label | ○ Place I Beam on the Test/ Reactive piles. Pile Stubs to be facing the same direction as the inner beam.
label | ○ Place Hydraulic Jack and the Dial Gauge, allowing the dial gauges to slightly touch the reference beam and securing it into place.
label | ○ Circular black casing to be turned until the reading is zero at 12’0 position.
button | Acceptance | Yes,No,N/A
label | Key - W
label | UGL Key - W
label | SHL Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Photos
checkpoint | 4.2 - Static Load Test Acceptance Criteria
label | Ref docs - Spec. 0003 Piling [Cl 3.13]
label | Acceptance Criteria - Test piles 1 & 2
label | Test results to conform to the following:
label | – – – – – – – – – – – – – – – –
label | Test Type ¦¦ Load: Description ¦¦ Magnitude (kN) ¦¦ Maximum Deflection (mm) ¦¦ Symbol
label | – – – – – – – – – – – – – – – –
label | Compression ¦¦ Serviceability (Proof) ¦¦ 120.0 ¦¦ 5.0 ¦¦ Ps
label | Compression ¦¦ Design Geotechnical Strength (Proof)1 ¦¦ 180.0 ¦¦ 10.0 ¦¦ Pg
label | Compression ¦¦ Ultimate Geotechnical Strength (Ultimate)2 ¦¦ 450.0 ¦¦ N/A ¦¦ Pu
label | Tension (Uplift) ¦¦ Serviceability (Proof) ¦¦ 80.0 ¦¦ 5.0 ¦¦ Ps
label | Tension (Uplift) ¦¦ Design Geotechnical Strength (Proof)1 ¦¦ 100.0 ¦¦ 10.0 ¦¦ Pg
label | Tension (Uplift) ¦¦ Ultimate Geotechnical Strength (Ultimate)2 ¦¦ 250.0 ¦¦ N/A ¦¦ Pu
label | – – – – – – – – – – – – – – – –
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - W
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Static Load Test Reports
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Static Load Conformance
label | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | Acceptance Criteria - The testing piles to conform with the following.
label | – The loading system shall have a capacity of at least 500kN.
label | – The overall loading and measuring system shall be capable of accommodating a pile movement of at least 25mm.
label | – Movements shall be measured with a system capable of delivery an accuracy of 0.1mm
label | – Test piles to have a min spacing of 2.5m
label | – Test piles top be min 5.0m from location of permanent piles.
label | – After UGL review of the Test report, the test piles to be removed and kept on site to facilitate inspection by UGL to determine their suitability for reuse.
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - W
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Test Method & Loading Sequence - Compression
label | Ref docs - AS2159-2009 8.4
label | Acceptance Criteria - Schedule of Lod Test Requirements from AS2159 Figure A1 Completed prior to commencement of loading.
label | ○ Loading & recordings to be carried out in accordance with AS2159 Table A1 (Attached as rear of ITP for reference)
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Load vs Displacement Records
checkpoint | Test Method & Loading Sequence - Tension
label | Ref docs - AS2159-2009 8.4
label | Acceptance Criteria - Schedule of Lod Test Requirements from AS2159 Figure A1 Completed prior to commencement of loading.
label | ○ Loading & recordings to be carried out in accordance with AS2159 Table A1 (Attached as rear of ITP for reference)
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | SHL Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Load vs Displacement Records
checkpoint | 4.5 - Reporting
label | Acceptance Criteria - Test reports forwarded to UGL/Snowy for Review/Acceptance in accordance with AS2159 A4
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Test Reports
holdpoint | AUTHORITY HOLDPOINT
section | 5.0 Conformance
checkpoint | 5.1 - Survey
label | Ref docs - Spec. 0003 Piling [Cl 3.10]
label | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
label | ○ The centreline at the top of the piles shall be within 75mm of the specified position.
label | ○ The inclination of the pile shaft shall be within ± 4% of the nominated inclination.
label | ○ The tolerance on the level of the top of the piles shall be ± 20mm.
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | As-Built Survey Conformance
holdpoint | AUTHORITY HOLDPOINT