## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-021 Screw Piling. REV 2 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-021 Screw Piling. REV 2
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks. UGL to confirm current IFC Drawings & Spec
button | Acceptance | Yes,No,N/A
label | Key - S
checkpoint | 1.2 - Determine lot size
label | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Lot map
bool | Piling Schedule
checkpoint | 1.3 - Material Certification
label | Acceptance Criteria - All Materials Certificate for all materials that are part of this works to be submitted to the client and approved
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Material Certification
checkpoint | 1.4 - Geotechnical Engineer
label | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience to provide Screw Pile design.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Bore Hole Log
section | 2.0 Materials & Equipment
checkpoint | 2.1 - Screw Piles Shop Drawing
label | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | Acceptance Criteria - Shop Drawings based on BH-308 to be submitted, reviewed, and approved by UGL.
label | Shop Drawings to include.
label | – Dimensional Requirement including tolerances if applicable.
label | – Sections designation and material grade
label | – All Welds and weld procedure
label | – Corrosion protection requirements
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Shop Drawings
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Manufacturing of Steel Screw.
label | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | Acceptance Criteria - Fabrications
label | ○ Where CHS is cut using a mechanical saw, cuts to be straight and at an angle as the drawings, ±1%. The height difference does not exceed 5mm. There is to be no excessive gapping.
label | Welding
label | ○ All welding to be in accordance with AS/NZA 1554. Welding procedure specification to be submitted, reviewed, and approved by UGL.
label | Helices.
label | ○ Pitch at the inside of the helix must be equal, (±4% and no greater than 10mm). Gradients of the helices to be constant. Any radial measurements of helices should be perpendicular (±4% and no greater than 10mm).
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Material Certification
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Piling Machine
label | Ref docs - Drawings
label | Acceptance Criteria - Details and calibration records of the Piling machine and any other tools that may be required shall be provided for approval by the Superintendent.
label | ○ Calibration records for piling rig monitoring instruments to be submitted to Superintendent
button | Acceptance | Yes,No,N/A
label | Key - R
label | UGL Key - S
label | SHL Key - W
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Calibration records
section | 3.0 Piling
checkpoint | 3.1 - Survey Setout
label | Acceptance Criteria - Pile locations shall be set-out at locations shown on the drawings and specifications
label | ○ Each pile is pegged by the surveyor and identified with a unique pile number.
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Survey Report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Screw Pile Installation
label | Ref docs - Spec. 0003 Piling [Cl 3.4]
label | Acceptance Criteria - Each screw piles shall be inspected as the works proceeds.
label | ○ Rate of penetration to be monitored, if one helix pitch per revolution, it needs to be recorded and designer notified.
label | ○ Screw piles installed as per design and required machine torque.
label | ○ Rate of penetration and torque vs depth to be recorded.
label | ○ Each piles finish height is to be checked.
label | Notice: 3 working days prior to excavation of test pile
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | SHL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Geotechnical Engineer Sign Off Sheet
bool | Pile Log Sheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Concrete supply
label | Ref docs - Spec. 0003 Piling [Cl 3.9]
label | Acceptance Criteria - Verify:
label | – Concrete mix
label | ○ A concrete delivery docket to be supplied with each batch delivered.
label | ○ Concrete work shall be in accordance with the technical specification for concrete supply, construction and grouting and any other notes on drawings.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - W
label | SHL Key -
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Material dockets
bool | Concrete Pour Record
bool | Pile Log Sheet
checkpoint | 3.4 - Concrete Placement
label | Ref docs - Spec. 0003 Piling [Cl 3.9]
label | Acceptance Criteria - Concrete to be placed as per the construction drawings in accordance with AS3600.
label | ○ Prior to the pour ensure there is no water or debris at the base of the pile shaft.
label | Notice: 1 working day prior to placing concrete for test pile
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - W
checkpoint | 3.5 - Pile Cap Installation.
label | Ref docs - Spec. 0003 Piling [Cl 3.9]
label | Acceptance Criteria - Reinforcement for pile cap to conform with drawings and specification. Reinforcement grade to be either 250N or 500N.
label | ○ Formwork to conform with drawings and specification.
label | ○ Concrete to be vibrated adequately during placement to ensure there are no voids or segregation.
label | Notice: 1 working day prior to placing concrete for test pile
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - W
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Concrete Pour Record & Pile Log Sheet
checkpoint | 3.6 - Concrete sampling
label | Acceptance Criteria - The nominal rate of sampling shall be taken:
label | (a) Compressive strength: One set per pour or as otherwise directed by Superintendent;
label | (b) Slump: One per batch of concrete (xxx mm)
label | Acceptance Testing shall be done at a NATA registered laboratory
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - W
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Test report
checkpoint | 3.7 - Concrete RL and depth
label | Ref docs - Drawings
label | Acceptance Criteria - Screw Piles depth, size, position, and concrete RL as per the Piling Pile Log Sheet and Drawings.
button | Acceptance | Yes,No,N/A
label | Key - S
label | UGL Key - S
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | Pile Log Sheet
section | 4.0 Conformance
checkpoint | 4.1 - Survey
label | Ref docs - Spec. 0003 Piling [Cl 3.10]
label | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
label | ○ The centreline at the top of the piles shall be within 75mm of the specified position.
label | ○ The inclination of the pile shaft shall be within ± 4% of the nominated inclination.
label | ○ The tolerance on the level of the top of the piles shall be ± 20mm.
button | Acceptance | Yes,No,N/A
label | Key - H
label | UGL Key - H
label | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
bool | As-Built Survey Conformance
holdpoint | AUTHORITY HOLDPOINT