## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | Ω (DEPRECATED) ITP-003 Subgrade/Foundation Preparation (v0) | itp | ITP-003 Subgrade/Foundation Preparation
3888cb15-c6e9-4774-94f4-ef0136a8d2b8 | section | Subgrade/Foundation Preparation
ac475546-f2ce-4c02-a316-d1bc173edfa8 | checkpoint | SP.1.1 - Underlying lot & ITP signed off and conforming
0ba38702-7e4a-5305-999e-9d0c380b72b1 | note | Responsibility - ENG
cd2dc35a-9502-5741-8b68-f7ea4a27f70c | note | Test Method - Visual
cdae2c66-de7c-5ca1-aaa5-1dcaadf88613 | note | Conformance Criteria - Topsoil ITP closed out
39fb73af-ee7e-5cfb-a384-6dabf3434961 | note | Frequency - Prior to Works
8ee4a552-2995-58d0-9e48-752e910a3518 | note | Link to ITP - TS1.6
2897bed4-d43c-43af-aa95-e7d21d62accd | checkpoint | SP.1.2 - Embankment fill material
6698839b-9391-5658-8be4-54b8641f1d75 | note | Responsibility - ENG
afc74dae-bdf5-5e03-929d-edad53d7c4be | note | Test Method - Visual
e98679c2-b70a-536b-9a9c-bef3a3d5405e | note | Conformance Criteria - Ensure CBR10 subgrade replacement materials have been approved for use and within specification
6171a00d-a560-5761-b6c3-27e3f1536543 | note | Frequency - Prior to works (Check if this has already been completed at ITP Pre-construction stage)
cd5ca6cd-ecd1-5805-9164-3664d4d56063 | note | Link to ITP - PC1.12
8ebc67a8-3f8e-5cfc-aa2c-2ab9989333fa | note | Thiess HP/WP Check - HP
c22e0b29-ee08-5f77-a31c-95c7a96e983a | note | Inspector HP/WP Sign Off - WP
e6f51fb7-6c5b-4f3e-b073-2d76ec83af4c | signoff | WITNESS POINT
f18384a0-36b1-404a-ba16-b643c5ba2214 | checkpoint | SP.1.3 - Survey Set out
4b25c72b-e94d-529d-aa6b-3835cde661fb | note | Responsibility - Surv
6db7605f-6648-5850-b3e9-c41e7f2cfe70 | note | Test Method - Field
d0b3b03b-7fa3-511c-b9b7-9c1db665c392 | note | Conformance Criteria - Areas of work to be set out by surveyor and/or models in plant
662d8646-ee30-5fd1-9ce4-7ccc7f1318a9 | note | Frequency - As required
57f8ebaa-8d19-5e99-8c43-2d16b8aff760 | note | Thiess HP/WP Check - HP
45364d23-92d3-5007-895d-5930c2185259 | note | Inspector HP/WP Sign Off - WP
4d57dd0c-68ce-48ab-bd54-2cee86b3fca9 | signoff | WITNESS POINT
dbba825e-74ac-4f55-a21f-fc1ed370c529 | checkpoint | SP.1.4 - Removal and replacement of unsuitable material
747e0dbf-fcba-5695-b1a3-01b9361dabf7 | note | Responsibility - SUP
30352755-f0c8-5be8-bb2c-b08aec36a9b4 | note | Test Method - Field
21dbc2ce-af3d-5371-a91b-5b924c2fdfbc | note | Conformance Criteria - Determination of unsuitable material by the Level 1 GITA or Inspector (Sedgman) is required prior to the removal of any unsuitable material. Unsuitable material criteria is in the specification.
e4d39c20-3fe5-5de7-bc69-b4f7f854c5fd | note | Frequency - As required
153058c6-af8e-59bf-ba0a-0d361dab80d0 | note | Link to ITP - PC1.12
c84d290d-5958-537c-9c8e-48a52d608cc3 | note | Thiess HP/WP Check - HP
47ac2868-dfa4-5963-aa63-9fdf4d28309a | note | Inspector HP/WP Sign Off - HP
abc7c254-a1c2-4d1e-a2cc-9dda06113411 | signoff | HOLD POINT
4fd12e0e-f712-429a-8540-2f342f7bb820 | checkpoint | SP.1.5 - Subgrade/Foundation preparation
53ba4411-a5de-531c-961b-c446ae05e42d | note | Responsibility - SUP
d0ce048c-197d-5912-80e4-60df6073967c | note | Test Method - Field
36fa4a64-d46f-5f5c-ba5f-c800dda0a565 | note | Conformance Criteria - Foundations for embankments to be ripped 200m deep, moisture conditioned then compacted. Density requirements: < 300mm from finished level under roads & structures minimum RDD 97%, all other areas and depths RDD 95%, moisture content -1% to +2%, normal level of testing 1 test per 500m3, reduced level of testing 1 test per 1,000m3.
aa96d8ee-81e4-5cf0-9311-27c35702a144 | note | ○ All material exposed in cuttings at subgrade level minimum CBR 3 or DCP 150kpa. If CBR2: Remove & replace with CBR10 select fill 150mm deep. If CBR1: Remove & replace with CBR10 select fill 250mm deep
0d516928-6b59-57fe-b7ca-1ee4b1414d64 | note | Frequency - As required
7ad79ff9-eae9-5987-9e5b-82402f192491 | note | Link to ITP - PC1.12
ed5e1566-2280-51c3-be8e-1eb5461ee755 | note | Thiess HP/WP Check - HP
0e74b08d-944f-5d4f-a1a0-598735ce57d8 | note | Inspector HP/WP Sign Off - HP
c760cec8-8ceb-4a0d-a985-5324d40c2be8 | signoff | HOLD POINT
187efc59-29ad-49ed-8390-8b60becf1967 | checkpoint | SP.1.6 - Trim subgrade
b3913e7c-bebc-5d12-9a25-bb41ac3c832f | note | Responsibility - SUP / SURV
ae93ba34-1d60-5116-972f-c6a9676fd814 | note | Test Method - Field
a76edf78-b419-5b0e-8f24-353676836a66 | note | Conformance Criteria - Trim all subgrade to the lines and levels shown on the drawings in accordance with the following tolerances: Top of bulk earthworks +/-50mm; Road subgrades & under buildings & structures +0mm to -25mm.
549c5914-07e3-55e7-bad0-0bbf1fce3fab | note | Frequency - As required
ffcc823b-be30-5129-a036-a226605a90d8 | note | Thiess HP/WP Check - HP
f45a1c01-4b58-5b13-93cd-bdb9bab52ee2 | note | Inspector HP/WP Sign Off - HP
f23b4a57-60f2-4a1f-bbca-c06f05da3796 | signoff | HOLD POINT
bf2a450e-c73d-4e58-b6c5-f8d0ad38ec50 | checkpoint | SP.1.7 - Proof rolling
6ac50545-6961-5f6e-9358-6a0ee1fb360f | note | Responsibility - SUP
c709b948-1ca6-56d0-9cf6-aefd7aedbedc | note | Test Method - Field
c378f6ef-6f7b-516a-8e9d-004032c7b05c | note | Conformance Criteria - Proof-roll subgrade/foundation surface prior to placement of embankment fill. Proof roll under a standard 8 tonne axle load or 10,000L water cart or heavy self propellled smooth drum roller dynapac 620D or equivalent to confirm that, in the Inspector (Sedgman) s opinion, deflections are negligible
3a550ce8-816b-5397-a561-01745103d955 | note | Frequency - As required
ffbdbde8-4eed-59a2-a503-187d9143d7f6 | note | Thiess HP/WP Check - HP
118fb4dc-b6f4-5712-8aa5-f3abc584a348 | note | Inspector HP/WP Sign Off - HP
6e4cdf2a-ea9e-4e8c-aef7-9e25439a1400 | signoff | HOLD POINT
71594be2-04a9-4642-8c27-46fc02041e66 | checkpoint | SP.1.8 - Surface level check and survey pick-up
ae3e3dc0-bbb7-5161-ab48-8f3e93da7c89 | note | Responsibility - SURV
0233e3da-d7b0-57cb-a28f-791670b10318 | note | Test Method - Survey / Field Test
181a65b6-888f-5718-abc5-1c5ea421f1f5 | note | Conformance Criteria - Surface level picked up as per Table 10 C15 (DXF file format, volume calculated and filr saved in Construction Team Sharepoint and detailed in register
8205adaf-59f9-5e9c-94e0-2407ce8f2386 | note | Frequency - As required
816da858-ab98-54c1-b51c-3cfa04e1791f | note | Thiess HP/WP Check - HP
8fd83ed0-b72c-5af0-9b4a-dc40044dbcee | note | Inspector HP/WP Sign Off - HP
4bcc759d-350a-4250-8f6b-244794b056e2 | signoff | HOLD POINT
cf8c9bf4-266f-4abf-8026-2827cb980a71 | checkpoint | SP.1.9 - QA close out
f480ed2e-dad9-5d6f-bd96-060b4d89131c | note | Responsibility - ENG
1a40051b-4408-5dcb-b87a-220c77689e1a | note | Test Method - Visual
f5308beb-802e-5f5c-af91-fc47fbd956cb | note | Conformance Criteria - GDP permits closed. ITP closed. Approved MDR.
5dd34aff-46bd-5dab-b2af-b6da8a1c725f | note | Frequency - As required
348d3807-5f57-5b32-ba96-d3d360a60099 | note | Thiess HP/WP Check - HP
b9692b12-b245-507c-a77b-b367d15bbc3d | note | Inspector HP/WP Sign Off - HP
fe791962-27f7-473b-bde7-91e7f40b4125 | signoff | HOLD POINT