## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-CIV-007-E - Utilities Ducting | itp |  |  |  |  | ITP-CIV-007-E - Utilities Ducting
section | 1 - Material Compliance (1.1 - Fill Materials)
checkpoint | 1.1.1 - Bedding material PAP 7 for PE pipes AP40 for Chambers
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.4
label | Acceptance Criteria - Accept/ Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.1.1 - Backfill Material GAP65 or TNZ M/4 AP40
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.5 CIV Spec - S4.4.5
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.2 - Pipes)
checkpoint | 1.2.1 - Pipes: 110 OD PE SDR 17, 160 OD PE SDR 17
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S12.3.3
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - All the PE pipe colors must comply with the respective service as mentioned in S12.3.3
holdpoint | HOLD POINT
checkpoint | 1.2.2 - Bends: Pre-Fabricated HDPE bends
label | Frequency - Each Bend
label | Spec/standard - CIV Spec - S12.4.5
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.3 - Electrofusion Couplers
label | Frequency - Each coupler
label | Spec/standard - CIV Spec – S12.4.6
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 2 - Construction (2.1 - Pre-Condition Assessments)
checkpoint | 2.1.1 - Existing ducts/chambers to be removed
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.4.1
label | Acceptance Criteria - Removed and disposed
label | Measuring Devices - N/A
label | Reporting Format - Photos / Asbuilts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - Once removed, all trenches to be backfilled to Subgrade level
checkpoint | 2.1.2 - Survey Setout Pipe alignments, Position, Heights
label | Frequency - Each Pipes/trench
label | Spec/standard - CAD Models
label | Acceptance Criteria - Survey Setout Pipe alignments, Position, Manholes Position and Heights
label | Measuring Devices - GPS, Total Station
label | Reporting Format - Setout CSV file, Photos/Visual
label | Remarks - Setout model and CSV provided by HCL
section | 2 - Construction (2.2 - Ducting)
checkpoint | 2.2.1 - Excavation Extents
label | Frequency - Each element installed
label | Spec/standard - CIV Spec - S12.4.2 CIV Spec - S4.5.9 (earthworks section)
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level and GPS
label | Reporting Format - N/A
label | HCL - M
label | Hold Points Sign off - Witness Point
checkpoint | 2.2.2 - HDPE Ground Mat
label | Frequency - Each Unit
label | Spec/standard - Note 10 – DP0001- MMD-DRW-UT-F-Z- 3137 - 3139
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - Photos, Dockets
label | Reporting Format - N/A
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - HDPE ground protection Mat will be installed only in areas shown in the drawings.
label | ○ Single layer, 1m for comms, 2m for HV&LV
checkpoint | 2.2.3 - Bedding, surround
label | Frequency - Per installation
label | Spec/standard - As per drwgs min/ max fill
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level / tape / staff
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - SUB
label | Consult - R
label | Remarks - PAP7 for PE
checkpoint | 2.2.4 - Pipe installation, Connection and jointing Electrofusion weld
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.4.5 CIV Spec - S12.4.6
label | Acceptance Criteria - N/A
label | Measuring Devices - Observation
label | Reporting Format - QVC, As-Builts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
label | Remarks - Caps to be used if lines not complete, All Welding to be performed under controlled Environmental conditions.
checkpoint | 2.2.5 - Weld Testing
label | Frequency - All welding Joints
label | Spec/standard - CIV Spec - S12.5.2
label | Acceptance Criteria - N/A
label | Measuring Devices - Visual Checks for each Weld
label | ○ Peel Decohesion Testing for at least 3 duct weld pieces is recommended
label | Reporting Format - QVC, Photos, Test Results
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
label | Remarks - Frequency of testing in line with ISO13954 & ISO13955
checkpoint | 2.2.6 - Tracer Wires
label | Frequency - Comms duct
label | Spec/standard - CIV Spec - S12.4.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Tracer Wire to 4mm2 multi-Strand Accept/Reject
label | Measuring Devices - Continuity Test (electronically generated tone and detector probe)
label | Reporting Format - Photos, Test results, QC
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.7 - Inspection for Duct size, color, spacing,
label | Frequency - All ducts
label | Spec/standard - CIV Spec - S12.4.5 DP001-MMD-DRW-UT-F-Z-3137 - 3139
label | Acceptance Criteria - N/A
label | Measuring Devices - N/A
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
checkpoint | 2.2.8 - Warning Tapes/ marker tapes
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S12.3.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Warning Tapes must refer to respective Services. Installation heights must follow the typical trench details.
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.9 - Mag Slabs/Polymeric Slabs
label | Frequency - HV and LV ducts
label | Spec/standard - CIV Spec - S12.3.10 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Installation heights must follow the typical trench details.
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.2010 - Draw Cord
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.3.8 S12.4.8, DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Continuous draw cord and excess to be left at the ends of each duct
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.2011 - Pipe Cover and Backfilling
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S4.4.5 Table 4.3 (Earthworks Section), DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Backfilling CIV > 25
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - SUB
label | Consult - I
label | Remarks - 12.5.2 of the DP Civil Specification only applies to the trench backfill material and does not apply to duct surround material.
section | 3 - Post Construction (3.1 - As-Builts)
checkpoint | 3.1.1 - As built Works
label | Frequency - Each pipe
label | Spec/standard - N/A
label | Acceptance Criteria - N/A
label | Measuring Devices - Surveyor Equipment, Total Station
label | Reporting Format - Certified As- built PDF and DWG file
label | HCL - R
label | SC - Sub
label | Consult - R
section | 3 - Post Construction (3.2 - Duct Condition)
checkpoint | 3.2.1 - Duct Cleaning and Proving
label | Frequency - Each Duct
label | Spec/standard - N/A
label | Acceptance Criteria - N/A
label | Measuring Devices - Brush and Mandrill
label | Reporting Format - Photos/Videos
label | HCL - M
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
checkpoint-no-status | Document Deliverables
textbox | (The documents listed below shall be completed and compiled during the course of the construction)
checkpoint | Distribution Records
signoff | Signoff