## Resources
Id | Type | Name | Values | Prompting Name
942065cb-d777-4656-8aff-4e2afaf9f151 | checklist | ITP No. 05 Switchboard Delivery |  | ITP No. 05 Switchboard Delivery
097a4350-1741-4d06-9542-6ff17576711f | checkpoint | Prior to delivery visual inspection by foreman to coordinate delivery on site
fe0ee135-358a-5bcc-baf0-2ff33ea6314c | note | Determine method of unloading eg. crane, forklift, man power, specialist subcontractor & arrange
cacf7da2-49ea-5a1d-b43c-b3f4a3b27899 | note | Coordinate time of delivery
7931900e-2fb9-5af6-bf49-4d4634b3d643 | note | Positioning into place eg. crane, forklift, rollers, manual, specialist subcontractor. if vast electrical vic are positioning main switchboard, maneuvering kit is to be delivered with the main switchboard. Distribution boards require lifting trolley
a7020310-b59f-40ca-8a15-18180a407d65 | checklist | zSYS - Toolbox Meeting Checklist V1 |  | Toolbox Meeting
f1ea0fc8-6885-4170-ae64-b23847a468a2 | checkpoint | Details
5f1a7e7a-ab8c-5e4a-a16f-00a5e98c6c27 | textbox | Supervisor
e013d24b-ba44-549e-bdc8-b2faeeb72859 | tickbox | David Interligi
35e0b83d-ad8a-5f42-84c4-cd4275673277 | tickbox | Michael Borg
6590847e-6909-5752-b67c-ed3a338ca5d0 | tickbox | Rob Pellegrino
02f88a85-ee3d-582a-b90e-398c41bbca6b | tickbox | Adrian Sibbing
3365848b-5ce7-58c6-87fd-db7439599ccc | tickbox | John Wolosz
1efa7ac7-3ea8-5812-b07e-b8e42236f0b9 | tickbox | Lochy Brannelly
db630244-097f-5cc8-bd2c-ce39e092c2f4 | tickbox | Damon Guy
57876400-8f5e-5378-bed4-38173cca9798 | tickbox | Jake Condon
8194a72b-f11c-5f75-ac94-bd21da5ddf58 | tickbox | Julian Cannata
743bfe77-618c-5d1d-90db-57ef42f27dd2 | tickbox | Devilliers Duvenage
439bb08a-ec4d-501f-8fb1-2c93ee8a1382 | tickbox | David Currie
01e81fc1-29a3-58c7-a367-21ebffa7c374 | tickbox | Steve Price
a151a57c-688b-5752-b9ad-e7d8a7d6c5bc | note | Topics discussed
fd26b6e5-18dc-5d9d-9f97-baeb70cf8def | tickbox | Injuries, near misses & incidents
90306640-533e-5893-9db4-9b4e24ee2fdf | tickbox | Management of major hazards
1a6d58d8-7c73-5d9c-b5d5-6e3de2966006 | tickbox | Compliance with Vast SWMS
008e5c6d-0007-5e77-ac45-feb378a05c0b | tickbox | Safety
9ea08a2a-9117-572b-b537-4c104905cd49 | tickbox | Housekeeping
97d2983b-8bbc-5c67-9739-a579f2f9be1c | tickbox | PPE (Glasses & Hard Hat's on at all times)
620e95c0-0275-51b7-9b94-0b1cb15ebc03 | textbox | Actions from last meeting:
c21ee053-2296-57a7-bc41-00c22d24aeba | textbox | Injuries, Near Misses and Incidents since last meeting:
37fd2546-d75b-509e-b6bb-d7875daef3b5 | textbox | Management of major Hazards and High Risk Activities:
5bc28950-37e0-5828-a6b3-57139c439173 | textbox | Compliance with SWMS & Risk Assessment Booklets or Forms:
fcd798cd-28ac-5d47-a096-a06ecf963478 | textbox | Reviews of any Safety Forms, SWMS, Policies, etc
9881fae8-4878-5a90-a37f-edc3ed203d07 | textbox | Comments/issues from the floor:
fb24dae8-5cab-46ea-abf9-868490e15a09 | checkpoint | Signed off by Supervisor
c8dac144-8c18-5978-b666-e698bb6792d6 | textbox | Corrective actions
01b5e3fb-9585-450a-adb5-d421f69dc932 | checklist | ITP No. 04 Conduit / Cable Tray |  | ITP. No 04 Conduit / Cable Tray
7d52b28a-d232-478e-a233-a416449746ef | checkpoint | Coordinate with other services
00021ec4-05fe-4b2b-97d9-cf3f5c34be30 | checkpoint | Ensure segregation from comms / data services
03c7caeb-4c2a-5713-9d67-83afa233bcb8 | textbox | Size and type of conduit
cbf58bd3-1d0c-4936-a00e-7c7284cb4602 | checkpoint | Install conduit fittings
c356a9ec-d944-5fa6-b1e8-ba47d6f22867 | textbox | Size of cable tray
3498c484-3223-4348-b681-00efe89629fa | checkpoint | Install fittings
a79d5182-4b77-453e-aa8c-6f16f5f695ad | checklist | Add Pre Start Meeting Checklist |  | Pre Start Meeting
2bcda5fd-e342-46c6-9d75-1ca983557bf6 | checkpoint | Details
108d9c54-fa00-58d9-aad6-55a00435e049 | textbox | Conducted by
11f7eced-d7c4-5634-9a5b-42f40edbf45b | textbox | Area
2a772b97-a2e6-407f-ac1c-352712648302 | checkpoint | Any Safety Concerns from last meeting - add comments if required
68b55c49-bcfc-5353-b223-3ea6c2bbb94c | textbox | Today's weather
ff44e96d-6d1d-57ad-905b-ae776dc13388 | textbox | Today's work is
82614f96-d108-5771-ab4d-517bc6edebe9 | textbox | Newly Identified Hazards Are
0285b4c0-52cd-543e-9c11-6619e7279637 | textbox | Control measures are
cc4ab476-a5fd-452c-9d61-7beb3f3b485e | checkpoint | Scope of work for the day was discussed and understood
27f95047-d008-45ce-ac8f-1522c08a3214 | checkpoint | Major High Risk Activities are understood and controlled in a SWMS
1b535f32-f037-4929-b81f-a3ea2a3f0a0a | checkpoint | Relevant SWMS were reviewed, understood and signed by all workers
27f0b807-bea5-4dd2-a088-c840880ca08e | checkpoint | Relevant Permits to Work are in place and understood
f63cc9d6-0565-4af1-9229-148bdbc6c3b3 | checkpoint | Tools and equipment are in good working order
22dda3f1-b6af-40dd-822c-b61355ae23ec | checkpoint | All electrical equipment displays current test tags
bdf7bf5f-a9b8-4c6c-9130-0cdedfe05ddd | checkpoint | Appropriate PPE for tasks is understood and available
b2a04cc9-de5d-41ea-a7a3-7944cbe44b25 | checkpoint | Housekeeping and clean-up has been discussed and is understood
8bb10d80-163b-5f69-bb6f-caca3f26139e | tickbox | David Interligi
ec73d7df-388f-59f0-a2c7-1e243e52ac28 | tickbox | Michael Borg
917c3df5-0a15-53d4-95f3-fc073c5919c4 | tickbox | Rob Pellegrino
6fb2ddfc-a104-5f1c-a2c4-8eb13d082fd3 | tickbox | Adrian Sibbing
447990f2-a013-5b7f-b6a7-5d6eabdf724b | tickbox | John Wolosz
a8c1cdd2-7ab8-5da5-a1d3-bd7614a0a4db | tickbox | Lochy Brannelly
8388cee1-2dbe-5fa3-a3c0-7ea71429b08f | tickbox | Damon Guy
95076296-e4b4-5521-84a0-1515b90d463f | tickbox | Jake Condon
0a10a9af-0730-5f8c-91b0-5bda05a74329 | tickbox | Julian Cannata
355b6eb0-45c2-5194-bc72-3d7c2a3d4521 | tickbox | Devilliers Duvenage
41f83a5d-ec84-5a4d-8f53-c1cd532fee3d | tickbox | David Currie
b6eae548-8509-554e-9e1f-5b27a8e36ee5 | tickbox | Steve Price
79a176fe-5859-4023-a0ad-5027fc7f7424 | checkpoint | Signed off by Supervisor
2e46cbb3-a806-4cb7-af7c-b57d550971f1 | checklist | ITR No. 03 Apartment - Electrical Fit Off |  | ITR No.3 Apartment - Electrical Fit Off
03cdc7c8-9d4a-4177-a197-b85b1a4e49d0 | checkpoint | Area clear, tidy and accessible
ba93f141-e489-4bab-b9e9-b8921b959f10 | checkpoint-no-value | Drawing Rev No.
c52cb059-6814-5f32-9340-165b50c2da36 | textbox | Drawing Rev No.
c666638a-5c36-456a-bec1-f7b633127609 | checkpoint | Fit Off Downlights
306244d9-c534-4940-9c0a-b709f763f1be | checkpoint | Fit Off Smoke Detectors ( leave tab & dust cover on )
54337a4d-0a7d-48c3-b10f-75c739a87901 | checkpoint | Fit off joinery GPO's & install cover plates.
9c1ea594-9ea8-4374-ac7c-8b0e9cd4dad9 | checkpoint | Fit off Laundry GPO & switch
ed33bd2c-518a-43e4-bdb5-1f0384268a17 | checkpoint | Fit off TV Point
3945e303-9148-4186-9671-26e7c0fa4753 | checkpoint | Fit Off Data Points
419ce6df-5864-48e1-b256-e4a27af90239 | checkpoint | Fit off Balcony Light
f5b8986c-7dff-4652-b70c-7934aa41eed5 | checkpoint | Fit off AC Isolator
70ca5d79-867b-497c-9dc1-9d60f12edd5c | checkpoint | Fit Off WP GPO ( if applicable )
f4e00515-357d-42a9-a922-5f9abf8d5ccc | checkpoint | Fit Off LED Strips
1e6b9c3e-a45f-47de-8999-5283fc2cc6a0 | checkpoint | Fit Off Pendent
421fc25c-53e4-477d-b45e-f13152cbcb0a | checkpoint | Install Oven
bccdfe94-e156-4528-ae3c-93e4e74b265e | checkpoint | Ensure area is left clean
fed9f1c7-a62d-4dee-b65a-793cf69e39b9 | checklist | ITP No. 09 Communications - Data & Voice Cabling |  | ITP. No 09 Communications - Data & Voice Cabling
33921c4c-e097-46ba-8897-38fa50cc3f0a | checkpoint | Obtain the relevant and most recent drawings and specification
23e0d5f1-0477-4193-99f3-f42ba4ff5849 | checkpoint | Install cable support or conduit where required
cdf68592-f9e7-5ebc-ab25-96fb4498beae | note | Verify correct cable type
4fc0f77e-dfaf-54a3-9c8e-c531d482ae97 | note | Decide appropriate cable numbering sequence relevant to final fit off sequence
681ff54c-5594-40a5-8eed-c24f0dc3d5a2 | checkpoint | Install cable within or on cable support system as appropriate
15db011e-ff2a-435c-835e-f98cd1e48ddc | checkpoint | Form cables into relevant fit-off groups at the cabinet end
26fb743b-68ce-44e1-b059-701257c41c91 | checklist | ITP No. 01 Conduit in Slab |  | ITP No. 01 Conduit in Slab
3a50a0f2-e275-4b70-865e-c014d6f35030 | section | Preparation
14d4a8de-3f6d-4470-9041-465ee22433ab | checkpoint | Area clear, tidy and accessible
072ff780-ed0f-4b6d-b122-5994d023c81f | checkpoint-no-value | Drawing Rev No.
a84fff2c-e61f-501a-9c13-2576ab3318ae | textbox | Drawing Rev No.
e1e875b4-c224-4cf2-bd2f-7a53c2858a86 | checkpoint | Determine origin and destination of riser cupboards
93af1630-0567-4d10-9c97-9f3de8344a3b | checkpoint | Check clear of other services, penetrations etc
ba3e3853-5e5c-4093-ada8-a4dac519a7dd | checkpoint | Check cable size to verify conduit size
694db822-a65a-4c1b-bda3-4d2b79c5918c | checkpoint | Mark out positions of junction boxes, orange flanges and penetrations where necessary
98b78427-b565-4bf1-acec-2b183babfff9 | checkpoint | Check if expansion joints are required
764255f5-c510-47cd-8423-fc7e92bba69b | section | Installation
909bfdb0-abee-4aec-9ab0-84da20494d4a | checkpoint | Installation of sleeves for stair lights
12bd26c7-a513-40ab-a4f3-686b3352877a | checkpoint | Installation of sleeves through the core
868f91c4-6e70-4dcf-b308-1b3b8c7e0b47 | checkpoint | Installation of foam at riser cupboards if applicable. Foam to be duct taped and secured down to deck.
8c4b3963-d68f-4c2a-8161-433182aeb2ce | checkpoint | Install junction boxes, flanges and conduits with glue
ef1813cb-39a8-411f-a3db-deb045194c0a | checkpoint | Install reo turned up in riser cupboard for earthing of the slab
eb6492ed-0d21-4f2f-b660-e11afe195ebc | checkpoint | Install any temp conduits where necessary for alimak lighting and temp toilets
97cfb283-e758-4a71-976f-6710f7a04603 | checkpoint | Ensure all conduits are 50mm above deck
14d931fc-2442-4e2b-bc9d-06146f7376ed | checkpoint | Ensure all conduits are tied and secured
a8b1730f-2d64-4b62-a8b6-c5e0bd2b6d6f | checkpoint | Ensure all conduits for the next pour are through to the next deck
fcf1544e-6520-4abc-8aab-d54c1de3a119 | checkpoint | Clean any mess left on deck
d805fb6b-c29b-4d44-a1b7-6a76fd10234e | checkpoint | Final walk through and mark up plan of conduit runs for as builts.
2d76e466-3ee6-4377-9e29-f369e9aba0d7 | checklist | ITP No. 14 DB Test Results |  | ITP No. 14 DB Test Results
43ab57f8-2f73-4253-b2ea-cfdec91083a0 | checkpoint | Visual inspection
5f4abc1e-9c8e-53a3-af66-c037c7b9bff1 | textbox | Vast testing device number
4343d93f-6209-53b3-902e-4e561131cf72 | textbox | Cert. electrical safety number
6fe21856-11f0-5d51-a4d1-8562313e9ace | textbox | Number of Lights
562d4d8e-0c31-572e-a247-3793a1fb55f8 | textbox | Number of GPO's
d9ebd074-7303-5e34-b4e0-8f0779dd4f43 | textbox | Earth & continuity resistance
a91b6147-4cb1-5d8e-86ca-3156915405b5 | textbox | Insulation resistance
8b0d93ff-697e-4ba3-bb45-17386e8bd9d7 | checkpoint | Polarity / correct connections
b49d999c-afa7-5af4-b39e-7779798c65b0 | textbox | Earth loop impedance
3fcc6f83-86d3-4250-8360-b6da4b75b2a1 | checkpoint | RCD testing contractual requirement
43840691-3640-42d7-81f1-4e45c6824dbc | checklist | Documents |  | Documents
0d32b920-3b40-4aac-aa40-13e45a1c0c35 | checkpoint | Attach Document
4133d766-35cd-4267-8a26-b7393b02e007 | checklist | ITP No. 08 Communications - Data & Voice Termination |  | ITP. No 08 Communications - Data & Voice Termination
18d10b04-ea9c-4e2e-bdc1-cd295a6b5b7d | checkpoint | Visual check ensuring cable to be fitted off in correct position
43e54b12-18c6-4234-87e5-45b7d8d3c4fc | checkpoint | Selection of correct tool to be used for termination type
2ffad2a4-bc50-48ab-9bee-77784e837a7a | checkpoint | Ensure cables are stripped no more than the specified distance
6e3a5eff-3a2e-4fb1-b49b-5ec158062560 | checkpoint | Check terminations at completion for colour code and sequence
d594dc94-3843-4361-9cf9-4bc1d019cac1 | checkpoint | Label outlets
78f0e962-06ac-47fa-8c7d-18669ea45b9e | checkpoint | Patch outlets to hardware devices where applicable and check for correct operation
c1b64272-031e-4954-b384-c42377eaecef | checkpoint | Complete certification if required
504aa7e0-a9b3-4fc7-a094-0ca72734fd21 | checklist | Exit & Emergency Testing checklist |  | Exit & Emergency Testing checklist
29c9c457-1572-4376-961e-30ec91cf5937 | checkpoint-no-value | Details entered below
8abcc5a7-efbc-54f7-820e-5f0ab551c425 | dropdown | Start time | 07:00AM, 07:30AM, 08:00AM, 08:30AM, 09:00AM, 09:30AM, 10:00AM, 10:30AM, 11:00AM, 11:30AM, 12:00PM, 12:30PM, 01:00PM, 01:30PM, 02:00PM, 02:30PM, 03:00PM, 03:30PM, 04:00PM, 04:30PM, 05:00PM, 05:30PM, 06:00PM, 06:30PM
9bb90884-517d-5e4a-ad9e-e7da8ecfe9b1 | dropdown | Lamp duration | 120 mins, 90 mins
a714b90f-013a-541a-b821-8e423bd69f58 | note | Starter switch
8cbc1d34-80ae-5c68-9011-4bc996e398e5 | note | Charge indicator
a5e8446b-eb49-5dd1-8f44-79d7ff468728 | note | Test switch
1d6eb3d8-34c9-5e9c-a818-260af52352fe | note | Circuit board
60af36bf-9dd6-537a-875c-d1c38b3a6d1c | note | Clean diffuser
95803977-b0e2-4bdb-a7f3-0256fec9aabc | checkpoint | Overall fitting
55e791a2-91eb-53cd-ac98-2db85c40f990 | note | Please add comments if additional action taken / other details
620ba6be-2e76-4d5d-90de-10b325d33a89 | checklist | zSYS - Add VAST Site Induction (old version) |  | VAST Site Induction
78797650-19f0-43cf-b4a3-feda22bbf131 | checkpoint | VAST Employee
ef74e485-6a60-587c-91bb-5c8969fbfee1 | textbox | Name
9cbdae28-8873-55e4-9b48-f613b92b6948 | textbox | Contact Number
c03f7700-3d89-55e2-b36d-44cfa4924019 | textbox | Date of Induction
4179b79a-f4cc-5d6b-9621-779e9451d4f1 | note | Tick if the following are understood:
a6603cb7-de4a-586c-9840-9cf936e5b258 | tickbox | How to report to the site and who you report to
5acc0dbb-4977-5efc-98ea-d27c97c1c006 | tickbox | The working hours on site
e0061ff0-a503-5afd-983b-501d8f1ef83f | tickbox | Who the managers and supervisors are on site
cf3a09cf-eea8-58da-a6d4-f326f6558737 | tickbox | The correct minimum PPE for site
7b62aa78-7329-5b55-88b1-d44d71815d9a | tickbox | How safety is communicated on site
767aa5a5-529c-5d09-9dd8-a051bd3aaa4b | tickbox | Where to have lunch and where the toilets are
1db68ef8-8ff9-50ac-b619-e11d48926d2e | tickbox | Where the First Aid Kit is kept and who is the First Aider
cc3bab0d-d53d-5e5c-b894-4aaa905e69cc | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
22bb7ed0-419f-5e7c-be65-47c5cf1c4693 | tickbox | What the high risk activities and hazards are on site
6efbf997-d08c-524e-8859-4dfecb9151f5 | tickbox | How to report WHS & Environmental hazards & issues
0a541d72-e908-5493-bec7-1ac8b689323f | tickbox | How to report a safety or environmental accident or incident
1cd4a1bd-c92c-5ac6-bda2-7212900a7b7f | tickbox | Housekeeping responsibilities
49b26424-df06-4d35-8341-fe9f3b34475b | checkpoint | EWP Licence - Please take a photo
a49ed8ba-8d46-46b3-8d01-d25d2af6e863 | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
11efe7be-16b2-4617-8803-44a8f3257358 | checkpoint | VAST Employee Signature
9ffdb14a-d6de-458c-919b-41344d26fd18 | checkpoint | VAST Supervisor Signature
ad5d0519-ce8d-4bf9-8825-621a934990f0 | checklist | ITR No. 08 Hallway – Commissioning Electrical & Permanent Power |  | ITR No.8 Hallway – Commissioning Electrical & Permanent Power
5f7aad87-c19c-41cc-81f2-d6838a466bf0 | checkpoint | Energisation permit completed prior to energisation
97f811b1-8e8f-4843-86b2-2313eb59f805 | checkpoint | Visual Check (against most current plan)
cd3893c7-108f-4b8a-b4a3-03918b4cdffe | checkpoint | Dead Testing
b6f6c237-1622-4da6-86dd-482b3f1d1493 | checkpoint | Live Testing
188a68be-3a36-5272-9aa4-24e7749cc5c9 | textbox | Record Metrel Results
e44b8a11-7e8b-4927-877b-f1a5ed53972e | checkpoint | Check operation of all sensors (individually on minimum time setting )
e0b2b443-bd26-4ca4-876b-e720d2264105 | checkpoint | Check sensors are set to specified time and lux
bcb7a16a-b67e-44d6-a0c3-45ce6206ae78 | checkpoint | Check operation of all EX/EMG, perform 120 min test ( initial )
4830e798-9894-41f8-92db-1b9df84d15f7 | checkpoint | Fit cover plates to all GPOs & exit signs
5330ff0f-9c5c-49f5-a451-a563ec0187fa | checkpoint | Ensure area is left clean
51696e7c-68f2-42fa-8e56-6b02127c66bc | checklist | ITP No. 12 Install DB's - Terminate Sub Main Cables |  | ITP. No 12 Install DB's - Terminate Sub Main Cables
6474acb6-ef3f-41a3-afa8-9a27eaa70d14 | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
dc0db123-0f30-41df-bad9-f0e017699d48 | checkpoint-no-value | Drawing Rev No.
9098cbdf-962b-5e25-89c6-b88f56fef674 | textbox | Drawing Rev No.
b3371122-e41c-4261-afec-1f92256f1fb6 | checkpoint | Locate & fix into position
1ab18953-87dd-4821-b5aa-0c8efb2d345a | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
4ceb3aa3-55d4-4d50-a566-8273916eab32 | checkpoint | Install lugs and terminate
8da70f7d-c29b-5b2e-a9e4-202fd03974a0 | note | Any cables not terminated prior to energisation must be removed from the cubicle at origin and have ends covered in heatshrink
654cef54-d8a8-59e7-956f-91100264854d | note | At destination cables must be covered in heat shrink and be contained in a junction box
1de66e1b-6a26-4bd8-a098-580f5ab1f5b0 | checklist | ITP No. 10 Comms: Data Jack Termination |  | ITP No. 10 Comms: Data Jack Termination
02d0f776-e28a-4ed7-b3a9-f6460e529268 | checkpoint | Visual check ensuring cable to be fitted off in correct position
193b1493-ce90-502c-81f5-eaf8a9f89b69 | note | Selection of correct tool to be used for termination type
a5080e27-b7db-46e6-9aef-0484322f499b | checkpoint | Ensure cables are stripped no more than the specified distance
3b6da24a-3c8e-500b-98f8-c1d56f0781c1 | note | Check terminations at completion for colour code and sequence
68053fa1-4b0c-45b1-974a-6eb6309ad3d6 | checkpoint | Put stuffer cap onto jack
20a7b812-301f-4782-881e-26f3497a1de0 | checkpoint | Attach wrap around label to cable no more than 60mm from the jack. Ensuring correct number sequence
ac6fcf31-7418-4141-b857-c21d24f1e621 | checkpoint | Install jack into workstation or wall outlet
1708e288-ca26-41a6-b18b-98c6c246fcfe | checkpoint | Label outlet ensuring correct number sequence
144b06d4-e496-46dd-b7b2-0548ffce70ab | checklist | zSYS - Toolbox Meeting |  | Toolbox Meeting
c35130b3-ada3-4374-bdf7-1f55527e9682 | checkpoint | VAST toolbox meeting completed
63b1bc2f-b2c6-5f9f-85b0-d9be5fe0d10f | textbox | Supervisor
49371db3-49a1-5fc9-bd9c-69d6c828d45b | textbox | Persons present
edf9ec6c-d8a7-51d5-bcb7-9d26d271643f | tickbox | Injuries, near misses and incidents
12355a90-5ef8-5a3d-b111-5ada48b4d141 | tickbox | Management of major hazards
b0282e9a-d78f-5258-abfe-2c804b60938c | tickbox | Compliance with our Vast SWMS
591f07d7-d2c3-5a19-9f22-ec6f4e80ef18 | tickbox | Safety
26d38d4f-b3f4-532a-a3d2-8284d19055bc | tickbox | House Keeping
6abb5fe9-d1c5-5ade-8083-8675caeb600f | tickbox | PPE (HARD HATS & GLASSES ON AT ALL TIMES)
c4e1127c-e005-5711-9ffc-c9e600081598 | textbox | Comments
c636586b-56f6-4f89-93e6-b6553997a105 | checklist | ITR No. 05 Hallway Rough In |  | ITR No.0 5 Hallway Rough In
ee09223d-59f4-42f7-a1fc-0516bda54fd2 | checkpoint | Area clear, tidy and accessible
309da757-6081-40f2-b9f1-c6cd6ced24d2 | checkpoint-no-value | Drawing Rev No.
26762b3e-2c8f-54d4-ab64-8e609f655f5b | textbox | Drawing Rev No.
645c7dfc-a32e-4e7b-8cb5-84901f8e9e67 | checkpoint | Mark out all public L+P in hallway
41c4e9ef-4623-4791-95bd-2265770a6453 | checkpoint | Rough in lighting, Emg/Exits and sensors
73a48591-db91-472a-b1d2-b1a2bd1b6a7a | checkpoint | Rough in cleaners power, water meter power, window louver (CS) if applicable
d52b4524-6d63-4af3-8bd8-0130795e34ab | checkpoint | Rough in comms riser power
c8619ecd-e57d-4105-802b-5d1867d0fdf8 | checkpoint | Rough in lighting feed to first lighting point near elec riser
f45c477f-fd67-4289-886b-87c8bc0f619c | checkpoint | Rough in power feed to first cleaners point near elec riser
a53564ae-a1b5-4b4f-ada9-5b0d25b9b2c6 | checkpoint | String all comms conduits
28ecbc50-6b77-453c-85a3-b91874a495c2 | checkpoint | Rough in all apartment sub mains from riser to apartment DBs and LABEL
ba472013-b644-40c6-a8af-3b13fd092b21 | checkpoint | Rough in stair doors access control
281314a7-ea99-44a3-980c-307cc1fd8002 | checkpoint | Rough in any relevant comms/access control from one floor to another ( Backbone )
94e15d95-4f6e-4b57-b35f-f487054560e1 | checkpoint | Check for clashes with other services
10f319dc-478a-4ad0-9f20-047115c2655f | checkpoint | Fire caulk riser cupboard door headers ( smoke seal only )
55814cd7-c479-4dc3-828c-ac7d0fdde817 | checkpoint | Fire caulk apartment door headers
2229ef90-f680-4412-a5d4-b206d617adde | checkpoint | Ensure area is left clean
429e1490-8f9a-4b01-a394-55b4ac721fe7 | checklist | ITP No. 17 Construction Wiring Installation, Test & Inspection and Removal |  | ITP No. 17 Construction Wiring Installation, Test & Inspection and Removal
4409a74c-ba69-41af-9734-75820277a22c | checkpoint | Area accessible & ready
13434c82-7f0b-5be2-9bba-1d71c9100ed3 | note | Prepare single line diagram of proposed distribution system
93063a87-f48a-466b-bdcf-a26ab9ca0b88 | checkpoint | Request power distribution to conduct fault discrimination study to verify correct functionality.
09fcd871-d6c8-481d-a407-fa6f3587ffd7 | checkpoint | Adjust circuit breaker sizes if required
c156ce92-e73d-4a6b-896f-4e7944753fd3 | checkpoint | Position and fix switchboard
1173e092-832f-4975-a6d8-95624952e0a1 | checkpoint | Cabling must be supported and protected from damage. construction wiring tape must be fitted at every 5 metres.
51147331-78e3-4aed-bdb8-27fd7d9cd7a1 | checkpoint | Terminate sub circuits and Sub Mains
5439df64-5ccb-4707-abe1-493cf40859f3 | checkpoint | Test & commission
8a8705c1-dbb5-5bd6-b4ba-6b752fdefefd | note | Lodge prescribed/non prescribed (as applicable) certificate of electrical safety. organise inspector (if required).
e5b6c9b7-6530-43ca-a7e2-19f48e50dfa2 | checkpoint | Earth leakage circuit breakers are to be used for circuit protection lights and sheds, 30 ma maximum outlets 30ma maximum
c8a65080-33aa-4c58-bb80-b7f35ec4d124 | checkpoint | Elcb’s must be fully tested initially and then tested every month with results recorded and c/b’s tagged
ac09b392-d20e-49e5-b436-32521501b4e9 | checklist | ITP No. 06 Soft Wiring |  | ITP No. 06 Soft Wiring
704fa199-53b3-41ea-bbab-8e3a7ed0ddcb | checkpoint | Delivery check for damage
271c5a6e-1f7e-44e8-8979-a7155d32f263 | checkpoint | Install hard wiring termination point
a407acdc-4994-4fa5-9b93-3f17091c3456 | checkpoint | Terminate cable at termination box
0039a6e9-da63-4a2f-b5d9-3b91b0c3630d | checkpoint | Loop flexible lead from termination box to light switch, sensor or outlet as required
c2bca54e-33d1-47e7-8eed-0878dc8c9fae | checkpoint | Test and commission
8357bc08-7a93-42fc-8363-27db83d5107b | checklist | Exit & Emergency Testing checklist V2 |  | Exit & Emergency Testing checklist V2
7c4721cc-8085-4877-b328-026e44751adb | checkpoint-no-value | Details entered below
b2b44129-dc61-5316-b2b8-dc148015882f | dropdown | Start time | 07:00AM, 07:30AM, 08:00AM, 08:30AM, 09:00AM, 09:30AM, 10:00AM, 10:30AM, 11:00AM, 11:30AM, 12:00PM, 12:30PM, 01:00PM, 01:30PM, 02:00PM, 02:30PM, 03:00PM, 03:30PM, 04:00PM, 04:30PM, 05:00PM, 05:30PM, 06:00PM, 06:30PM
f9d3f7cd-5143-5388-9e11-b2d6fe86e8fb | dropdown | Lamp duration | 120 mins, 90 mins
7cbbb13c-dea9-5135-bd54-824606b4dd22 | tickbox | Starter switch
74169403-30f6-51ea-a9ec-550b68e0b3d4 | tickbox | Charge indicator
342c7048-55d0-5c65-a077-86c7e221d820 | tickbox | Test switch
eed44d7b-a3c2-5e1a-b50d-33cf330aabe9 | tickbox | Circuit board
c3726a26-db59-51e7-a491-c7d77dc86e56 | tickbox | Clean diffuser
29ada6a1-7711-4d4c-a15e-3f1a1c76f48f | checkpoint | Overall fitting
6ed39e09-35f7-58b8-b800-a7f3ed88c642 | note | Please add comments if additional action taken / other details
e505717a-25ea-4a3f-adb6-feba9e65f6b1 | checklist | Apprentice Contract of employment |  | Apprentice Contract of employment
e7732d71-6869-4b0e-a903-185684fbe6d0 | checkpoint | Attach Document
9f5bb4f2-b534-41a5-959b-c8e6b1df5dd0 | checklist | Preventative Maintenance Checklist |  | Preventative Maintenance Checklist
e1b8eb24-22a6-4ff1-a530-cd343cdf51ac | checkpoint | Visual Inspection of Electrical Installation
8d90ab72-6272-5e16-bd16-689f807a6e0b | note | Lights are operational
f3ea1f35-1fd8-5042-8b60-13afdd7a0908 | note | Light fittings correctly installed and not hanging down
9f3b9727-71ea-5a43-86dd-68b7e167b930 | note | Switches and Power outlets securely fixed and cover plates not missing
cd394615-f34b-5068-a477-88423dc29055 | note | Switchboards not missing pole fillers
537c3bc3-c423-5fff-bb4f-dd7a0553106b | note | Any surface conduit or tray work is securely fixed
ca15487d-ff72-5f88-9e36-32355bd22b46 | note | Diffusers, fittings, switchboard cupboards free from obvious debris
71835161-2cf2-438e-91b7-b005b4c4736f | checkpoint | Exit & Emergency Lighting Testing Carried Out & Logbook Completed
fc671b03-29c5-4960-9e4c-5fd83ab1db84 | checkpoint | Operation of Switchboards Checked
d34d33bd-c590-5816-84c0-6322624e5131 | note | Performed at 12 months only unless otherwise advised by Builder
7f1fcb07-f9bf-4c1c-8522-47e7d0c2d312 | checkpoint | Operation of Lighting Control Checked
5c8584e2-f6ed-48db-a9d6-24862c706076 | checkpoint | Check & Replace Fault Lamps
de2eb51a-94a0-46d5-83f7-ef18fb56ae9f | checkpoint | Fire Detection System Test carried Out
613bd411-54dc-47c3-86f7-bff63d8c60b5 | checkpoint | Fire Detection System Test Results Issued
b45c4fd6-0e18-47d0-8a6a-19ad27a072ef | checkpoint | Switchboard Thermal Imaging Test Carried Out & Report Completed
fdd04c4c-7145-5650-9e30-f331df1e5d0d | note | Performed at 12 months
1f8bef0c-664a-48c8-8370-e2e058f14a0f | checkpoint | Solar
bc9c9e8a-b936-4103-990a-9eb145da61f5 | checkpoint | UPS
40b5c8ba-8d32-4c8d-8970-01c512f93ede | checkpoint | Data & Communications
f0ba16b4-d079-4ccc-b136-4df460931e48 | checklist | ITP No. 13 Commissioning of DB's |  | ITP. No 13 Commissioning of DB's
f4e69526-d7ab-414c-b141-ac65128e8f9e | checkpoint | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
3b00e467-8738-5fdc-b6b7-c0560bfef13d | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
7e89bbb9-77b6-5809-bad0-9b4a4fd041a9 | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
c3667d10-83f5-5591-a785-8e170e016a49 | note | Collect material from office and have correct db structure downloaded.
00759227-aa49-4821-8796-e46d9d8a3fc1 | checkpoint | Commence commissioning
8f4dae53-9b75-4ebb-bd6e-f7abeca2d093 | checklist | ITP No. 02 Rough In Sub Circuting Cabling |  | ITP. No 02 Rough In Sub Circuting Cabling
35785279-8b3f-44a3-8a80-edbe9162a193 | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
ecac6e40-2f80-4f20-92ff-b1d331c15f6d | checkpoint-no-value | Drawing Rev No.
006fdcff-9a53-5dc7-ac54-2aa52c203c13 | textbox | Drawing Rev No.
9fe04e58-0b70-5f12-88ce-79272569e884 | note | Determine cable size as per itp 30 selection of cables for subcircuit wiring etc
8bc227d5-f75d-5284-9dd1-d56c273b40fe | textbox | Cable size / max length
c30f8d92-4ff7-5c64-b876-0df8ae19413f | note | Determine cable support system ie. catinary, cable tray, fix to structure, ducting
f03e7280-87d1-41da-8c90-84f8304b767c | checkpoint | Install cable support system
183066a5-99eb-4948-b75f-19c5a62fc87e | checkpoint | Check cable size/type
7c9af774-15dd-587d-a425-915d96b77a11 | note | Black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
64f5fa5b-2c7f-4900-a0f9-99549b86b18a | checkpoint | Install and identify cables
fc646844-a6d8-5a90-a3d9-43b4e5015bc8 | note | Any cable not terminated immediately must have the ends taped covering the bare copper
f3a82761-856b-423e-8472-63fad255f875 | checkpoint | Fix cables to support system
8751adde-6b09-4098-b926-64ead8ccd277 | checkpoint | Fit-off outlets, plug bases etc. (if necessary)
512d571a-4604-52a3-9344-24d9790b4a1a | note | Each circuit to be fitted off completely & clean up area
ec1ffdc7-0630-4232-a140-f3e7c4eb1a26 | checklist | ITP No. 18 Light Fitting Installation |  | ITP. No 18 Light Fitting Installation
34db5686-f2b8-4de9-a2c9-27c56ed525f2 | checkpoint | Delivery check for damage and correct quantities
cf0fc51c-2996-4c0f-8a7e-1abd92dbcf87 | checkpoint | Locations coordinate with other services
f6ad06cc-0bec-5eaf-92f5-c353e16483b9 | note | Marking out if required - refer to reflected ceiling plan for set out
999627b2-7909-4a3b-8916-a4615d5d9abe | checkpoint-no-value | Drawing Rev No.
53a1d37a-4328-5275-8993-2c7919dd005a | textbox | Drawing Rev No.
a58a2dcf-28f7-48be-8456-de436816c1da | checkpoint | Plug in or fit off light / plug base
f05db11a-7418-4f7b-8ec5-0ac69a8320fe | checkpoint | Install light fitting
aca4daa4-6636-45d4-bbfe-5d2c43be617f | checkpoint | Install lamps and diffuser
bd8d3b01-7555-4d9b-8215-e975db4d6da7 | checkpoint | Clean fitting, lamp diffuser
7085805e-42f9-4474-a336-773714ef10a4 | checklist | Drawings / Documents |  | Drawings / Documents
571c2731-68da-4b3a-8f3c-1b8846d05b5c | checkpoint | Attach Drawings / Document
1d0607f6-e23d-4dbb-a6d7-39b78fae82fb | checklist | ITR No. 07 Hallway - Fit Off Electrical (High Level & Walls) |  | ITR No.7 Hallway - Fit Off Electrical (High Level & Walls)
3417a6fd-5260-4392-bd0d-cb550c293532 | checkpoint | Area clear, tidy and accessible
ecd66f75-3f57-4eef-82fc-8f45f9b9051f | checkpoint-no-value | Drawing Rev No.
ab98b686-3bd7-5e3b-901c-a66d3c95a867 | textbox | Drawing Rev No.
2d697abe-5a87-4e3c-b7b0-8de1725ddde4 | checkpoint | Fit off all Lights
641caac3-3401-4b45-bd12-71d14107d61d | checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
0422e5bc-851a-4cd9-905c-f0310cf6a13f | checkpoint | Fit off all EX/EMG’s
cad330e8-3679-4fea-8d55-a5d0e25b2b4c | checkpoint | Label all EX/EMG’s as per plan number
b5db37e0-8f66-4882-aa4a-99f036ae291b | checkpoint | Fit off all Cleaners GPO’s
db2cecbf-ce2a-4dd8-afc8-a2f92d2119d5 | checkpoint | Fit off all Comms Riser GPO’s
e53d1b49-ad82-4506-b51a-c53cdcf1b118 | checkpoint | Ensure area is left clean
ec3690c4-db79-49dc-a2b3-8734a59fe0fe | checklist | ITP No. 19 Copper Data & Voice Testing |  | ITP No. 19 Copper Data & Voice Testing
fa9eda02-3dc4-461d-b546-d379ec942a2c | checkpoint | Area accessible & ready
fe52c65b-8d1c-4e80-9a15-9e65adcd6a42 | checklist | ITP No. 22 Bakelite & Power Installation |  | ITP. No 22 Bakelite & Power Installation
e4929978-a1cc-4202-83c6-437e50ee7ac0 | checkpoint | Check drawings for quantity, brand type and colour location/compliance wet areas, hazards etc. mounting heights
dd9a0482-6b10-4f37-98b3-1368458357d7 | checkpoint-no-value | Drawing Rev No.
754e0e84-4058-52cc-9034-b74457451d2b | textbox | Drawing Rev No.
5d5a5723-f226-45b9-9211-935048952724 | checkpoint | Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch
754e0e84-4058-52cc-9034-b74457451d2b | note | Each circuit must be fitted off completely
1f4f04f7-9247-4094-9a91-a6ad09d0156e | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use shroud
7a925405-60f3-5315-99fb-ed1c49650686 | note | Each circuit must be fitted off completely
536c8cdc-e5c7-4493-8c13-d4b0c46cfa99 | checkpoint | Fit off final appliances
98a06d06-5915-5f63-a064-2a5e51af0a6f | button | Cover plates (if required) | Yes, No, N/A
34e5bad3-e62b-55cf-837a-9f205bb720db | button | Install label (if a specified requirement) | Yes, No, N/A
811c840b-78a8-4329-8918-cee6eb680702 | checklist | zSYS - Toolbox Meeting Checklist |  | Toolbox Meeting
8b4ceea1-7963-432f-adce-fb01d475faae | checkpoint | Details
717e797c-ec3e-5270-8c89-047a545f89c4 | textbox | Supervisor
084abdf9-7275-5cc8-872d-b71cc0f02072 | tickbox | David Interligi
16ad7117-78c2-5ff5-9e03-b6e523e6e623 | tickbox | Michael Borg
ad5b68a6-7896-5504-9a18-fe75f69179aa | tickbox | Rob Pellegrino
3840916b-b875-5b7b-823d-04efed1533d8 | tickbox | Adrian Sibbing
4ed1757c-7afc-5c7a-a8f5-319da8879243 | tickbox | John Wolosz
b3428edf-69b6-5913-9655-7e6d6407aabe | tickbox | Lochy Brannelly
c66ef8b4-a66e-5fd3-8dc1-7bc768aadc6f | tickbox | Damon Guy
2ae9425c-e118-5e77-bece-56820172cbd7 | tickbox | Jake Condon
b3c31838-fab1-5909-8022-9a940c4e81e3 | tickbox | Julian Cannata
8df36e14-bf39-5b66-b708-1c0174149986 | tickbox | Devilliers Duvenage
2b9c1296-314e-5c94-b12b-825814849440 | tickbox | David Currie
29aa1daf-bc6a-5993-8725-0306b3b893e9 | tickbox | Steve Price
a0748d01-1664-590d-a1f3-a4afde9b158b | textbox | Actions from last meeting:
a06b5651-2e24-55dc-997a-092e7aefa51b | textbox | Injuries, Near Misses and Incidents since last meeting:
0910a513-4810-5d56-98aa-b2b8ea4cc394 | textbox | Management of major Hazards and High Risk Activities:
683b8ba0-c0ed-52ed-94ad-adfd5580745e | textbox | Compliance with SWMS & Risk Assessment Booklets or Forms:
1eecf130-63d3-5614-909f-1e3dfa11c741 | textbox | Reviews of any Safety Forms, SWMS, Policies, etc
c67c4405-3916-567b-bf59-cd655c224d47 | textbox | Comments/issues from the floor:
b363e52f-2861-4952-b0a4-7b7f4d42d8b3 | checkpoint | Signed off by Supervisor
a9242d9b-0578-5ce5-9cd2-0532e1de907a | textbox | Corrective actions
7cce01ba-08e9-46b7-a0ab-dff71413ed57 | checklist | zSYS - VAST Site Induction |  | VAST Site Induction
f37e2b03-a5ca-42d5-8dc0-216bc3399dc0 | checkpoint | VAST Employee
e001aba4-7d8e-5638-b09f-36a6ab5c1e2a | textbox | Name
fda3113f-4e4a-57e5-bc72-33ae17bbb780 | textbox | Contact Number
04ca305f-26f2-5191-8074-295cbf85cc88 | textbox | Date of Induction
12841d34-6b99-5a84-8928-4eeb0c7dfabf | note | Tick if the following are understood:
bee90432-7150-5cdb-8c35-782536e9e065 | tickbox | How to report to the site and who you report to
ad88561d-16a3-5089-bad8-591bc956a4ea | tickbox | The working hours on site
f2c37a1a-9b22-5c0b-a965-f405a5886200 | tickbox | Who the managers and supervisors are on site
3cc0d559-232f-50fb-b911-e4a32f61fd74 | tickbox | The correct minimum PPE for site
73efbd53-e540-5575-b344-e6f4b02122af | tickbox | How safety is communicated on site
8737230f-1428-5ae9-a49d-f663f25faee6 | tickbox | Where to have lunch and where the toilets are
6b90f2fc-d229-5cde-baa8-3f90a5cbb4a7 | tickbox | Where the First Aid Kit is kept and who is the First Aider
d1e59acd-4173-533e-ac3d-920000204a9f | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
552f82e3-54a5-5b02-9a16-9bb2aac54c57 | tickbox | What the high risk activities and hazards are on site
885d2490-8994-5df9-9a69-76fca2671d14 | tickbox | How to report WHS & Environmental hazards & issues
6ac47ca0-b962-570c-867f-9703ca95dd54 | tickbox | How to report a safety or environmental accident or incident
1c39aa80-6829-5deb-bfcf-6120043181fe | tickbox | Housekeeping responsibilities
f34af980-b34a-419c-9df7-6608754b1084 | checkpoint | EWP Licence - Please take a photo
d57dfccf-f777-4de2-8e35-1f26d72839ea | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
ecac10de-4cf3-431d-9796-3e45269c1293 | checkpoint | VAST Employee Signature
ad9a2e21-0148-41e5-a4f5-bd500271acd3 | checkpoint | VAST Supervisor Signature
0f62d89e-57a0-4260-831a-65fe04aeeb47 | checklist | Toolbox Meeting |  | Toolbox Meeting
decd8a96-685e-4f28-8e50-47e2bd93d09d | checkpoint | Details
acd446e9-425e-519b-992d-37c653e93b3a | textbox | Location
584c8b07-1952-52fb-96b1-d33f22ebebe2 | textbox | Supervisor
f2df7993-08bd-55a7-b963-f6a24029d7ac | textbox | Date
86bf3f4c-4b87-5460-95df-79f833b3d475 | textbox | Time
aada1ba2-e42e-522a-ae83-93188c9d606e | textbox | Persons present
2edb7a82-9792-5c51-b090-590b130131a1 | note | Topics discussed
8620ec71-f1d1-5bde-a218-01579e56052b | tickbox | - Injuries, near misses and incidents
dcd8d09c-2b0c-5491-af13-836000890d20 | tickbox | - Management of major hazards
eb62f661-8372-533c-a886-19ced59e43bd | tickbox | - Compliance with our Vast SWMS
109aba20-cfdb-59df-8651-ead89987567b | tickbox | - Safety - E.g., Apply LOTO processes when applicable. When Megger testing ensure that no person is working at the other end of cable being tested.
f3c0de5c-d953-5538-b42c-851b5412762b | tickbox | - Housekeeping
a8f4766f-f8aa-5b17-80ae-f20aa19b7cdc | textbox | Comments from the floor
b377adb1-f1ad-48f3-be8c-121139fc5603 | checklist | ITR No. 12 Switchboard Commissioning |  | ITR. 12 Switchboard Commissioning
0416db91-f1ea-4711-b15a-1799cee5307e | checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensure compliance With This Procedure
9fe60678-49da-4648-b1a2-ed560d2b0b5c | checkpoint | Place all required signage and barricading and have LV rescue kit on standby.
9cefc730-0bc8-4d13-83b1-4014520b991c | checkpoint | Refer To As Installed Drawings
a47b52f2-f6ee-4b00-a1b1-974368014b6e | checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
5f6c10d4-8cd9-4ca7-ab95-702025f85c0e | checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioing
f37194c5-5b42-4506-a773-ac56736bc027 | checkpoint | Complete Visual Checks
8ef5fa65-e4d6-4b32-8300-8167c9d83012 | checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
9c09c495-2512-4fe5-86a1-191696078591 | checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
cae2885e-c680-4199-bcc3-d34a1d537547 | checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
a6fb945b-9361-4b9d-8fac-878b27e007aa | checkpoint | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
dac25eb5-8424-41fe-9617-9d79c547c6d3 | checkpoint | Ensure Vast Witness Test Has Been Completed
bf43c5b9-3c4e-467d-a3d1-630aede1c03f | checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
e0fb19a0-42fc-410c-b31c-8a7c04a79f60 | checkpoint | Ensure No Access To Live Parts
d0987c4e-7b93-4b0a-80a4-e766728258e4 | checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
6434ccb7-26d3-441c-989b-5a5642e30b7c | checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
344f8e3e-f91f-45b4-8dc0-c777dac38ade | checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder
d0df8d09-88fd-4f3b-b2f4-bd4ba7b67725 | checkpoint | Take photo's of all Switchboard internals without escutcheon
b394fd5f-e9b6-423f-821d-cef7cde18096 | checklist | ITP No. 11 Data & Patch Panel Termination |  | ITP. No 11 Data & Patch Panel Termination
304c01bc-55a3-4d18-b619-c4b97b0a8a19 | checkpoint | Visual check ensuring cable to be fitted off in correct position
66d643cd-5d79-5315-be93-f2080e5e9a57 | note | Selection of correct tool to be used for termination type
ccf91404-b865-4244-a460-699ff9be71c0 | checkpoint | Install patch panel into cabinet loom cables to the back of the patch panel
24bb835a-d9dd-540e-a1a2-365b1b184833 | note | Tie into position using velcro strip and/or cable ties supplied
76728025-9a09-45ff-a203-553cb72b779d | checkpoint | Ensure cables are stripped no more than the specified distance
385768cc-2230-5b13-8ced-69c52d92c763 | note | Check terminations at completion for colour code and sequence
3337042e-01c1-4099-9ef1-a67c71778906 | checklist | ITP No. 18 Light Fitting Installation |  | ITP No. 18 Light Fitting Installation
50456aef-857a-40bd-9ddc-bc9be28b2d68 | checkpoint | Area accessible & ready
0fe2a060-c475-4f77-9b6e-c63c4cb7a6d6 | checkpoint-no-value | Drawing Rev No.
ca073d91-c1c9-5986-a93e-3b71200e9a52 | textbox | Drawing Rev No.
eb333df5-7ebd-4f02-bc9d-90337268e9a8 | checkpoint | Delivery check for damage and correct quantities
7ede8471-07fa-4617-98c0-277ee868aa74 | checkpoint | Locations coordinate with other services
87507f30-79d5-58fa-9ec6-e7e9a3ee56b0 | note | Marking out if required - refer to reflected ceiling plan for set out
513f52e6-6a61-454a-8fd5-fa5afdd7b202 | checkpoint | Plug in or fit off light / plug base
94ccf444-f08e-41da-bebc-23f71c651054 | checkpoint | Install light fitting
75ae8c4d-a86b-4fca-b6db-8ef71a07bcc0 | checkpoint | Install lamps and diffuser
3b9c390a-79d8-4763-af01-50f1ee5c4762 | checkpoint | Clean fitting, lamp diffuser
c65fe2cf-5c01-43c8-a89b-546657035424 | checklist | ITR No. 04 Commission Electrical & Permanent Power |  | ITR. No 4 Commission Electrical & Permanent Power
11440775-4912-4ab8-b7b1-77cc2715d1ab | checkpoint | Energisation permit completed prior to energisation
e919948c-f1a8-5b84-a1c8-8843fbe69266 | note | Visual Check all items
f7aa73b9-8214-4c22-9186-39063a7eacdf | checkpoint | Dead Testing
aceb2b37-20a5-444a-9cff-62b4b99dd60e | checkpoint | Live Test
8379ea70-198f-5b02-b52d-9e43c0246050 | textbox | Record Metrel Results and log
1d4914a2-94b1-4002-95d9-ce106ec8e86f | checkpoint | Test 4 pin plug base for switching
24915b19-b370-4919-ba5a-5313b3ffb96b | checkpoint | Check light switches for correct switching functions
9bbc4719-cf38-4cc5-b3da-b6ae62de7493 | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
736a4a6b-1e3f-46d9-a0c1-857db9f52fd3 | checkpoint | Install switchboard cover / label (take photos)
79bdf925-1250-4653-82bb-a0914a796eef | checkpoint | Remove battery tabs on smoke detectors ( after MFB certification )
7411ed54-44d0-429f-9e3f-32d8b08dc072 | checkpoint | Ensure area is left clean
243a9ec3-350a-47c1-8e79-9249ba5b3fdf | checklist | ITP No. 07 Comms: Backbone Cabling Installation, Termination & Testing |  | ITP No. 07 Comms: Backbone Cabling Installation, Termination & Testing
fbce480b-5a69-42b9-a3a6-4cbf9fadd4ca | checkpoint | Obtain the most recent drawings and specifications
01c9afe4-2287-457d-8e89-5e1a531a719a | checkpoint | Install cable support or conduit where required
d464904a-18a3-443e-97a6-888308bdd45b | checkpoint | Dress cables to final location, ensure velcro straps for cat 6 cabling
a7faf4f4-0d5f-4f63-a593-a61a373da058 | checkpoint | Terminate cabling ensuring correct colour code
19e63e99-5d4f-5ce6-9738-56df49c2271f | note | Ensure correct termination tool used as per vendor recommendation
1646b3a7-0bc2-438a-b3fa-4fcbb5d0df87 | checkpoint | Test terminations using wizard tester for krone block terminations and mod tap tester for patch panel terminations
1fcc9e62-ee66-5b67-b641-83f8d6886056 | textbox | Device number
9a175e11-acb7-5499-9a92-ca4355e1c085 | textbox | Record results
d7a3459c-de88-4234-94a2-0311632440ca | checkpoint | Complete telecommunications cabling advice form and attachment if required
2e20096d-42f5-458d-8011-6705abd4f1d9 | checklist | Exit & Emergency Testing checklist V3 |  | Exit & Emergency Testing checklist V3
0da3ff6c-4c05-43da-be8a-1e06d5adcf2d | checkpoint-no-value | Details entered below
74881d6d-9fea-5766-8f3a-64175340184f | dropdown | Start time | 07:00AM, 07:30AM, 08:00AM, 08:30AM, 09:00AM, 09:30AM, 10:00AM, 10:30AM, 11:00AM, 11:30AM, 12:00PM, 12:30PM, 01:00PM, 01:30PM, 02:00PM, 02:30PM, 03:00PM, 03:30PM, 04:00PM, 04:30PM, 05:00PM, 05:30PM, 06:00PM, 06:30PM
a01cfa72-3f70-5abd-9c73-ff5376a829c8 | dropdown | Lamp duration | 120 mins, 90 mins
3bbab6b3-1b7c-5b00-a4df-d7dc18a1136c | note | Starter switch
d17dc1ad-100b-5e10-b5b8-feb2ea5146ce | note | Charge indicator
5f41b39e-245f-5639-8c24-234d0a1620e8 | note | Test switch
67805fa6-468b-58f3-8926-b43093cfc98b | note | Circuit board
cbb1f9fe-5176-5b6d-9ad3-bf4116192215 | note | Clean diffuser
14bbf9a5-1332-481a-be6a-2dca5e8b497e | checkpoint | Overall fitting
218a66a2-056d-5795-a7d5-3340ad7ddb4f | note | Please add comments if additional action taken / other details
24deff79-877c-47ff-94ac-ef6e6f1b5425 | checklist | ITP No. 16 Terminate Sub Circuit Cabling |  | ITP No. 16 Terminate Sub Circuit Cabling
56d2a377-bef5-4582-a40e-3433088dd89c | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate
159dba9f-b291-53e9-a141-6d9015d30f72 | note | If circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end
3f3cb747-2c5a-4985-bfec-d7c97f709264 | checkpoint | Clean & vacuum
652332a1-e179-5691-afc7-f6fb417bbb0a | note | Record relevant information and any changes on db schedule. And return to administrator/office for commissioning team
5665f939-b89e-4567-a1c7-76a4b29db642 | checklist | ITR No. 02 Apartment Cut Out |  | ITR No. 02 Apartment Cut Out
d75e2cc0-e554-41c7-9e65-ab331c6c2fb4 | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
7350f815-8e22-4018-874f-7ce137a2775d | checkpoint-no-value | Drawing Rev No.
b5b50ffc-b16d-5f87-9cce-d7196f1364f0 | textbox | Drawing Rev No.
70bece3d-9c16-4c3b-9587-0fbc651d803f | checkpoint | Cut out for light fittings
050be8a1-e6e1-4562-9132-38f5dd4dc1d3 | checkpoint | Cut out smoke detectors
aa771f97-0ff4-4428-af71-3f6e892d29c5 | checkpoint | Cut out kitchen to kitchen plan
00238d24-cf37-46b2-a88f-3c387cf2e02e | checkpoint | Cut out switches & GPO’s
4f43ca77-dcbc-47e5-b328-3a38833cfe18 | checkpoint | Cut out Bathroom and Study Led Strips Fig 8
d862698c-1904-4788-ab8c-82a3599b9f67 | checkpoint | Ensure AC isolator is in correct position
f306f08e-75ec-4ee3-a42e-de2a5498b23a | checkpoint | Ensure Wall light is in correct position
1f9f112a-22d5-49eb-916d-96a444d8f35c | checkpoint | Ensure kitchen outlets are in correct position
a1e681ff-9225-44a4-9f4d-960f74a47cf3 | checkpoint | Locate all cables ( including Smoke Detectors & Pendants )
33660f39-897f-43f3-8efe-0a27e5db7ca3 | checkpoint | Install Fire Boxes and hit all 4 tabs in
90bb542e-6ea3-46fb-9f81-b9e2e89d916b | checkpoint | Fire caulk kitchen cables ( if applicable )
1887ebad-a57b-4bb5-9145-fbfb733e193e | checkpoint | Ensure area is left clean
3c645d25-6aa5-449f-9698-d098947be17d | checklist | ITR No. 01 Apartment Rough In of Electrical Services |  | ITR No.1 Apartment Rough In of Electrical Services
a206157c-775e-4da7-9def-bc3759952631 | checkpoint | Area clear, tidy and accessible
5cadb29b-7679-40cc-aef1-eb0c784b9194 | checkpoint-no-value | Drawing Rev No.
914cb580-50e8-5f90-9255-18c021bb9842 | textbox | Drawing Rev No.
80e64b0d-3302-44cf-83d3-3560dd3e2395 | checkpoint | Rough in Hard Actives to all switches
c7eedba4-8cc1-4ff4-845c-be8d88aa67e2 | checkpoint | Rough in of Switched Actives from switches to lights & Fit off Quick connects whilst on ladder
47a81b8a-85ba-4f0d-aab8-60ee0233db76 | checkpoint | Rough in GPOs
16d74f66-3e64-4c8b-b9aa-8a8a92b685bc | checkpoint | Rough in of all kitchen general power (including island bench) above bench, gas cooktop, fridge, microwave, rangehood & dishwasher
d9547bc9-e6e3-490d-9a09-4287898d3664 | checkpoint | Rough in A/C & Oven
db676e67-ce90-45c7-b123-3e416a030684 | checkpoint | Rough in single tail island bench Pendant to the nearest downlight
cc9866eb-b372-4b2a-a3de-a47e98dec2ff | checkpoint | Rough in a loop from Pendant to LED strip at rangehood
0a45a744-2394-4817-8159-e88d9e99cc54 | checkpoint | Rough in bathroom LED Fig 8 downight location and switch separately
f4d57431-837c-4638-8e6b-0296b37297b4 | checkpoint | Rough in LED fig 8 to study desk to nearest downlight
0eb7c5c3-9366-462b-ba43-bb9357e1a2d1 | checkpoint | Rough in all internal lights
11e0bb13-800e-4aa4-a5ed-91c3e50cf8f7 | checkpoint | Rough in Balcony wall light- If 2 lights, bring 2 switch wires back to switch
219a3c67-4152-4f3d-be9e-421b38709db4 | checkpoint | Rough in smoke detector and interconnect to other detectors.
ee11b574-4ab0-431c-9d0e-6d04bc7fc1c7 | checkpoint | Rough in bathroom fans off power circuit and HA loop at fan
f7fcbdc0-b1ba-4883-a33c-ed5f95c61ca3 | checkpoint | Rough in WM/DR and install SDI from dryer gpo to laundry switch
61ec9e8e-fcaa-48ed-8a6c-65a0ed1b4e26 | checkpoint | Rough in WP GPO to balcony if applicable
797bb3fd-3719-4c9f-969a-0e615aa15658 | checkpoint | Rough in intercom patch lead to LBNCO hub
09aeb5a1-deef-4770-a6ff-00f5e9db35da | checkpoint | Rough in tv points to LBNCO hub
a4278a67-83c5-4c87-ba85-571e7c58804e | checkpoint | Rough in data points to LBNCO hub
4f454e61-68ae-52ba-ac08-f4f9e5380274 | note | Ensure LBNCO draw string is in
8ba03f60-87ab-5ddc-99f7-693a4298a3cd | note | Ensure Sub Mains are at Switchboard Location
67b15e39-5c60-4013-a1d0-9cdb9c9f55e6 | checkpoint | Install switchboard & fit off
5f5e6f38-a2ff-5d33-8636-17bd3d314476 | button | Install 150mm stud protecting sub main and earth with nut & bolt | Yes, No, N/A
7d285a23-1d0d-5068-8bbf-d85ea696f08c | button | Install 2.5mm earth tags | Yes, No, N/A
2582625a-4cf7-53e1-9ee0-e4ba93967be3 | button | Fire caulk sub main into DB and all cable entries | Yes, No, N/A
b30e1a98-645c-5392-a059-b57fb25cb5de | button | Fit off 4 pin plug base | Yes, No, N/A
3d38d15d-582a-4e96-bae6-ce3b8e5d1dc5 | checkpoint | Ensure all Quick Connects are fit off
03370382-1e15-5196-90cc-35667210ea3b | button | Ensure all cables are neat, taped to studs and easily accessible for cut out | Yes, No, N/A
632d220e-669f-53a9-b7f1-a01e3340fa27 | button | Ensure all cables are clearly labelled at DB and at party walls | Yes, No, N/A
93efd2d8-e384-4ab6-a3b4-575c052a438f | checkpoint | Ensure area is left clean
8932aa9b-c907-4043-be68-5bb9ff077dc7 | checklist | ITP No. 03 Mains & Substation Installation |  | ITP. No 03 Mains & Substation Installation
4705fc2e-a8b0-4e5a-87ef-dfec580b61d6 | checkpoint | Measure cable runs with appropriate accurate measuring instrument (eg tape measure, wheel)
c56c27a6-1a16-4161-bb5f-e9920f4b4fb2 | checkpoint | Check cable sizes resistance of protective earth conductor - shall be low enough to permit passage of current necessary to operate protective device
96f32459-d6f6-433f-afbf-ada8ac7bc289 | checkpoint | Confirm length of cable if sub contract item & order
7bd5d7f5-fc89-589d-8593-16a00a4ff6b6 | textbox | Record length of cable
fed89742-f21c-4d0c-99b6-0ea463bbd9c4 | checkpoint | Install cable in applicable method (EG. Cable stands, electric winch, pulleys etc.) - ANY CABLE NOT TERMINATED IMMEDIATELY MUST HAVE THE ENDS TAPED COVERING THE BARE COPPER - please take a photo
0942badc-dcfd-44ae-9b5f-51ee8a9a3518 | checkpoint | Trefoil cables & tie cables to support system (ensure spacing)
4cfcfc64-5a39-4111-a4de-eeeabf56801f | checkpoint | Check requirements for cable identification & install