## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DB # | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000003 - Main Switchboards
section | PRE-REQUISITE WORKS
checkpoint | Confirm All Work Has Been Completed
section | INSTALLATION CHECKS
checkpoint | Completion of "Visual Inspection of Distribution Board" Check list
section | VISUAL INSPECTION
checkpoint | Complete Visual inspection immediately prior to testing
button | No damage | YES,NO
button | Sufficient supports | YES,NO
button | Correct labelling | YES,NO
section | INSULATION RESISTANCE
checkpoint | R-W
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
section | CIRCUIT BREAKER OPERATION
checkpoint | OPEN POSITION
label | Continuity Test – With breaker in open and closed position
checkpoint | CLOSED POSITION
label | Continuity Test – With breaker in open and closed position
section | CIRCUIT BREAKER SETTING CHECKS
checkpoint | Verify Breaker Settings are as per Distribution Board Shop drawings, Associated schematics & DB Schedules (Board Drawings to be attached to ITC)
section | CURRENT TRANSFORMER POLARITY CHECKS
checkpoint | Visual Inspection – Confirm CT Marking Indicators are as per manufacturer Install. Guidelines. Visual Inspection of all other wiring
section | CURRENT TRANSFORMER RATIO CHECK
checkpoint | Visual Inspection of CT Ratio. Record CT ratio and confirm it is as per the switchboard shop drawing
textbox | CT Ratio |  |  | Record actual CT ratio
textbox | Shop Drawing |  |  | Record CT ratio on Chadwick’s shop drawing
section | METER CALIBRATION CHECKS
checkpoint | Multimeter reading (V=Volts & A=Amps)
textbox | Red Phase |  |  | Record V & A
textbox | White Phase |  |  | Record V & A
textbox | Blue Phase |  |  | Record V & A
checkpoint | DB Meter reading (V=Volts & A=Amps)
textbox | Red Phase |  |  | Record V & A
textbox | White Phase |  |  | Record V & A
textbox | Blue Phase |  |  | Record V & A
holdpoint | BOJV Acceptance
checklist | DB # | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000004 - Distribution Boards
section | PRE-REQUISITE WORKS
checkpoint | Confirm All Work Has Been Completed
section | INSTALLATION CHECKS
checkpoint | Completion of "Visual Inspection of Distribution Board" Check list
section | VISUAL INSPECTION
checkpoint | Complete Visual inspection immediately prior to testing
button | No damage | YES,NO
button | Sufficient supports | YES,NO
button | Correct labelling | YES,NO
section | INSULATION RESISTANCE
checkpoint | R-W
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
section | CIRCUIT BREAKER OPERATION
checkpoint | OPEN POSITION
label | Continuity Test – With breaker in open and closed position
checkpoint | CLOSED POSITION
label | Continuity Test – With breaker in open and closed position
section | CIRCUIT BREAKER SETTING CHECKS
checkpoint | Verify Breaker Settings are as per Distribution Board Shop drawings, Associated schematics & DB Schedules (Board Drawings to be attached to ITC)
section | CURRENT TRANSFORMER POLARITY CHECKS
checkpoint | Visual Inspection – Confirm CT Marking Indicators are as per manufacturer Install. Guidelines. Visual Inspection of all other wiring
section | CURRENT TRANSFORMER RATIO CHECK
checkpoint | Visual Inspection of CT Ratio. Record CT ratio and confirm it is as per the switchboard shop drawing
textbox | CT Ratio |  |  | Record actual CT ratio
textbox | Shop Drawing |  |  | Record CT ratio on Chadwick’s shop drawing
section | METER CALIBRATION CHECKS
checkpoint | Multimeter reading (V=Volts & A=Amps)
textbox | Red Phase |  |  | Record V & A
textbox | White Phase |  |  | Record V & A
textbox | Blue Phase |  |  | Record V & A
checkpoint | DB Meter reading (V=Volts & A=Amps)
textbox | Red Phase |  |  | Record V & A
textbox | White Phase |  |  | Record V & A
textbox | Blue Phase |  |  | Record V & A
holdpoint | BOJV Acceptance
checklist | LEVEL / AREA | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000005 - Conduits
section | CONDUITS
checkpoint | CORRECT LOCATION TO DRAWING
label | As per HD SHD
checkpoint | CORRECT SIZE AND TYPE
label | As per HD SHD
checkpoint | CORRECT SPACING IN SLAB
As per HD SHD
checkpoint | CORRECT DEPTH IN SLAB
As per HD SHD
checkpoint | CLEAR TO OTHER SERVICES
As per HD SHD
checkpoint | ACCEPTABLE INSTALLATION STANDARD
As per HD SHD
checkpoint | NO DAMAGE TO CONDUITS & CONDUITS ARE SECURELY FIXED
checkpoint | MEASUREMENTS ARE TAKEN FOR ANY DEVIATION & PHOTOS RECORDED
holdpoint | BOJV Acceptance
checklist | LEVEL / AREA | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000006 - Cable Tray
section | CABLE TRAY
checkpoint | AREA/LOCATION
label | As per HD SHD
checkpoint | CORRECT SIZE
label | As per HD SHD
checkpoint | CORRECT TYPE
label | Tray/Ladder/Basket
checkpoint | CORRECT RATING
label | Fire Rated/Standard
checkpoint | CORRECT MATERIAL
label | Zinc/Gal/HD/SS
checkpoint | CORRECT SUPPORT
label | As Per Manufacturer's guidelines
checkpoint | CORRECT ALIGNMENT
label | Visual Inspection
holdpoint | BOJV Acceptance
checklist | CABLE ID: FROM - TO | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000008 - Low Voltage Submain Cables
section | LOW VOLTAGE SUBMAIN CABLES
checkpoint | PRE-REQUISITE WORKS
button | Compliance | FIRE RATED,NON-FIRE RATED
button | Type | XLPE90,XHF110
textbox | Size |  |  | RECORD DIAMETER
textbox | Cores |  |  | RECORD CORES
checkpoint | INSTALLATION CHECKS
label | VISUAL INSPECTION TO CONFIRM NO DAMAGE TO INSULATION
checkpoint | CONTINUITY TEST
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device
label | RESISTANCE OF EARTH SHALL NOT BE MORE THAN 0.5Ω
textbox | TARGET RESISTANCE (OHM)
textbox | RESULT
section | INSULATION RESISTANCE
checkpoint | R-W
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
section | PHASE ROTATION
checkpoint | PHASE ROTATION
label | AS/NZS 3017:2007 3.5 Phase Sequence - Phase sequence testing is necessary to ensure that multi-phase equipment such as multi-phase motors and semiconductor controlled equipment operates in a predictable manner.
label | Record result
textbox | ROTATION:
section | VOLTAGE CHECK
checkpoint | RED PHASE
label | Test Line Voltages and ensure the voltages are within acceptable range
label | Aus Grid NS238 6.1.1.1 Low Voltage Supply
label | 230V +10% / -6% = Range 216V to 253V
label | 400V +10% / -6% = Range 376V to 440V
textbox | RED PHASE:
checkpoint | WHITE PHASE
label | Test Line Voltages and ensure the voltages are within acceptable range
label | Aus Grid NS238 6.1.1.1 Low Voltage Supply
label | 230V +10% / -6% = Range 216V to 253V
label | 400V +10% / -6% = Range 376V to 440V
textbox | RED PHASE:
checkpoint | BLUE PHASE
label | Test Line Voltages and ensure the voltages are within acceptable range
label | Aus Grid NS238 6.1.1.1 Low Voltage Supply
label | 230V +10% / -6% = Range 216V to 253V
label | 400V +10% / -6% = Range 376V to 440V
textbox | RED PHASE:
section | EARTH FAULT LOOP IMPEDANCE TEST
checkpoint | IMPEDANCE (OHM)
label | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
label | 20A TYPE C PROTECTION 1.53 Ω.
label | 32A TYPE C PROTECTION 0.96 Ω.
textbox | IMPEDANCE: |  |  | Ω
checkpoint | TARGET IMPEDANCE (OHM)
label | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
label | 20A TYPE C PROTECTION 1.53 Ω.
label | 32A TYPE C PROTECTION 0.96 Ω.
textbox | TARGET IMPEDANCE: |  |  | Ω
holdpoint | BOJV Acceptance
checklist | CABLE ID: FROM - TO | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000009 - Main Earthing System
section | MAIN EARTHING SYSTEM
checkpoint | PRE-REQUISITE WORKS
label | Confirm All Work Has Been Completed
checkpoint | VISUAL CHECK
label | Visual Inspection – No damage, outlet installed correctly
checkpoint | CONTINUITY TEST
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
label | 2.5MM 2C+E 20A Type C – < 0.50 Ω
section | ELECTRICAL RESISTANCE TEST
checkpoint | RESISTANCE (OHM)
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
label | 2.5MM 2C+E 20A Type C – < 0.50 Ω
textbox | RESISTANCE: |  |  | Ω
checkpoint | TARGET RESISTANCE (OHM)
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
label | 2.5MM 2C+E 20A Type C – < 0.50 Ω
textbox | RESISTANCE: |  |  | Ω
holdpoint | BOJV Acceptance
checklist | LOCATION | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000010 - Lightning Protection - RWV
section | EARTHING
checkpoint | Rods, clamps, conductors
textbox | Location
textbox | Correct size
textbox | Correct number
textbox | Straight and secure
checkpoint | Test points
textbox | Location
textbox | Correct number
textbox | Straight and secure
section | DOWN CONDUCTORS
checkpoint | Structure used
textbox | Location
textbox | Correct number
textbox | Continuity testing
checkpoint | Separate
textbox | Location
textbox | Correct size
textbox | Correct number
textbox | Straight and secure
section | Aerial termination;
checkpoint | Terminals
textbox | Location
textbox | Correct size
textbox | Correct number
textbox | Straight and secure
checkpoint | Strapping
textbox | Location
textbox | Correct size
textbox | Correct number
textbox | Straight and secure
checkpoint | Bonding
textbox | Location
textbox | Correct size
textbox | Correct number
textbox | Straight and secure
section | TESTING
checkpoint | Earth resistance test
textbox | Report number
checkpoint | Column continuity test
textbox | Report number
checkpoint | Full system test
textbox | Report number
holdpoint | BOJV Acceptance
checklist | CABLE ID: FROM - TO | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000011 - Lighting Circuits
section | LIGHTING CIRCUITS
checkpoint | PRE-REQUISITE WORKS
button | DB COMPLETE | YES,NO
button | DB ENERGIZED | YES,NO
button | DB COMMISSIONED | YES,NO
checkpoint | INSTALLATION CHECKS
label | Visual Inspection to confirm no damage to insulation, Plug bases installed correctly
section | CONTINUITY TEST
checkpoint | TARGET RESISTANCE (OHM)
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device
label | EXAMPLE 2.5MM 2C+E 20A Type C – ˂ 0.50 Ω
textbox | TARGET RESISTANCE: |  |  | Ω
section | INSULATION RESISTANCE
checkpoint | R-W
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
section | VOLTAGE CHECK
checkpoint | RED PHASE
label | Test Line Voltages and ensure the voltages are within acceptable range
label | Aus Grid NS238 6.1.1.1 Low Voltage Supply
label | 230V +10% / -6% = Range 216V to 253V
textbox | RECORD VOLTAGE
section | POLARITY CHECK
checkpoint | NO TRANSPOSITION
label | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
label | Verification through continuity testing of each conductor
checkpoint | SWITCH IN ACTIVE
label | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
label | Verification through continuity testing of each conductor
section | RCD TRIPPING TEST
checkpoint | TRIP CURRENT
label | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
label | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
label | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
label | Result < 300ms
checkpoint | TRIPPING TIME
label | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
label | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
label | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
label | Result < 300ms
holdpoint | BOJV Acceptance
checklist | LEVEL / NETWORK | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000012 - Lighting Control - Automated
section | INSPECTION AND PROGRAMMING
checkpoint | Dynalite equipment Load schedules completed with circuitry information for each output equipment by flash testing individual outputs
checkpoint | Testing of output unit for each DALI universe operation by flash testing individual outputs
checkpoint | Field input lighting control equipment (Switches, occupancy Sensors, light Level Sensors) installed and terminated as per specification
checkpoint | Input commissioning sheets complete with field device information
checkpoint | Programming of DALI control units as per zone mark up
checkpoint | Programming of lighting control input units (Switches, occupancy Sensors, Light Level Sensors)
checkpoint | Touch screen operation tested
section | COMMISSIONING
checkpoint | Tested power failure recovery system isolate power to control system
checkpoint | Addressing of Network Bridges and gateways ping test via ICN network
checkpoint | Allocated devices responding to allocated addresses via Ping test
checkpoint | Tested Head End operation and control functions
checkpoint | Mapping of Graphical data points (read/white), Manual controls buttons
checkpoint | Witness testing verifies correct control
checkpoint | Device functionality confirmed
checkpoint | Realtime reporting demonstrated
section | TESTS
checkpoint | Test Required: Functional
holdpoint | BOJV Acceptance
checklist | FITTING ID | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000013 - Emergency Lighting
section | EMERGENCY LIGHTING
checkpoint | PRE-REQUISITE WORKS
checkpoint | CORRECT LOCATION
checkpoint | CONSTRUCTION AND FINISH
checkpoint | LEVEL AND ALIGNMENT
checkpoint | ACCESS PROVISIONS
checkpoint | EARTH CONNECTION
checkpoint | LABELLING
checkpoint | DISCHARGE AUTONOMY TEST
holdpoint | BOJV Acceptance
checklist | OUTLET # | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000014 - Power Outlets
section | POWER OUTLETS
checkpoint | PRE-REQUISITE WORKS
label | Confirm All Work Has Been Completed
checkpoint | INSTALLATION CHECKS
label | Visual Inspection – No damage, outlet installed correctly
section | CONTINUITY TEST
checkpoint | RESISTANCE (OHM)
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
label | 2.5MM 2C+E 20A Type C – < 0.50 Ω
textbox | RESISTANCE: |  |  | Ω
checkpoint | TARGET RESISTANCE (OHM)
label | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
label | 2.5MM 2C+E 20A Type C – < 0.50 Ω
textbox | TARGET RESISTANCE: |  |  | Ω
section | INSULATION RESISTANCE
checkpoint | R-W
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-B
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-N
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | R-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | W-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
checkpoint | B-E
label | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
textbox | The insulation resistance shall be not less than 1 MΩ.
section | POLARITY CHECK
checkpoint | NO TRANSPOSITION
label | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
label | Verification through continuity testing of each conductor
checkpoint | SWITCH IN ACTIVE
label | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
label | Verification through continuity testing of each conductor
section | EARTH FAULT LOOP IMPEDANCE TEST
checkpoint | IMPEDANCE (OHM)
label | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault loop to cause a protective device to operate within a specified disconnection time.
label | 20A TYPE C PROTECTION 1.53 Ω.
label | 32A TYPE C PROTECTION 0.96 Ω.
textbox | IMPEDANCE: |  |  | Ω
checkpoint | TARGET IMPEDANCE (OHM)
label | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault loop to cause a protective device to operate within a specified disconnection time.
label | 20A TYPE C PROTECTION 1.53 Ω.
label | 32A TYPE C PROTECTION 0.96 Ω.
textbox | TARGET IMPEDANCE: |  |  | Ω
section | RCD TRIPPING TEST
checkpoint | TRIP CURRENT
label | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
label | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
label | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
label | Result < 300ms
checkpoint | TRIPPING TIME
label | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
label | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
label | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
label | Result < 300ms
holdpoint | BOJV Acceptance
checklist | INSTRUMENT S/N # | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000016 - PFC Equipment
section | INSTALLATION INSPECTION (WARNING: SYSTEM MUST BE DE-ENERGISED)
checkpoint | SIGNS OF EXTERNAL DAMAGE
checkpoint | SIGNS OF INTERNAL DAMAGE
checkpoint | ENCLOSURE SECURELY MOUNTED
checkpoint | ENCLOSURE VENTILATION
checkpoint | SIZE OF POWER CABLE
checkpoint | SIZE OF NEUTRAL CABLE
checkpoint | SIZE OF PE CABLE
checkpoint | CABLE CONNECTIONS
checkpoint | PHASE SEQUENCE
checkpoint | POSITION OF CT'S
checkpoint | POWER FUSES
checkpoint | CONTROL FUSES
checkpoint | CT LINKS
section | INSULATION RESISTANCE (WARNING: SYSTEM MUST BE DE-ENERGISED)
checkpoint | L1 - L2
label | MEGGER VALUE: >200MΩ
checkpoint | L1 - L3
label | MEGGER VALUE: >200MΩ
checkpoint | L2 - L3
label | MEGGER VALUE: >200MΩ
checkpoint | L1 - N
label | MEGGER VALUE: >200MΩ
checkpoint | L2 - N
label | MEGGER VALUE: >200MΩ
checkpoint | L3 - N
label | MEGGER VALUE: >200MΩ
checkpoint | L1 - PE
label | MEGGER VALUE: >200MΩ
checkpoint | L2 - PE
label | MEGGER VALUE: >200MΩ
checkpoint | L3 - PE
label | MEGGER VALUE: >200MΩ
checkpoint | N - PE
label | MEGGER VALUE: >200MΩ
section | RESISTANCE OF EARTHING SYSTEM (WARNING: SYSTEM MUST BE DE-ENERGISED)
checkpoint | GLAND PLATE
label | MEGGER VALUE: <0.5Ω
checkpoint | ENCLOSURE
label | MEGGER VALUE: <0.5Ω
checkpoint | DOORS
label | MEGGER VALUE: <0.5Ω
section | CIRCUIT BREAKER SETTINGS (WARNING: SYSTEM MUST BE DE-ENERGISED)
checkpoint | CIRCUIT BREAKER INSTALLED
bool | in switchboard
bool | in HAPFC system
checkpoint | PROTECTION FUNCTION - Long Delay Overload
label | RECOMMENDED SETTING: 1.25 to 1.5 times In
textbox | SETTING AT COMMISSIONING:
label | To determine In, use the following formula:
label | In (A) = ((Q kVAr/50kVAr) x 70A + IAHF)) x 1.3
label | Where:
label | In – Total Nominal Current of HAPFC unit (expressed in Amps)
label | Q – Total Nominal Reactive Power of Capacitor bank (expressed in kVAr)
label | IAHF – Total Rated Current of HPQ modules (expressed in Amps)
label | NOTE: IT IS ESSENTIAL TO CHECK AND MAKE ALL NECESSARY ADJUSTMENTS TO THE HAPFC CIRCUIT BREAKER(S) TO ENSURE DISCRIMINATION IS CO-ORDINATED WITH THE UPSTREAM PROTECTION.
checkpoint | PROTECTION FUNCTION - Instant Short Circuit
label | RECOMMENDED SETTING: 5 times In
textbox | SETTING AT COMMISSIONING:
label | To determine In, use the following formula:
label | In (A) = ((Q kVAr/50kVAr) x 70A + IAHF)) x 1.3
label | Where:
label | In – Total Nominal Current of HAPFC unit (expressed in Amps)
label | Q – Total Nominal Reactive Power of Capacitor bank (expressed in kVAr)
label | IAHF – Total Rated Current of HPQ modules (expressed in Amps)
label | NOTE: IT IS ESSENTIAL TO CHECK AND MAKE ALL NECESSARY ADJUSTMENTS TO THE HAPFC CIRCUIT BREAKER(S) TO ENSURE DISCRIMINATION IS CO-ORDINATED WITH THE UPSTREAM PROTECTION.
section | THERMO CONTROLLER (WARNING: SYSTEM MUST BE DE-ENERGISED)
checkpoint | STAGE #1
textbox | Set to
checkpoint | STAGE #2
textbox | Set to
section | CONTROLLER
checkpoint-no-status | Details
textbox | Model
textbox | Serial Number
textbox | HMI Version
textbox | HMI Data Version
section | HPQ MODULE - MASTER
checkpoint-no-status | Details
textbox | Model
textbox | Serial Number
textbox | Manufacturer
textbox | MCC Version
section | HPQ MODULE - SLAVE
checkpoint-no-status | Details
textbox | Model
textbox | Serial Number
textbox | Manufacturer
textbox | MCC Version
section | CAPACITOR BANK (UNIT MUST BE DE-ENERGISED)
checkpoint | CAPACITOR BANK
textbox | Stage:
textbox | Size, kVAr:
label | Capacitance, uF
textbox | L1-L2:
textbox | L1-L3:
textbox | L2-L3:
section | VOLTAGE WHEN SYSTEM DE-ENERGISED
checkpoint | LINE VOLTAGE
textbox | L1-L2
textbox | L1-L3
textbox | L2-L3
section | CAPACITOR BANK - CURRENT
checkpoint | CAPACITOR BANK - CURRENT
textbox | Stage:
textbox | Size, kVAr:
label | Current, A
textbox | L1
textbox | L2
textbox | L3
section | CONNECTION SETTINGS
checkpoint | Controller
textbox | Name
textbox | IP-address
textbox | Port
checkpoint | HPQ Master
textbox | Name
textbox | IP-address
textbox | Port
checkpoint | HPQ Slave
textbox | Name
textbox | IP-address
textbox | Port
section | HPQ SETTINGS - COMMISSIONING
checkpoint | ENABLE IGBT OPERATION
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | CONNECTION TYPE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | ELECTRICAL CONNECTION (3W/4W)
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | CONFIRMED FREQUENCY
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Confirmed voltage
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | COMPENSATION MODE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | BALANCING DEGREE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | X1 CT-RATIO (CUSTOMER CTS)
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | TOTAL INSTALLED CURRENT
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | X3 CT-RATIO (AUXILIARY CTS)
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | ENABLE AUTOSTART
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | ENABLE AUTOACK
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | ENABLE STAND-BY
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | STAND BY TRIGGER LEVEL
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | X1 CT-POLARITY L1
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | X1 CT-POLARITY L2
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | X1 CT-POLARITY L3
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL OUTPUT 0
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL OUTPUT 1
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL OUTPUT 2
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL OUTPUT 3
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL INPUT 1
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL INPUT 2
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DIGITAL INPUT 3
textbox | HPQ - Master
textbox | HPQ - Slave
section | HPQ SETTINGS - HPQ PARAMETERS
checkpoint | Enable HPQ
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | HPQ-MODE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | UNIT ROLE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | ENABLE FO
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | OVERVOLTAGE LIMIT
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | THDU TRIP LIMIT
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | STEP COUNT
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | STEP SIZE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | SERIES REACTOR
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | RATED CAPACITOR VOLTAGE
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | HYSTERESIS LIMIT
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | DISCHARGE TIME
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | ENABLE LAST DO AS TRIP
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | CONNECTION ALARM COUNT
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | TARGET POWER FACTOR
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | CAPACITIVE POWER FACTOR
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | SECONDARY POWER FACTOR
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | PRIORITY CURRENT LEVEL
textbox | HPQ - Master
textbox | HPQ - Slave
section | HPQ SETTINGS - COMPENSATION DEGREE
checkpoint | Ih2
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih3
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih4
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih5
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih6
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih7
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih8
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih9
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih10
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih11
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih12
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih13
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih14
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih15
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih16
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih17
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih18
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih19
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih20
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih21
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih22
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih23
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih24
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih25
textbox | HPQ - Master
textbox | HPQ - Slave
checkpoint | Ih1
textbox | HPQ - Master
textbox | HPQ - Slave
section | POWER QUALITY PARAMETERS
checkpoint | HAPFC Mode - "STOP"
textbox | THD_V, L1
textbox | THD_V, L2
textbox | THD_V, L3
textbox | THD_I, L1
textbox | THD_I, L2
textbox | THD_I, L3
textbox | PF
checkpoint | HAPFC Mode - "RUN"
textbox | THD_V, L1
textbox | THD_V, L2
textbox | THD_V, L3
textbox | THD_I, L1
textbox | THD_I, L2
textbox | THD_I, L3
textbox | PF
section | VOLTAGE WHEN SYSTEM OPERATING
checkpoint | LINE VOLTAGE
textbox | L1-L2
textbox | L1-L3
textbox | L2-L3
checkpoint | PHASE VOLTAGE
textbox | L1-L2
textbox | L1-L3
textbox | L2-L3
section | FUNCTIONAL TEST
checkpoint | FUNCTIONAL TEST
holdpoint | BOJV Acceptance
checklist | LEVEL | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000017 - MATV
section | MATV
checkpoint | QLTY
textbox | Prg
textbox | Mode
textbox | Freq. [MHz]
textbox | Prg.Name
textbox | Local Osc [MHz]
textbox | S.Rate or CH.BW.
textbox | Lnb Pol SEGMENTS
textbox | DiSEqC LAYER
textbox | Stand. or Constel
textbox | Level or Power [dBuV]
textbox | C/N MER EVM [dB]
textbox | bBER aBER PER
textbox | N.MA. [dB]
textbox | FEC HP/LP CODE RATE
holdpoint | BOJV Acceptance
checklist | CABLE # | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000019 - Fibre Optic Cabling
section | FIBRE OPTIC CABLING
checkpoint | PRE-REQUISITE WORKS
label | Confirm All Work Has Been Completed
checkpoint | INSTALLATION CHECKS
label | Visual Inspection – No damage, outlet installed correctly
checkpoint | VERIFICATION & TESTING
label | REFER TO SEPARATE FLUKE TEST SHEETS FOR TESTING RESULTS
button | LABELLING COMPLETE | YES,NO
button | FLUKE TEST PASS | YES,NO
holdpoint | BOJV Acceptance
checklist | CABLE # | itp |  |  |  |  | SMCSWSPS-HEY-OSN-ED-ITP-000020 - Comms Copper Cabling
section | FIBRE OPTIC CABLING
checkpoint | PRE-REQUISITE WORKS
label | Confirm All Work Has Been Completed
checkpoint | INSTALLATION CHECKS
label | Visual Inspection – No damage, outlet installed correctly
checkpoint | VERIFICATION & TESTING
label | REFER TO SEPARATE FLUKE TEST SHEETS FOR TESTING RESULTS
button | LABELLING COMPLETE | YES,NO
button | FLUKE TEST PASS | YES,NO
holdpoint | BOJV Acceptance