## Table 1
BESS Alinta Wagerup Peaking Power Station Field Inspection Checklist – Drainage installation Document Number: RR-SEPD-BESS-FIC-005
Document Information
Checklist title |  |  | Drainage installation
Checklist No |  |  | RR-SEPD-BESS-FIC-005
Lot Description
Revision no. |  |  | 1
Revision Date (DD/MM/YYYY)
Description of Changes |  |  | First Issue
Document Review
Prepared by:
Responsibility |  | Name |  |  | Signature |  | Date (DD/MM/YYYY)
Drafted by (Engineer) |  | Juan Orozco |  |  |  |  | 2025-03-13
Reviewed by (Supervisor) |  | Craig Stein |  |  |  |  | 2025-03-13
Approved by (Manager) |  | Artur Krupinski |  |  |  |  | 2025-03-14
Part 1 – Preliminaries (photos where applicable)
Inspection/Test item |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
[7 empty] | ROBAR | SEPD
1.1 | Review of approved construction drawings and specifications |  |  | All drawings and specifications approved and up to date | WBS-SS-CI-SPC-006
1.2 | Verification of permits |  |  | All relevant permits (GDA/GDP) in place | GDA/GDP
1.3 | Site access and safety preparation |  |  | Site access cleared and made safe | WBS-SS-CI-SPC-006
1.4 | Safety inductions and toolbox talks |  |  | All personnel inducted; safety briefings completed | Induction record
1.5 | Environmental controls in place |  |  | Dust, noise, and sediment barriers installed and functioning | SEPD environmental requirements
Part 2 – Excavation and trenching (photos where applicable)
2.1 | Trench depth and width comply with design |  |  | Set-out verified and matches IFC drawings | Site IFC Drawings AS/NZS 3500
2.2 | Stable trench walls (benching, battering) |  |  | Trenches deeper than 1.5m require benching, or battering unless certified by a geotechnical engineer. | WBS-SS-CI-SPC-006 AS 4744
2.3 | Pipes inspected for defects before installation |  |  | Material certs from manufacturer and visual inspection Material to align with design drawings and load rating | Manufacturer certifications
2.4 | No water accumulation in trenches |  |  | No standing water or excessive moisture inside the trench. | AS/NZS 3500
2.5 | Exclusion zones around excavation established |  |  | Proper barricades and signage placed around excavation area. | AS 1742
2.6 | Spoil stockpiles located at least 1m from trench edges |  |  | Stockpiles away from excavation to maintain safety of batters | WBS-SS-CI-SPC-0006
2.7 | Access and egress (ladders, steps) provided for trenches deeper than 1.2m |  |  | Access and egress for each trench. | WHS
Part 3 – Bedding & Pipe Installation (photos where applicable)
3.1 | Correct bedding material used (sand, gravel, etc.) |  |  | Material complies with particle size, moisture content, MMDD | WBS-SS-CI-SPC-0006 Test material results
3.2 | Bedding compacted to required density |  |  | Layers placed in maximum 300mm (loose) thickness | WBS-SS-CI-SPC-0006
3.3 | Pipes and materials inspected for defects before installation |  |  | Installed to design grade ±10mm and alignment within 5mm tolerance. | AS/NZS 3500
3.4 | Pipes laid at correct grade and alignment |  |  | Levels and grading match design tolerances (+/- 20mm) | WBS-SS-CI-SPC-0006, Survey Report
3.5 | Correct pipe jointing method used (rubber ring, solvent weld, etc.) |  |  | Joints must be fully engaged and sealed per manufacturer specifications | Manufacturer specifications
Part 4 – Backfilling and compaction (photos where applicable)
4.1 | Initial backfill material placed evenly around pipes |  |  | Site-won material approved by geotechnical engineer | Geotechnical report AS/NZS 3725
4.2 | No large rocks or debris in backfill |  |  | No rocks or debris in backfill | WBS-SS-CI-SPC-0006
4.3 | Backfilling in controlled layers (300mm lifts) |  |  | Backfill in uniform layers of maximum 300mm thickness | WBS-SS-CI-SPC-0006 Drainage drawings
4.4 | Backfill shall be placed to a depth of 300mm above collars of pipes or conduits |  |  | Minimum 300mm above collars of pipes | WBS-SS-CI-SPC-0006
4.5 | Compaction tests performed and passed (Proctor Density, NDM, etc.) |  |  | Compacted to 93% MMDD | WBS-SS-CI-SPC-0006 AS 1289 TQ # 66
4.6 | Surface reinstated as per project specs (concrete, asphalt, topsoil) |  |  | Backfill to match existing ground levels with ±10mm tolerance. | IFC drawings
Part 5 – Final inspections and acceptance (photos where applicable)
5.1 | Air pressure test |  |  | The pipe system must not lose more than a defined amount of pressure within the test duration. PVC - 25 kPa (3.5 psi) – pressure drop ≤3.5 kPa (0.5 psi) in 5 min. Concrete - 25-50 kPa (3.5- 7.0 psi) – pressure drop ≤10% drop in 5 min. | WBS-SS-CI-SPC-0006 AS 4033.2
5.1 | As-built survey verification |  |  | As-built levels and layout match design | As-Built Drawings Survey Report
5.2 | Removal of temporary works |  |  | All temporary structures, barriers, and access points removed | Site inspection
5.3 | Final inspection sign-off |  |  | All drainage activities completed and accepted | WBS-SS-CI-SPC-0006
Document Sign-off
Prepared by:
Responsibility |  | Name |  |  | Signature |  | Date (DD/MM/YYYY)
ROBAR (NER Engineer)
SEPD (Engineer)