## Table 1
Project Scope: Drainage installation | [20 empty] | Ref: RR-SEPD-BESS-ITP-005
Project: BESS Alinta Wagerup Peaking Power Station | [20 empty] | Revision: 01
ITP Description: Drainage installation
Work Pack number: RR-SEPD-CI-SOW-005-00
Client: SEPD
Prepared By: | [6 empty] | Sign & Date: 03/10/2024 |  |  | Reviewed & Approved By: | [10 empty] | Sign & Date: 03/10/2024
Juan Orozco – Project Engineer | [9 empty] | Ronan Egan – Project Manager
Reviewed & Approved By: | [6 empty] | Sign & Date: 03/10/2024 |  |  | Reviewed & Approved By: | [10 empty] | Sign & Date: 03/10/2024
Artur Krupinski - Project Controls | [9 empty] | Craig Stein – Site Supervisor
Definitions
Hold Point |  | A point beyond which a work process must not proceed without the nominated authority’s express authorization.
Witness Point |  | A point in a work process where the Contractor must give prior notice to the nominated authority and the option of attendance may be exercised by the nominated authority.
Responsibility | [5 empty] | Method |  |  |  | Frequency | [8 empty] | Verification Requirement
SUP | Supervisor |  |  |  |  | I | Inspection |  |  | PW |  | Prior to works | [6 empty] | HP |  |  | Hold Point
SE | Site Engineer |  |  |  |  | R | Review |  |  | PL |  | Per lot | [6 empty] | WP |  |  | Witness Point
PE | Project Engineer |  |  |  |  | S | Survey | [11 empty] | M |  |  | Milestone
SPE | Senior Project Engineer |  |  |  |  | T | Test | [11 empty] | V |  |  | Verification
PM | Project Manager | [17 empty] | NA |  |  | Not Available
SV | Surveyor
QM | Quality Manager
QR | Quality Representative
ER | Environmental Representative
IV | Independent Verifier
Contractor Name |  |  |  |  | ROBAR Rentals | [10 empty] | ITP no. |  |  |  | RR-SEPD-BESS-ITP-005-01
Responsible Engineer |  |  |  |  | Juan Orozco | [10 empty] | Work Pack no. |  |  |  | RR-SEPD-CI-SOW-005-00
Responsible Supervisor |  |  |  |  | Craig Stein / Aidan Mulligan
Location
Description
Item no. | Inspection/Test Point |  |  | Responsibility | Specification Reference |  |  | Conformance Criteria Summary |  |  | Method |  | Frequency |  | Reviewer |  | Hold/Witness Point Requirements | [6 empty] | Records or Checklist Document Number
[17 empty] | ROBAR | SEPD |  |  |  |  | Client
Section 1: Preliminaries & Permits
Remarks / NCR No. / HP No. / RFI No. / Notice Date
1.1 | Collect and verify information (Site boundary, utilities, survey map, design drawings) |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Results included in work pack |  |  | R |  | PW |  |  |  | V | NA |  |  |  |  | NA | IFC Drawings
1.2 | Permit approval (GDA/GDP) |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Approved excavation permit (GDP) prior to commencing works |  |  | R |  | PW |  |  |  | HP | HP |  |  |  |  | NA | RR-SEPD-CI- SOW-002-01
1.3 | Site set-out |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Verify levels, site boundaries, and physical bounds per IFC drawings |  |  | R |  | PW |  |  |  | V | NA |  |  |  |  | NA | IFC Drawings
1.4 | Sediment control plan |  |  | SE/PE | WBS-SS-PM- PLN-0024 WAE230103- 03-003 TM Rev0 |  |  | Sediment control measures in place |  |  | R |  | PW |  |  |  | V | NA |  |  |  |  | NA | SEPD environment- al plan
1.5 | Dust control plan |  |  | SE/PE | PP3 section 1.5 and section 4.1 |  |  | Dust control measures in place |  |  | R |  | PW |  |  |  | V | NA |  |  |  |  | NA | SEPD environment- al plan
Section 2: Materials
2.1 | Import fill material inspection |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Material certificate and test report for particle size distribution, moisture content, MMDD |  |  | R |  | PW |  |  |  | V | V |  |  |  |  | NA | Material certificates
2.2 | Verify suitable foundation material (compaction >95% MMDD) |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Geotechnical test results showing compliance |  |  | R |  | PW |  |  |  | HP | HP |  |  |  |  | NA | Test results
2.3 | Quality documentation RCP & precast drainage pits |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Supplier’s quality system certifications Product of compliance to AS 4058, AS 3500, AS 3996. (Load rating & liner shall align with design drawings) |  |  | R |  | PW |  |  |  | HP | HP |  |  |  |  | NA | Supplier’s documents
2.4 | Delivery acceptance of RCP |  |  | SE/PE | WBS-SS-CI- SPC-0006 AS/NZS 4058 |  |  | Acceptability of defects of RCP’s. Fibre RCPs shall be rejected if fractures and cracks wider than 0.1 mm and deeper than 0.3 mm are present. |  |  | R |  | PW |  |  |  | HP | HP |  |  |  |  | NA | Delivery dockets
Section 3: Construction
3.1 | Excavated trench |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Inspection following excavation of trench. Wacker plate to be use for compacting base. |  |  | I |  | PL |  |  |  | V | V |  |  |  |  | NA | IFC Drawings
3.2 | Bedding |  |  | SE/PE | WBS-SS-CI- 0006 |  |  | Material to be compacted at 100mm depth minimum. |  |  | I |  | PL |  |  |  | V | V |  |  |  |  | NA | IFC Drawings
3.3 | Placement of concrete pipes |  |  | SE/PE | WBS-SS-CI- SPC-0006 IFC drawings |  |  | Placed and joint in accordance with the manufacturer’s specifications Female ends upstream and lifting holes uppermost. Lifting holes in pipes shall be filled with plugs provided by pipe manufacturer |  |  | T |  | PL |  |  |  | HP | HP |  |  |  |  | NA | This ITP
3.4 | As-built survey prior to backfilling |  |  | SE E | WBS-SS-CI- 0006 |  |  | Variation of reduced level of invert from specified level: Whitin +/- 10 mm of specified position. Invert of structure shall not impede the gravity flow of water into or from structure |  |  | I |  | PL |  |  |  | V | V |  |  |  |  | NA | Survey report
3.5 | Installation of precast drainage structures |  |  | SE/PE | WBS-SS-CI- SPC-0006 AS 3500 Design drawings |  |  | Inspection pit cover to be installed flush with the final surface Where precast drainage structure is used, the external joint with pipe shall be strengthened with a concrete fill circling the joint. |  |  | T |  | PL |  |  |  | HP | HP |  |  |  |  | NA | Test results NER engineer specifications
3.6 | Trench/Precast drainage item backfill |  |  | SE/PE | WBS-SS-CI- SPC-0006 PPR |  |  | Unless specified otherwise, backfill layers shall be maximum 300 mm layers. |  |  | S |  | PL |  |  |  | V | V |  |  |  |  | NA | Compaction report
Section 4: Final Inspection
4.1 | Air pressure test |  |  | SE E | WBS-SS-CI- SPC-0006 AS 4033.2 |  |  | The pipe system must not lose more than a defined amount of pressure within the test duration. PVC - 25 kPa (3.5 psi) – pressure drop ≤3.5 kPa (0.5 psi) in 5 min. Concrete - 25-50 kPa (3.5-7.0 psi) – pressure drop ≤10% drop in 5 min. |  |  | S |  | PL |  |  |  | V | V |  |  |  |  | NA | WBS-SS-CI- ITP-920049
4.2 | Finish level compliance with design drawings |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | As-built drawings. |  |  | S |  | PL |  |  |  | V | V |  |  |  |  | NA | WBS-SS-CI- ITP-920049
4.3 | Final Inspection Checklist (FIC) completion |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Signed FIC |  |  | R |  | PL |  |  |  | V | V |  |  |  |  | NA | WBS-SS-CI- ITP-920049
Document sign-off
Close-out
Company |  |  | Name | [5 empty] | Position |  |  |  |  | Signature |  |  |  |  | Date (DD/MM/YYYY)
ROBAR (NER Engineer)
SEPD