## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Commissioning |  | Commissioning | 2dce675f-9bd9-4398-a169-b7d3e0d8a403
| checkpoint | SCV-Locks/chain/labels/pipework stickers/sprinkler spares & spanner/block plans
| checkpoint | Booster Cupboard-Signage/Locks/chain/labels/plan sleeve+block plans label/block plans
| checkpoint | Hydrant Mains/Isolation Valves-Locks/chain/labels/pipework stickers
| checkpoint | Water Meter Assembly-Locks/chain/labels
| checkpoint | Check sluice valves & water meter valves are open
| checkpoint | Fire Pump/Tank-Fuel full, Exhaust piped, Mains power, Drains/Relief Valve piped, Water Supply on, Locks/chain/labels/pipework stickers
| checkpoint | Adjust Bermads & float Valves to fire tanks
| checkpoint | Pump Room-Block Plans
| checkpoint | FIP-Block plans/test all alarm devices
| checkpoint | Test all Valves & Flow switches to ensure correct operation
| checkpoint | Set Pressure switches to Jacking pump & alarm line
| checkpoint | Block plans/Tactical Fire plans/FRV way finding plan
| checkpoint | FRV Shortfall drawings & FRV stat signage ie: x2 30m hose
| checkpoint | Individual Floor Block plans (If applicable)
| checklist | Fire Booster Cupboard Checklist |  | Fire Booster Cupboard | 2477694e-ac7b-4940-bf79-ebd04d39c1b3
| checkpoint | Install Suction/ Millcocks & Hydrant, Sprinkler Boosters
| checklist | Fire Extinguishers/Blankets |  | Fire Extinguishers/Blankets | 9a5360b3-914b-447d-8f0e-30f1d10efd8f
| checkpoint | Install Extinguishers
| checkpoint | Install appropiate signage
| checkpoint | Install Fire Blankets
| checkpoint | Fire Hose Reel signs
| checklist | Fire Penetrations Checklist |  | Fire Penetrations | 2edc8c9b-33b6-4f45-88fd-dd5d226f489e
| checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 Drawing Reference No.
| checklist | Fire Pumps/Tanks Checklist |  | Fire Pumps/Tanks | 1e575ff3-27f1-47cf-8dbb-1522065aa16d
| checkpoint | Install Plinth & secure
| checkpoint | Install Pumps & secure to plinths
| checkpoint | Install all pipework/isolation valves to pumps
| checkpoint | Install Annubar/coolant drains
| checkpoint | Install Pump Exhaust to designated point
| checkpoint | Water Test all Pipework to pumps
| checkpoint | Install all Pipework and Valves to Fire Tank
| checkpoint | Water test all pipework to and from Water Tank
| checklist | Hydrant/Sprinkler Mains/Risers/Hose Reel Checklist |  | Hydrant/Sprinkler Mains/Risers/Hose Reel | 801739e9-b2b2-44b1-8172-08b529190acc
| checkpoint | Rough In: All Mains & isolation valves installed
| checkpoint | Install Hydrant/ Sprinkler/Test Drain Risers & Mill Cocks
| checkpoint | Sprinkler Floor Control Valves installed and secured
| checkpoint | Fit Off: Check all millcock clearances/angles/Mill cocks in closed position & Install 2400kPa pressure gauge to top of risers
| checkpoint | Install Fire Hose Reels & pipework
| checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
6b08ebbc-55fe-5dbe-98b8-2e36e8d4fc84 | textbox | Start time:
d42ba8fc-3f90-509a-8a66-f49bea49243a | textbox | Completion time:
| checkpoint | Water Test: Pressure test to 1700Kpa for duration of 2 hours
130ab3a4-2ea3-56f9-970b-82b7fe01b599 | textbox | Start time:
4d9fd909-dfb6-5328-95ab-1a1f88fed285 | textbox | Completion time:
| checkpoint | FHR: All FHR been bled from excess air & proof of water
| checkpoint | PFP Foreman signature
| checklist | Incident Reports |  | Incident Reports | 94ff4877-5896-4288-a1e5-f0b4ed958d23
| section | Details of accident/incident
| checkpoint | Please attach any relevant photos & documents
b8e398b2-9f07-5ec4-ad4a-0ea6fabc58e0 | textbox | Date of incident
02157b38-0ec0-519e-afe1-313b8775c525 | textbox | Time of incident:
91b02009-1773-58e9-900e-b305c1295f7a | textbox | Time of report:
| checkpoint | Nature of incident
cde6122b-b5e0-5ba6-b664-32a2e177a72b | tickbox | Injury (attach completed WHSE Form 01 Injury report)
9f653aba-f79c-593f-8eb1-b50ccb91ecca | tickbox | Environmental (pollution)
9df6ceaf-a027-55e2-89f5-f258174ac943 | tickbox | Damage to property/assets/services
44cbdb69-18d6-5ae4-8ae2-c6b709b58a18 | tickbox | Incident
| section | Names of person(s) involved
| checkpoint | Please attach any relevant photos & documents
7c4273cc-af07-52a4-97b1-53941168e7f5 | textbox | Name
71658073-19eb-5eea-bd41-fb94e610c237 | textbox | Phone Number
b3f80afd-26f3-501b-a409-767be003e5bd | note | (home, mobile & work)
54ce6835-250c-57e5-bae2-d3882dba79e5 | textbox | Address
8600b9e2-f2de-565e-9cea-e3e3884a049c | textbox | D.O.B
e307318e-78af-5141-863c-ac8e5cdce34c | textbox | Email
971ea7bf-ecac-544e-86ac-9699e7ebcf9b | textbox | Activity in which the person(s) was engaged at the time:
378c10d6-48f6-5fa0-8209-1d175551b42c | textbox | Exact site location where injury/incident occurred:
c920932f-497a-5451-ada9-2013bee5f877 | textbox | Type of injury/pollution/damage/ incident:
aa2af06b-2849-52ba-871a-b29727d9d28d | textbox | Describe the accident/incident in detail:
| section | Witness to incident (each witness may need to provide an account of what happened
| checkpoint | Please attach any relevant photos & documents
d72f495c-3188-5a81-9ea4-3d5e42e5d643 | textbox | Witness Name
a4ef17e7-c680-5a72-81ec-9fa8a9656c12 | textbox | Witness Contact
cd71384b-6a3a-585d-a89d-298c349880db | textbox | Witness Name
b1fed57b-03d8-54e0-b822-47f279f7474b | textbox | Witness Contact
| section | Are there any notable/significant factors relevant to the accident/incident?
| checkpoint | Please attach any relevant photos & documents
aeb9b489-0ff0-5f33-80a3-4fcbd43c2db9 | textbox | Details
| section | Arrangements made to store any equipment that believed to have contributed to injury/incident?
| checkpoint | Please attach any relevant photos & documents
09c304f9-891b-5e20-b32a-2894b06dcc47 | textbox | Details
| section | Did any third parties (subcontractors, visitors, etc.,) contribute to the incident? If so, how?
| checkpoint | Please attach any relevant photos & documents
8d532223-c1bb-58b3-be24-2cfb5a61ff8f | textbox | Details
| section | Immediate corrective actions taken? (e.g., works ceased, area made safe, barriers erected, etc.,)
| checkpoint | Please attach any relevant photos & documents
89732764-536b-57ab-a503-66b0acf0f774 | textbox | Details
| section | Future actions taken (e.g., engineering solutions, training, toolbox talk, etc.,)
| checkpoint | Please attach any relevant photos & documents
dcfdf928-4a3c-5d86-802e-41e884aba8ac | textbox | Details
| section | Review & Sign off
| checkpoint | Have all actions been completed and reviewed as effective?
| checkpoint | Have all documents relating to the incident, including corrective action evidence been completed
| signoff | Signed Off
| checklist | Project Drawings |  | Project Drawings | 94f96b6a-2018-4302-8d4b-c0d7633d6a21
| checkpoint | Upload project drawings
| checklist | Site Diary Checklist |  | Site Diary Checklist | a2df845e-5ccd-473e-82bd-103d74af051c
| checkpoint | Comment/notes
| checklist | Sprinkler Control Valves Checklist |  | Sprinkler Control Valves | a130c08c-90d9-41d0-a933-871fbf89e5d5
| checkpoint | Install Sprinkler Control Valves/ Jacking Pump
| checkpoint | Test full operation of Control Valves
| checkpoint | Install Sprinkler Spares box, spare sprinklers & spanner
| checkpoint | Set Jacking Pump pressure switch min 150 kPa above towns main/manifold pressure
| checkpoint | Install Gong/Electric Bell & test operation
| checkpoint | Check for adequate drainage and test
| checklist | Sprinkler Fit Off Checklist |  | Sprinkler Fit Off | 15943692-857e-4be3-88c9-cccc687094c9
| checkpoint | Fit Off: Check all sprinklers have been fit off
| checkpoint | Check sprinkler heights pre paint
| checkpoint | Fit off Escutcheon plates
| checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
9131a2a8-5731-557c-ac6f-3662b76fcae2 | textbox | Start time:
6d030d6b-d62f-5ce2-af93-23524bc4e2e4 | textbox | Completion time:
| checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
2fa3f395-7198-5b5b-ab46-2b8342ab5a37 | textbox | Start time:
b0f62d96-51e2-531a-8231-062e21e5a50e | textbox | Completion time:
| checkpoint | PFP Foreman signature
| checklist | Sprinkler Rough In Checklist |  | Sprinkler Rough In | bfe2439a-c41d-4660-a334-e642daf0c488
| checkpoint | Rough In: All Mains, range pipes, clips installed & secured
| checkpoint | Concealed Space Sprinklers & Flexible droppers Installed
| checkpoint | Arm pieces / Under Duct pipework installed and secured
| checkpoint | Balcony Sprinklers installed
| checkpoint | Car Park Sprinklers Installed
| checkpoint | Car Stackers pipework installed & secured (if applicable)
| checkpoint | Install Remote Test drain pipework
| checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
b9757940-5951-5d7b-81a6-1a677e8c4afd | textbox | Start time:
18b5a95f-c4b3-58d2-b337-8f72830d37f1 | textbox | Completion time:
| checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
c9e0d1ee-966d-56ab-83f9-a7de9fe7d377 | textbox | Start time:
d2ffee9e-94f8-5722-9388-791a1a5b2340 | textbox | Completion time:
| checkpoint | PFP Foreman signature
| checklist | Toolbox Meeting Checklist |  | Toolbox Meeting Checklist | a5f287e2-dd8c-49e8-897d-c25064617ed4
| section | Attendance
| checkpoint | Attendance - list of attendees added below
| section | Minutes
| checkpoint | Actions from last meeting
| checkpoint | Safety: (including hazards / near misses / controls / site specific)
| checkpoint | Plant, tools & Equipment all in good working order?
| checkpoint | PPE-ensure everyone has PPE
| checkpoint | Housekeeping to be maintained
| checkpoint | Ensure Electrical equipment test and tagged
| section | New Business / Other
| checkpoint | Any new business / other comments added below
| section | Meeting Closure
| checkpoint | Meeting Closed
e5267aec-42c2-55be-bc03-6d2e07b16376 | textbox | Meeting Closed time
3649d014-4afc-5f34-aab0-c0902d8aecd4 | textbox | Minutes taken by (Name)
| checkpoint | Employee sign off
| checklist | Undocumented Variations |  | Undocumented Variations | 05b55b57-734d-4995-ad29-05ebf0b50a2b
| checkpoint | Attach relevant details
| checklist | Variations |  | Variations | df25d15f-b8d3-4a77-b2ad-5a7103e12220
| section | Payer Details
| checkpoint | Payer Details entered below
0f20223c-477d-5370-8e75-d45b7aaa141e | textbox | Contact
9be10722-627a-51f0-986a-9182fc5c52bd | textbox | Company
d0784a7f-ca20-56f4-99da-9f2c55b029ae | textbox | Contact No.
| section | Variation Details
| checkpoint | Variation Details Entered
3cbe9f48-0ae5-5171-8f0f-85f43cbdb6a6 | textbox | Description of work
2fd38eea-b9a9-53ae-9156-3c2af8792240 | textbox | Reason for variation (unless stated in instruction)
71ca1e15-1f98-573a-b074-b2ce43b095ee | textbox | Area/Location
8751cfdc-786f-5f86-9310-92630ff3fddf | textbox | As directed and requested by
2aa22bc7-c9d2-5975-87b3-665b6e75f383 | textbox | Date
e94f0685-873a-58fa-b162-4178de336a9b | textbox | Normal Hours
69d37f89-b930-5514-9329-c4409c236002 | textbox | Overtime Hours
11902ba5-38fd-5a33-b139-e0b6481c3ace | textbox | Material used to complete task
| checkpoint | Variation Completed
| section | Sign Off
| checkpoint | Variation signed
55fc4bd8-5627-56f1-bb42-48679d15ca19 | note | I hereby authorise you to carry out the extra work detailed above and I agree that the same shall be paid as an addition to your original contract order
| signoff | Builder / Client signature