## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 561469-ITP-0008 - Overflow Line (DG-QA-TP018) | itp |  |  |  |  | 561469-ITP-0008 - Overflow Line (DG-QA-TP018)
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Review all Drawings and Documents
label | Inspection Point: Quality Control Activity - Review all drawings and documentation provided to the Contractor.
label | Acceptance Criteria - Prior to the commencement of Works it must be ensure that all necessary documentation has been provided.
label | Verifying Document - ITP
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - R
label | Inspection: By (Role Key) - PM/QE
checkpoint | 3.2 - Setting Out Levels and Alignment
label | Inspection Point: Quality Control Activity - All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4
label | Acceptance Criteria - Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Compliance surveys or spot checks
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
label | Inspection: By (Role Key) - SP/QE/SV
holdpoint | HOLD POINT
checkpoint | 3.3 - Pipes Delivery
label | Inspection Point: Quality Control Activity - Pipes and pipe fittings shall be of the material, pipe class and joint type nominated on the Drawings. Specs 1131: 14.1 and Drawings C152 - C153
label | Acceptance Criteria - The charasteritics of the pipes delivered to site match the corresponding drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/CR
checkpoint | 3.4 - Joints and Fittings
label | Inspection Point: Quality Control Activity - All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2
label | Acceptance Criteria - The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent
label | Verifying Document - Delivery docket, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Trenches for flexible pipes shall be excavated within tollerances in table from Specs 1131: 15.2.5 unless otherwise stated Drawing C115
label | Acceptance Criteria - Depth of trench to achieve required minimum 600 mm cover
label | Verifying Document - Photos
label | Frequency - During trench excavation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.2 - Pipe Bedding and Haunching
label | Inspection Point: Quality Control Activity - Bedding and Haunching for submains should be in accordance with Drawing C115
label | Acceptance Criteria - Bedding material to have max size of 20mm
label | Verifying Document - Photos
label | Frequency - During bedding and haunching installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.3 - Pipe Line and Level
label | Inspection Point: Quality Control Activity - Pipes shall be laid true to the design line as in Drawings C100-C104
label | Acceptance Criteria - Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - SP/QE/SV
checkpoint | 4.4 - PE Pipe Installation
label | Inspection Point: Quality Control Activity - Buried PE pipes shall be installed in accordance with AS/NZS 2033 and AS/NZA 2566.2, as applicable. Specs 1131: 15.3.2.2
label | Acceptance Criteria - PE Pipe Joints and Intallation comply with standard and specifications
label | Verifying Document - Pipe welds QA records, welding checksheets and machine printouts, destructive tests results (if required)
label | Frequency - Per weld, and during pipe installation
label | Inspection Type (Visual, other) - Visual, Document Check, Lab test (if required)
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.5 - PVC Pipe Installation
label | Inspection Point: Quality Control Activity - Buried PVC pipes shall be installed in accordance with AS/NZS 2032 and AS/NZS 2566.2, as applicable. . Specs 1131: 15.3.1.
label | Acceptance Criteria - PVC Pipes Joints and Intallation comply with standard and specifications
label | Verifying Document - Photos
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - As-built Drawings
label | Inspection Point: Quality Control Activity - Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 5.2 - Pressure Testing
label | Inspection Point: Quality Control Activity - Test for PE pipelines shall be completed in accordance with AS/NZS 2566.2:2002 relevant appendices. Specs 1131: 16.3.1
label | Acceptance Criteria - Test results per pipe size comply with the standard and specifications
label | Verifying Document - Test Records, Photos
label | Frequency - At sections of pipe required
label | Inspection Type (Visual, other) - Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
section | SECTION 6 - COMMENTS
checkpoint | Customer Release Granted
textbox | Certificate Number:
date | Date: