## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 1630-P200-SYM-QAC-ITP-0016 Power Relocation | itp |  |  |  |  | 1630-P200-SYM-QAC-ITP-0016 Power Relocation
section | ITP Details
checkpoint | ITP Details
label | ITP No. - 1630-P200-SYM-QAC-ITP-0016
label | Rev No. - 00
label | Date of Issue - 15/12/2023
label | ITP Type - New/Revised
section | 1.0 Pre-start activities
checkpoint | 1.1 - Check Survey Set-out
label | Ref docs - IFC Drawings
label | Acceptance criteria - Ensure alignment setout has been completed and pegged.
button | Has all of the above been completed? | Yes,No
label | Freq - Prior to start of works
label | Key - H
label | Resp - SE/SS
checkpoint | 1.2 - Boring under Carriageways
label | Ref docs - VR Clause 706.04
label | Acceptance criteria - Boring by water jet not permitted.
label | ○ Detailed proposals for boring under carriageways shall be submitted to the superintendent for review two weeks prior to the programmed commencement of work.
button | Approval to proceed? | Yes,No,N/A
label | Freq - Prior to start of works
label | Key - H
label | Resp - SE
label | SI Key - H
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Conduit Covers
checkpoint | 2.1 - Excavation and Cover Requirements
label | Ref docs - VR Clause 706.03
label | Acceptance criteria - Cover requirements for electrical assets shall be:
label | ○ Pavement surface to top of conduit minimum 1200 mm.
label | ○ Invert of open drain to top of conduit minimum 750 mm.
label | ○ Unpaved areas to top of conduit minimum 600 mm.
label | ○ As per asset authority requirement for cover to other assets
label | Or else as specified on design drawings in accordance with asset owner requirements.
button | Has all of the above been completed and approved? | Yes,No,N/A
label | Freq - Each Lot & Each possession
label | Key - S
label | Resp - SE/SS
section | 3.0 Backfill and Compaction
checkpoint | 3.1 - Backfilling/Compaction (Areas not being paved)
label | Ref docs - Ausnet Tech Spec
label | Acceptance criteria - Works outside road: As per Power Authority
label | Freq - Each Lot
label | Key - R
label | Resp - SE/SS
checkpoint | 3.2 - Backfilling/Compaction (Under areas to be paved included shoulders and verges)
label | Ref docs - VR Clause 706.08, 706.09
label | Acceptance criteria - Unless backfilling requirements are specified by the Asset Owner Authority, backfill material properties as per VR706.061:
label | – trench shall be backfilled up to the nominated or designed subgrade level with selected backfill material placed and compacted in layers not exceeding 150 mm loose thickness, and above that level with common backfill material.
label | – The number of tests per lot shall be three. Backfill, the whole of which passes the 37.5 mm AS sieve, shall be compacted to a mean value of density ratio of not less than 97% based on Standard compactive effort. A lot shall consist of a single layer of work. A minimum of 20% of all lots constructed shall be tested.
label | – Considerations to be made to allow for Asset Owner Authority working restrictions, including vibratory restrictions.
button | Has all of the above been completed and approved by the relevant authority? | Yes,No,N/A
label | Freq - Each Lot
label | Key - R
label | Resp - SE/SS
button | Remarks/record (eg. Test frequency reports, certificates, checklist etc) - NATA Test Report (if applicable) | Yes,No,N/A
section | 4.0 Work Lot Close Out
checkpoint | 4.1 - Test Reports
label | Ref docs - VR706
label | Acceptance criteria - All Test reports received and reviewed.
button | Has all of the above been proven to meet and/or exceed minimum tested requirements? | Yes,No,N/A
label | Freq - Each Lot
label | Key - R, I
label | Resp - SE
checkpoint | 4.2 - As-built Information
label | Acceptance criteria - Where applicable, as built pickup or as constructed drawing been provided by authority.
button | Has all of the above been completed correctly and to a high standard? | Yes,No,N/A
label | Freq - Each Lot
label | Key - R
label | Resp - SE
checkpoint | 4.3 - Audits, checklists, and approvals
label | Ref docs - Ausnet Tech Spec
label | Acceptance criteria - Civil Audits for all trenches (If applicable).
label | ○ Cable Hauling audits (If applicable).
label | ○ Trench inspection and detailing of all conduits and cables (If applicable).
label | ○ Pre-commissioning audit with all non-conformances rectified (If applicable).
label | Freq - Each lot
label | Key - R
label | Resp - SE
button | Remarks/record (eg. Test frequency reports, certificates, checklist etc) - Conformance Report | Yes,No,N/A
checkpoint | 4.4 - Product Non-Conformance
label | Ref docs - CQMP
label | Acceptance criteria - All Product Non-Conformance(s) recorded and closed (if applicable)
button | Has all of the above been proven to meet and/or exceed minimum tested requirements? | Yes,No,N/A
label | Freq - Each Lot
label | Key - R
label | Resp - SE
button | Remarks/record (eg. Test frequency reports, certificates, checklist etc) - NCR reports | Yes,No,N/A