## Table 1
Item no. | Inspection/Test Point |  | Responsibility | Specification Reference | Conformance Criteria Summary |  | Method | Frequency |  | Hold/Witness Point Requirements |  |  |  | Records or Checklist Document Number
[10 empty] | ROBAR | SEPD |  | Client
Section 1: Preliminaries
1.1 | Review of approved construction drawings and specifications |  | SE/PE | WBS-SS-CI- SPC-0007 | Approved IFC drawings and project specifications available on-site |  | R | PW |  | V | NA |  | NA | IFC Drawings
1.2 | Site condition check and access preparation |  | SE/PE | WBS-SS-CI- SPC-0007 | Site cleared, accessible, and suitable for concrete slab works |  | R | PW |  | V | NA |  | NA
1.3 | Site safety induction and toolbox talks |  | SE/PE | WBS-SS-CI- SPC-0007 | All personnel inducted and briefed on safety, site-specific risks |  | R | PW |  | V | NA |  | NA | Site inductions records
1.4 | Inspection of plant and equipment (e.g., concrete pump, vibrators) |  | SE/PE | WBS-SS-CI- SPC-0007 | All equipment calibrated and operational |  | R | PW |  | V | NA |  | NA | Calibration/P re-start
1.5 | Foundation preparation |  | SE/PE | Geotechnical report/memo/ geotechnical engineer’s specifications | Compaction test reports/geotechnical engineer’s specifications |  | R | PW |  | V | V |  | NA | Calibration/P re-start
Section 2: Pre-pour preparations
2.1 | Verification of work permits |  | SE/PE | WBS-SS-CI- SPC-0007 | All necessary permits for concrete works in place (GDA/GDP) |  | R | PL |  | V | V |  | NA | GDA/GDP
2.2 | Blinding concrete installation |  | SE/PE | WBS-SS-CI- SPC-0007 Design drawings | Approved mix design |  | R | PL |  | V | V |  | NA | FIC
2.3 | Review of concrete mix design and material certificates |  | SE/PE | WBS-SS-CI- SPC-0007 | Approved mix design, material certificates compliant with AS 1379 |  | R | PW |  | HP | HP |  | NA | Product certificate of compliance
2.4 | Formwork inspection – alignment, cleanliness, and dimensions |  | SE/PE | WBS-SS-CI- SPC-0007 | Formwork in line with drawings, clean, and dimensionally correct |  | R | PW |  | HP | HP |  | NA | TWD FIC
2.5 | Reinforcement inspection (size, spacing, placement, cover) |  | SE/PE | WBS-SS-CI- SPC-0007 AS 4671 | Correct bar size, spacing, reinforcement securely tied, adequate cover |  | R | PW |  | HP | HP |  | NA | IFC Drawings FIC
2.6 | Verify waterproofing membrane |  | SE/PE | WBS-SS-CI- SPC-0007 | Membrane installed as per drawings/specs |  | R | PW |  | WP | WP |  | NA | IFC Drawings FIC
2.7 | Re-entrant bars (starter bars) and corner reinforcement |  | SE/PE | WBS-SS-CI- SPC-0007 | Correct positioning of all embedded items per drawings |  | R | PW |  | WP | WP |  | NA | IFC Drawings FIC
2.8 | Concrete batch plant inspection |  | SE/PE | AS 1379 | Batch plant adheres to mix design, and delivery meets timing requirements |  | R | PW |  | V | NA |  | NA | FIC
Section 3: Concrete placement
3.1 | Pre-pour concrete delivery inspection |  | SE/PE | WBS-SS-CI- SPC-0007 AS 1379 | Batch delivery dockets match approved mix |  | I | PL |  | WP | WP |  | NA | Delivery dockets
3.2 | Slump test at site (conformance to mix design) |  | SE/PE | AS 1012 | Slump within specified range (e.g., 100mm +/- 20mm) |  | I | PL |  | HP | HP |  | NA | Lab test report
3.3 | Concrete placement and compaction |  | SE/PE | WBS-SS-CI- SPC-0007 | Concrete placed within formwork, no segregation, fully compacted |  | T | PL |  | V | V |  | NA | Pour record
3.4 | Cylinder samples for compressive strength testing |  | SE/PE | AS 1012 | Minimum of 12 cylinders in total for 7, 14, 28-day tests |  | I | PL |  | HP | HP |  | NA | Lab test report
3.5 | Concrete temperature monitoring |  | SE/PE | WBS-SS-CI- SPC-0007 | Temperature within acceptable range |  | T | PL |  | HP | HP |  | NA | Pour record
3.6 | Placement monitoring – free- fall limit |  | SE/PE | WBS-SS-CI- SPC-0007 AS 3600 | Concrete poured with a maximum free-fall height of 1.8m to avoid segregation |  | T | PL |  | V | V |  | NA | FIC
3.7 | Vibration and compaction monitoring |  | SE/PE | WBS-SS-CI- SPC-0007 AS 3600 | Concrete properly compacted with vibrators, no voids or segregation |  | T | PL |  | V | V |  | NA | FIC
3.8 | Concrete curing |  | SE/PE | WBS-SS-CI- SPC-0007 FRP section 4.25.11 AS 3600 | Concrete curing per approved concrete curing method statement |  | T | PL |  | V | V |  | NA | FIC
Section 4: Final Inspection
4.1 | Surface finishing (Class of finish per AS 3610) |  | SE/PE | WBS-SS-CI- SPC-0007 AS 3610 | Class 5 finish for surfaces that are not visible after construction |  | S | PL |  | V | V |  | NA | FIC
4.2 | Curing procedure inspection |  | SE/PE | WBS-SS-CI- SPC-0007 AS 3799 | Curing compound applied or wet curing in place |  | R | PL |  | V | V |  | NA | FIC
4.3 | Formwork stripping and post-pour inspection |  | SE/PE | WBS-SS-CI- SPC-0007 AS 3610 | Formwork removed at required strength, surface defects repaired |  | R | PL |  | WP | WP |  | NA | FIC
4.4 | Compressive strength test results |  | SE/PE | AS 1012 | Compressive strength >32 MPa at 28 days |  | R | PL |  | HP | HP |  | NA | Lab test report
4.5 | Final inspection and acceptance of slab |  | SE/PE | WBS-SS-CI- SPC-0007 | Surface levels, dimensions, and finish within tolerances |  | R | PL |  | V | V |  | NA | FIC
4.6 | Joint Inspections |  | SE/PE | WBS-SS-CI- SPC-0007 | Expansion and contraction joints installed per design drawings |  | R | PL |  | V | V |  | NA | FIC
4.7 | Post-cure inspections for shrinkage and cracking |  | SE/PE | WBS-SS-CI- SPC-0007 | Inspection for early shrinkage cracks and proper curing continuation |  | R | PL |  | V | V |  | NA | FIC
Document sign-off
Close-out
Company |  | Name |  |  |  | Position |  |  | Signature |  |  | Date (DD/MM/YYYY)
ROBAR
SEPD