## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Prefix | Postfix | Usage Count | Resource Id
| checklist | Ω (DEPRECATED) ITR-E-19 HV Cable Install |  | ITR-E-19 HV Cable Install
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
90ad256a-cc82-47b2-be68-9a9ef3ab8b3d | checkpoint | HV Cable Install
cc29fa55-5fe5-542d-aae6-b5a317818561 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
3733b5ca-b64f-54bd-ba7c-aed07846a861 | button | Check dressing / cleating, cable undamaged | Yes,N/A
2bbb5df0-4010-557e-b31d-498f09f1e5ce | button | Check cable cores correctly identified and labelled. | Yes,N/A
3cf74f56-d88c-5ab3-8481-56c37a833142 | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
b7192934-0b91-5863-a040-df3cc234946a | button | Check Armour / Screen correctly made off. | Yes,N/A
db79cc67-bcee-5799-9eb7-63146f45bafc | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
8543d1a2-2cf8-58af-950a-b69fd0b88f9f | button | Glanding / Locknuts correctly installed. | Yes,N/A
429d748c-2b60-5309-9d6f-cc4108496a9c | dropdown | Cable Voltage | 11kV,33kV
1d3abe04-a329-541d-ba46-ea69fd91659a | textbox | Temperature:
1b9d8cb2-e175-5a88-878b-c5f1b97638f3 | textbox | Cable Point to Point:
7591ec71-d9d8-40f4-9572-07a1a6b71781 | checkpoint-no-value | Electrical Tests
a598796e-f8b5-560f-8616-052299e798ea | note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ.
b23c38ff-795d-555a-9db5-6b118428b720 | textbox | R-WBE |  |  |  | GΩ
b58fc05a-668d-5951-9d0a-e0aa26497667 | textbox | W-RBE |  |  |  | GΩ
d3aee404-6d4b-545e-8f34-01439b4d5763 | textbox | B-RWE |  |  |  | GΩ
d920a905-8990-5944-98ae-7117035d7879 | textbox | One Core |  |  |  | GΩ
e522260b-45be-4509-97a6-67cc2cb9a311 | checkpoint-no-value | Sheath Integrity Test
a83836d2-51e2-5b6d-bcbf-973658a28930 | textbox | Test Duration:
ff9b4409-cb93-5d68-bb8a-2f8ec1f70f82 | textbox | Test Voltage: |  |  |  | GΩ
01dafb52-67d2-56bb-95ea-97d522e08cec | textbox | Result (GΩ):
17ec1322-89c4-48fa-8d02-aed878f0ef01 | checkpoint-no-value | Test Equipment Details
e3c0e447-7654-5559-a02d-66073ef7160b | textbox | Make
af3d6851-5fe7-5c6f-aad3-271b7930e96b | textbox | Model
4a41adaf-c867-5778-b8fc-3d63e1106d0c | textbox | Serial No
ad61610c-21d8-57dd-9641-37d7310f5550 | textbox | Calibration Expiry Date
db024b07-edc6-49ca-bee7-7aeaad1efdad | checkpoint-no-value | Installer Sign-off
4997561d-fb4f-4a8a-998f-ad8ecb55915c | signoff | Installed by:
70fb74f8-a3c4-4a06-be4b-bed696e25411 | checkpoint-no-value | Client Sign-off
dbfc3f8b-2d70-4d1e-8059-3cbe99d6d564 | signoff | Client Representative: