## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Low Voltage Cables (Mains/Submains) | [5 empty] | Testing & Commissioning - Low Voltage Cables (Mains/Submains)
section | WSA20-MPX-04000-EL-ITC-31052000 Construction Tests (Pre-energisation)
checkpoint | Pre-requisite Works
checkpoint | Insulation Damage
checkpoint | Correct Type of Termination
checkpoint | Correct Cable Size and Labelling
signoff | Checked By (Heyday):
checkpoint-no-status | Insulation Resistance
checkpoint | R-W
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | N-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
signoff | Checked By (Heyday):
checkpoint-no-status | Continuity Testing
checkpoint | Red Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | White Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Blue Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Neutral
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Earth
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
section | WSA20-MPX-04000-EL-ITC-31053000 Component (Energised)
checkpoint-no-status | Phase Rotation
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
checkpoint-no-status | Voltage
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
checklist-flat | HV/LV Transformers | [5 empty] | Testing & Commissioning - HV/LV Transformers
checkpoint | Schneider Electric Transformer QA/QC Test Report – Installation Configuration Page 3.
checkpoint | Schneider Electric Transformer QA/QC Test Report – Pre-Testing inspection Page 4.
checkpoint | Schneider Electric Transformer QA/QC Test Report – Transformer Test - Page 4:
label | Continuity test on HV and LV Windings
label | ○ Insulation Resistance Test LV Winding to Earth
label | ○ Winding Resistance
label | ○ Winding Ration verification (taps: +2.5%, +1.25%, 0, -1.25%, -2.5% )
label | ○ Vector Groups
label | ○ Check bushings
label | ○ Control cubicle visual inspection
label | ○ Control Cabling within the control cubicle visual inspection and connection verification against approved schematics
label | ○ Confirm opening of LV door operates “normally open contact when doors are closed”
signoff | Checked By (Heyday):
checklist | Main Switchboards | [5 empty] | Testing & Commissioning - Main Switchboards
section | WSA20-MPX-04000-EL-ITC-31032000 - Construction Tests (Pre-energisation)
checkpoint-no-status | Physical Checks
checkpoint | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
checkpoint | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
checkpoint | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
checkpoint | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
checkpoint | 8. Confirm correct circuit identification and labelling
checkpoint | 9. Confirm easy access to controls termination
checkpoint | 10. Confirm correct location, access and sufficient support for incoming cables
checkpoint | 11. Confirm correct location, access and sufficient support for outgoing cables
checkpoint | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
checkpoint | 13. Confirm correct phase identification of busbars and cables inside the board
checkpoint | 14. Confirm correct size of incoming power cables as per approved cable schedule
checkpoint | 15. Confirm correct size of earthing conductors
checkpoint | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
signoff | Checked By (Heyday):
checkpoint-no-status | Mechanical Checks
checkpoint | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
checkpoint | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | 6. Repeat mounting and dismounting of control fuses 1 time
checkpoint | 7. Repeat mounting and dismounting of control fuses 1 time
checkpoint | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
checkpoint | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
checkpoint | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
signoff | Checked By (Heyday):
checkpoint-no-status | Switch Gear Busbar Insulation Resistance Test
checkpoint-no-status | Preliminary Checks
checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 2. Confirm Main Incomers ACBs/MCCBs are Closed
checkpoint | 3. Confirm Bus-coupler is Closed (if exist)
checkpoint | 4. Confirm Outgoing Feeders is Closed
checkpoint | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
checkpoint | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
checkpoint | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
checkpoint-no-status | Insulation Resistance (1000V)
checkpoint | 1. Between L1 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 2. Between L2 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 3. Between L3 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 4. Between Neutral and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 5. Between L1 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 6. Between L2 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 7. Between L3 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 8. Between L1 Phase and L2 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 9. Between L1 Phase and L3 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 10. Between L2 Phase and L3 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
signoff | Checked By (Heyday):
section | Circuit Breaker Settings Check |  | Refer to tab "MSB-Board List" for quantities of placeholder sections required
checkpoint | Circuit Breaker Settings Check
textbox | Cubicle ID
textbox | Feeder Name
textbox | Protection Device Name
button | Setup as per Discrimiation settings (YES/NO) | YES/NO
signoff | Checked By (Heyday):
section | Current Transformer Checks
checkpoint | Current Transformer Checks
textbox | CT ID | YES/NO
button | CT Polarity is Correct | YES/NO
button | No crossed phase CT connections | YES/NO
button | No phase sequence CT connection errors | YES/NO
signoff | Checked By (Heyday):
section | WSA20-MPX-04000-EL-ITC-31033000 - Component (Energised)
checkpoint-no-status | Phase Voltage Reading
checkpoint | Red- Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
checkpoint | Neutral - Earth
textbox | Voltage (V)
checkpoint | Red- White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint-no-status | Phase Rotation
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
checklist | Distribution Boards | [5 empty] | Testing & Commissioning - Distribution Boards
section | WSA20-MPX-04000-EL-ITC-31042000 - Construction Tests (Pre-energisation)
checkpoint-no-status | Physical Checks
checkpoint | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | Confirm correct circuit identification and labelling
checkpoint | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
checkpoint | Confirm correct phase identification of busbars and cables inside the board
checkpoint | Confirm correct size of earthing conductors
checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
checkpoint-no-status | Mechanical Checks
checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | Repeat mounting and dismounting of power fuses for 1 time
checkpoint | Repeat mounting and dismounting of control fuses 1 time
checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
checkpoint-no-status | Preliminary Checks
checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 2. Confirm Main Breaker Closed
checkpoint | 3. Confirm Outgoing Breakers Closed
checkpoint-no-status | Insulation Resistance (500V)
checkpoint | 1. Between L1 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 2. Between L2 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 3. Between L3 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 4. Between Neutral and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 5. Between L1 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 6. Between L2 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 7. Between L3 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 8. Between L1 Phase and L2 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 9. Between L1 Phase and L3 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 10. Between L2 Phase and L3 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
signoff | Checked By (Heyday):
checkpoint | Earth Continuity Test
textbox | Incoming Earth Size (mm²)
textbox | From (MSB/DB)
textbox | Resistance (Ω)
signoff | Checked By (Heyday):
section | WSA20-MPX-04000-EL-ITC-31043000 - Component (Energised)
checkpoint-no-status | Phase Voltage Reading
checkpoint | Red- Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
checkpoint | Neutral - Earth
textbox | Voltage (V)
checkpoint | Red- White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint-no-status | Phase Rotation
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
checklist | Low Voltage Busduct | [5 empty] | Testing & Commissioning - Low Voltage Busduct
section | WSA20-MPX-04000-EL-ITC-31062000 - Construction Tests (Pre-energisation)
checkpoint | Pre-requisite Works
checkpoint | Insulation Damage
checkpoint | Correct Type of Termination
checkpoint | Correct Colour Code
checkpoint | Correct Size and Labelling
checkpoint | Correct Routing
signoff | Checked By (Heyday):
checkpoint-no-status | Continuity Testing
checkpoint | Red Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | White Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Blue Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Neutral
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Earth
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
checkpoint-no-status | Insulation Resistance
checkpoint | R-W
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | N-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
signoff | Checked By (Heyday):
section | WSA20-MPX-04000-EL-ITC-31063000 - Component (Energised)
checkpoint-no-status | Phase Rotation
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
checkpoint-no-status | Voltage
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
checklist | Subcircuits | [5 empty] | Testing & Commissioning - Subcircuits
section | WSA20-MPX-04000-EL-ITC-31072000 - Construction Tests (Pre-energisation)
checkpoint | Pre-requisite Works
checkpoint | Insulation Damage
checkpoint | Correct Type of Termination
checkpoint | Correct Colour Code
checkpoint | Correct Outlet Rating and Size
signoff | Checked By (Heyday):
checkpoint | Earth Continuity
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
checkpoint | Polarity Check
button | No Transposition | YES,NO
button | Switch in Active | YES,NO
signoff | Checked By (Heyday):
checkpoint-no-status | Insulation Resistance
checkpoint | R-W
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | R-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | W-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | R-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | W-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | B-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | R-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | W-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | B-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | N-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
signoff | Checked By (Heyday):
section | WSA20-MPX-04000-EL-ITC-31073000 - Component (Energised)
checkpoint-no-status | Voltage
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
checkpoint | Earth Fault Loop Impedance Test - (N/A if the circuit is RCD Protected)
textbox | Impedance (Ω)
textbox | Target Impedance (Ω)
checkpoint | RCD/RCBO Tripping Test
textbox | Trip Current (mA)
textbox | Trip Time (ms)
signoff | Checked By (Heyday):
checklist | Earthing Systems | [5 empty] | Testing & Commissioning - Earthing Systems
section | WSA20-MPX-04000-EL-ITC-31092000a - Construction Tests (Main Earth System)
checkpoint | RWV Industries – Earthing Test Report. Steel Reinforcement Continuity
checkpoint | RWV Industries – Earthing Test Report. Footing Earthing
section | WSA20-MPX-04000-EL-ITC-31092000b – Construction Test (Earth System Reticulation)
checkpoint | Correct Cable Size and Labelling
checkpoint | Earth Continuity
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
checklist-flat | PFC | [5 empty] | Testing & Commissioning - PFC
checkpoint | WSA20-MPX-04000-EL-ITC-31102000 - Construction Tests (Pre-energisation)
checkpoint | WSA20-MPX-04000-EL-ITC-31073000 - Component Test (Energised)
checkpoint | CT Ratio Verification (V,A,kVA) L1/L2/L3 - Component Test (Energised)
checkpoint | Power Factor Correction Controller Configuration as per manufacturers recommendations - Component Test (Energised)
checklist | UPS | [5 empty] | Testing & Commissioning - UPS
section | WSA20-MPX-04000-EL-ITC-31122000 - Construction Tests (Pre-energisation)
checkpoint | Commissioning & Installation / Start-up Report - System Room Check – Page 6
checkpoint | Commissioning & Installation / Start-up Report - System Check – Page 6.
section | WSA20-MPX-04000-EL-ITC-31123000 - Component Tests (Pre-commissioning)
checkpoint | Commissioning & Installation / Start-up Report - Unit pre start-up check – Page 7
checkpoint | Commissioning & Installation / Start-up Report - Unit Functional Check – Page 7
checkpoint | Commissioning & Installation / Start-up Report - Unit Final Inspection – Page 8
section | WSA20-MPX-04000-EL-ITC-31124000 - System Commissioning
checkpoint | UPS – Functional Performance Test Report
label | The following tests are conducted (see Schneider Electric - Site Acceptance test protocol for results and trends): • Load Transfer test • Inverter to bypass transition on NO LOAD • Inverter to bypass transition on FULL LOAD • Load step test (0%-50%-0%) • Load step test (25%-75%-25%) • Load step test (50%-100%-50%) • Load step test (75%-100%-75%) • Load step test (0%-100%-0%) • THDi and THDv measurements (0%, 25%, 50%,75%, 100%) • Expected Results: Total Harmonic Distortion (THD) is to be under 5% • UPS efficiency calculation (Unity PF@0%, 25%, 50%, 75%, 100%) • UPS battery discharge test (15min EOL)
signoff | Checked By (Heyday):
checklist | Load Bank | [5 empty] | Testing & Commissioning - Load Bank
section | WSA20-MPX-04000-EL-ITC-31143000 - Component Tests (Pre-commissioning)
checkpoint | Sephco Commissioning Checklist
signoff | Checked By (Heyday):
checklist | Solar Photovoltaic System | [5 empty] | Testing & Commissioning - Solar Photovoltaic System
section | WSA20-MPX-04000-EL-ITC-31152000 - Construction Tests (Pre-energisation)
checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – Inverter)
section | WSA20-MPX-04000-EL-ITC-31153000 - Component Tests (Pre-commissioning)
checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – AC Measurements)
signoff | Checked By (Heyday):
checklist-flat | Communications Cabling | [5 empty] | Testing & Commissioning - Communications Cabling
checkpoint | Cable installed to Manufacturers requirements
checkpoint | Cable Labelled
checkpoint | Cable Terminated
checkpoint | Cable Tested
checkpoint | As-Builts reflects installed Cable Number and Location
signoff | Checked By (Heyday):
checklist-flat | Emergency Lighting | [5 empty] | Testing & Commissioning - Emergency Lighting
checkpoint | Pre-requisite Works
checkpoint | Correct Location & Labelling
checkpoint | Correct Software Mapping
checkpoint | Discharge Autonomy Test
signoff | Checked By (Heyday):
checklist-flat | Lighting Control | [5 empty] | Testing & Commissioning - Lighting Control
checkpoint | Pre-requisite Works
checkpoint | Correct Location & Labelling
checkpoint | Manual Control
checkpoint | Occupancy Sensor or PE Cell Control
signoff | Checked By (Heyday):
checklist | PMCS | [5 empty] | Testing & Commissioning - PMCS
section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests (Pre-commissioning)
checkpoint | Schneider Point to Point Validation ITP - RIOM
checkpoint | Schneider Point to Point Validation ITP - PAC
checkpoint | Schneider Point to Point Validation ITP - EPS
checkpoint | Schneider Point to Point Validation ITP - PFC
checkpoint | Schneider Point to Point Validation ITP - UPS
checkpoint | Schneider Point to Point Validation ITP - EV
checkpoint | Schneider Point to Point Validation ITP - IEM
checkpoint | Schneider Point to Point Validation ITP - eGSE
checkpoint | Schneider Point to Point Validation ITP - GEN
checkpoint | Schneider Point to Point Validation ITP - LCS
checkpoint | Schneider Point to Point Validation ITP - EML
checkpoint | Schneider Point to Point Validation ITP - PV
signoff | Checked By (Heyday):
section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests (Commissioning)
checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
checkpoint | Schneider WSA LV PMCS Cx ITP - EV
checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
checkpoint | Schneider WSA LV PMCS Cx ITP - EML
checkpoint | Schneider WSA LV PMCS Cx ITP - PV
signoff | Checked By (Heyday):