## Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
289fb117-46f9-472a-b07d-e7d5ce5d832b | checklist | ITC 171.1 In Slab - Works |  | ITC 171.1 In Slab - Works
cbe80638-0dfc-4432-946b-4afe77ee5f48 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
9ee5fdff-7f3a-56af-a937-9a15aa750fdb | textbox | Reference and Revision:
af37a30c-4285-55dd-9fd1-2417458c6f97 | textbox | CCT Ref:
2ec69ea9-2635-509d-9002-8d7bb1fefefc | textbox | Pour Location (e.g. Document Gridlines):
02c2ebda-af66-4882-9f38-f856660b048f | checkpoint | No Structural Implications
08876d29-cb79-48d0-bc2f-6dde50cbbf3b | checkpoint | Marked Out Correctly
5fc09cc1-491f-4ceb-98d5-6f849688d8c8 | checkpoint | Glued & Tied Securely
e78a93cc-3672-519d-8cc7-b9f0df0dc325 | textbox | Conduit Size
c086a5b2-0fc0-5c2e-b38f-abae4f655644 | textbox | Approx Lengths of Conduit
3a0eb9d8-7aa2-43e2-99e6-d68e2d3ba4ba | checkpoint | As Installed Drawing Attached
d799ed04-f749-4583-9689-d5d76b6b0082 | checkpoint | Conduit Ends Capped
939a4c1e-c3e0-47b9-a250-cfa4dd8b0971 | checkpoint | Signed off by Installing Tradesman
0f5e3720-0b00-40d5-bf5f-bcc4e1a55a62 | checkpoint | SDC Foreman Sign Off
81678e2e-3459-4835-9f54-69ba1ad3ded4 | signoff | Complete Sign Off
0d1e36b0-2bde-44a6-9ee6-0edf07bcd360 | checkpoint | Passive Fire Sealing
bdf268c4-1d7a-49b9-94f6-927283eb6b72 | checklist | ITC 175.1 In Ground Works |  | ITC 175.1 In Ground Works
99a144de-4e80-42a7-9880-093753ece3a3 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
abd6d3e5-ae04-5cb5-92b5-e167d17834ed | textbox | Reference and Revision:
d1addea9-88a2-53b8-a10f-afaccb4291b1 | textbox | CCT Ref:
89d0bdbe-f338-59b4-a311-7a73dc245c97 | textbox | Pour Location (e.g. Document Gridlines):
102c8c43-1301-4c0d-8ebd-32d113c7cbb5 | checkpoint | No Structural Implications
3c362982-140f-4dc0-bac0-18e347b8adc2 | checkpoint | Marked Out Correctly
656d8394-1459-451b-a24a-12a6f0c168dc | checkpoint | Glued & Tied Securely
f8bf5f0d-5f5e-5097-864d-ec2cc2c5b700 | textbox | Conduit Size
2056980a-2f65-5bee-b27a-e7b7ff7ad352 | textbox | Approx Lengths of Conduit
0f6e526f-75e0-4ccc-be1c-968bdc6e7804 | checkpoint | As Installed Drawing Attached
fe18d372-9b1e-48fa-a0a6-e475551972fc | checkpoint | Conduit Ends Capped
585f361e-9c54-469c-bbec-59ddc9987bc6 | checkpoint | Signed off by Installing Tradesman
dbcc83d2-b2ab-430e-93d8-69e65bd9043d | checkpoint | SDC Foreman Sign Off
7c2f5f9e-14ce-412d-94dd-512416904aec | signoff | Complete Sign Off
68c40800-73b7-4c4e-9ad5-5b330175d91a | checkpoint | Passive Fire Sealing
830f07e4-b6e1-438e-82b1-cb5c568c975e | checklist | ITC 183.1 Pit Install |  | ITC 183.1 Pit Install
303efb75-8877-45ea-92dc-7e86dfa8ed1e | checkpoint | Installed to IFC Drawing
fed40605-ffa8-5151-9f38-96fe730b1a55 | textbox | Lighting Pit Reference Number ID
5ab5f5c0-ab64-459d-a5af-4439688ce7f2 | checkpoint | Pit Installed Correct RL
bba3ed5c-cf99-4163-9aff-09d924364f90 | checkpoint | Down Conductor Identified
0ea30b46-a0c1-4703-8b20-2bc50e8326eb | checkpoint | Earth Stake Correct Length
3b7bc9dc-268c-49d8-b589-acf793ffa745 | checkpoint | Test Link Installed
8ee60c7b-55f4-45d3-8b88-27b46790fd52 | checkpoint | All Earth Cables Clamped / Terminated
ea8527b8-90ac-43a2-9830-d4613abd1734 | checkpoint | Earth Pit Labelled
baf1b87d-62c6-4dd4-b820-89835d2c64e7 | checkpoint | SDC Foreman Sign Off
4204e9ef-8017-47a5-ab59-87542166aec5 | signoff | Complete Sign Off
9c5923a0-5fc5-43f9-9ff8-97d020706b9e | checkpoint | Passive Fire Sealing
e71a73b2-2523-4820-8c5f-19a1cafb2796 | checklist | ITC-167.1 Consumer Mains, Sub Main or Bus Bar Test Sheet |  | ITC-167.1 Consumer Mains, Sub Main or Bus Bar Test Sheet
b88f8eb5-f4c3-451c-8881-c1827347aef3 | checkpoint | POWER IS TO BE OFF / DB ISOLATOR TURNED OFF
f8dda942-b357-5d0e-8c49-46445efc7f86 | note | Test between phases / neutral & earth tick boxes after complete. Install danger tag if required. Should be zero volts.
447d2aad-6a80-547c-afb8-5b0339cf42ee | textbox | R-W
bb5b4e1e-aa8c-57c2-b8e5-095645f54c0e | textbox | R-B
299e461e-aec8-52dc-875d-8733499d4d1e | textbox | W-B
1939e9f1-0b41-5026-a27a-7a79aa8d0abe | textbox | R-E
ac2f0c25-fc1c-5101-ac04-6b7b85c857f1 | textbox | W-E
44f1d7f8-e30d-5627-902e-1ed33c745287 | textbox | B-E
01125511-139d-500b-b2d3-054273fac135 | textbox | R-N
d1018184-20f1-5b1a-b8f7-78beb2616817 | textbox | W-N
1ae41ba4-902f-5d9a-a056-b4da840d60e9 | textbox | B-N
fb3bbf8c-e4cb-5337-8036-5283f85be03c | textbox | Power Off
969ff78e-a894-4318-b1c1-84a899d24cb9 | checkpoint | Disconnect M.E.N. Remove earth from neutral bar. Disconnect for all tests.
93714fde-974a-592a-808f-5e7aae448f4d | tickbox | Disconnect | Yes,No
fea757aa-429b-5cf9-bb5c-6b604315bb93 | textbox | Date:
59915ce9-bca9-5f70-934d-87cbdf8c5573 | tickbox | Reconnect M.E.N | Yes,No
9f0feab6-e712-5c38-9748-20ab8faed8af | textbox | Date:
7d6bab21-ee3b-46df-8c39-6e4d39b89e9b | checkpoint | Resistance of main earth. Do a resistance test on the cable from one end to the other. Make sure M.E.N is disconnected. AS3000 - 5.5.1.4 (Shall Not Exceed 0.5 Ohms)
21ecd97d-6817-5b93-941e-82c8c6ac649d | textbox | Size of active conductor
fe078d2d-3b34-5bc1-b389-7cd6a3ff0327 | textbox | Size of Main Earth
083c4f42-a79a-5f7b-9730-c9e79b864883 | textbox | Resistance of main earth Ω
ff533ffb-8f6e-55ee-bb48-3b30c363c2a7 | dropdown | Pass or Fail | Pass,Fail
bf02a8c0-00aa-4eef-aaaf-fb03bc79bb38 | checkpoint | Insulation Resistance
5dcbd887-3037-550b-8281-b574692a4ce8 | note | Connect earth and isolate cable both ends. Test with Mega set to 500V/1000V between phases / neutral and earth.
5ea0db24-abd1-5f58-8e87-ff272a9fa742 | note | Shall not be less than 1 MΩ
3f10f18a-994d-5e57-8293-b9e480b4ed4d | textbox | R-W MΩ
b1c57e92-000a-5252-bb36-fbccb2fd4d1e | textbox | R-B MΩ
a38301d6-94e0-591b-8eb6-38bb23bdf5ec | textbox | B-W MΩ
aef23b5e-0e18-5ec7-b354-ab696d2cc9cb | textbox | R-E MΩ
a5adb732-ca1f-5ef6-88e4-2118662a3ec5 | textbox | W-E MΩ
2b969c89-c931-51e9-8b31-b9856dbcf687 | textbox | B-E MΩ
3a4f3ed2-5904-5729-93d4-e420859b26db | textbox | R-N MΩ
be30d9d5-7247-59f8-a9e8-2dff01376094 | textbox | W-N MΩ
783fac1a-2ccd-5f1d-90c3-f2d5c1fc40b0 | textbox | B-N MΩ
02ae566c-80cc-426e-9352-6e5daf618bb0 | checkpoint | Polarity Of Consumer Mains / Sub Mains
ef5a6c73-4fbf-5d7f-9fa3-511c02c87b50 | note | Using the main earth or a trailing lead as a reference conductor short a phase one end & test with meter set to ohms across other end. If you get no reading on the meter the polarity is incorrect.
44a2e134-7df4-5d92-87ec-2b029c2773e0 | textbox | E-R Ohms
d1ee2667-ff73-5a38-92a5-2e81381f3902 | textbox | E-W Ohms
84ddb0f1-c99d-5618-aedd-26efa6d70dcd | textbox | E-B Ohms
bfb8a0a6-a11a-5b0f-8d29-e89a16d9bf4f | textbox | E-N Ohms
6da3cb9c-1508-5e78-84f6-ede1dd796d00 | dropdown | Pass or Fail | Pass,Fail
61306a50-edb2-4e9f-9f2f-6d47cf599956 | checkpoint | HOLD POINT - Complete Energised Isolation Permit HSF-042. This service is safe to energise
79e085ec-696b-4b32-acb9-7435eac79895 | checkpoint | Phase Rotation Test On satisfactory completion of above tests, and power is energised, connect phase rotation tester Red, White, Blue leads to respective phase colours and check rotation. Must be clockwise.
64625f72-84ef-4f01-81eb-ef39831dbf4c | checkpoint | Fault Loop Impedence
6bf30f55-dcb0-5968-a23c-0765fe580c50 | note | If Energised, Confirm less than AS-3000 table 8.1 (Zs)
634ed4d9-c1e6-530a-9b52-e9883382a519 | note | If De-energised,Confirm less than AS-3000 table 8.2 (Rphe)
ab3ec110-0131-5a5a-ba0f-3be40b1bede4 | textbox | Reading (Ω)
35f248f3-2ca6-5e59-8e1d-aa4ed7059673 | textbox | AS 3000 Table Requirement
bf47d23b-24cf-5be9-a814-e6f66e769bc3 | dropdown | Pass or Fail | Pass,Fail
6152f378-2b22-4e31-b017-a4e9f3a9f9b9 | checkpoint | Pre-switchboard Energisation ITC-168 has been completed
8638760a-e4d3-4481-b5c8-62fdc79ca7db | checkpoint | Check all necessary drawings available and latest issue.
d9e2e0a0-d179-4b05-a715-eee0c6c520b2 | checkpoint | Check cables of correct size, type & voltage rating is used for wiring.
69142cb7-beee-416e-ba9a-f020e6410aa1 | checkpoint | Ensure correct main switch rating and cabling terminated
927a46ba-0722-42ef-8789-d4736c58138d | checkpoint | Ensure equipment fixed at the correct height. (2000mm switch height max)
183403ad-532f-44bc-affd-954e24881ba6 | checkpoint | Check cable gland is secure and tight on cable
3fc24210-9129-4fda-a36d-446ac6e14685 | checkpoint | Check cable bending radius is correct
74ead0be-b45b-4f1a-b302-f856d612aef9 | checkpoint | Identification & labelling
8a432c7b-40c9-423c-959c-ad0bb1a28042 | checkpoint | Check for cleanliness & for visible damage
454cbc14-da2c-45d4-9e78-963aaf1b42c7 | checkpoint | SDC Foreman Sign Off
f1f4382a-2c5a-4f93-ae0d-5aa730c8e4ca | signoff | Complete Sign Off
161fedae-6d60-455b-aced-cd53eb6287a1 | checkpoint | Passive Fire Sealing
413ea245-c71d-4e4c-af09-97f79d804266 | checklist | ITC-167.2 Single & Three Phase Sub-Circuit Test Sheet |  | ITC-167.2 Single & Three Phase Sub-Circuit Test Sheet
d9803676-1417-432e-9fcc-13acbb0e5a31 | section | De-Energised Test
c4dd04bf-ba24-44b1-a361-118f0de74c91 | checkpoint | Attach any photos or documents
9f9f36e5-2360-53ce-aefd-79d7ecf00f2f | textbox | CB No.
8990abb5-8db4-5b65-9746-1e477abaff9d | textbox | Neutral No.
385e3bb9-1d16-57f2-b4aa-58af17e91580 | textbox | Circuit No.
d398b264-732b-544b-95b4-952e05306fcc | textbox | Cable Size
8ee5750d-0c33-5504-ba72-c23d9e9496c5 | textbox | Destination
83f99a57-e9d6-54e9-b382-fa00ccfe58e1 | textbox | No. Pts
1252f9d1-187f-5ab1-b73e-4f8f4d8849c6 | textbox | Visual Check (tick)
7cf2bdc6-d046-5b9a-8caf-cbb914b47ce8 | textbox | CB Size (Amps) & Type (A, B, C, D)
3f1bd9ec-f5dd-52b7-bce3-050ad35d0f17 | textbox | Earth Continuity (Ω)
37ca0098-8fd0-537a-b438-ee1bc00478bd | note | Insulation Resistance (MΩ)
cf22abe3-14da-5c5c-99a1-b33fcaacab8a | textbox | Red to White
fad61a92-0add-559e-bf7a-a5d102ea6a2a | textbox | White to Blue
3bb2d0ec-6150-5538-91ca-4cc6e116cf22 | textbox | Blue to Red
fe571895-a153-561e-92cc-8770be8f22ea | textbox | A Phase to Neutral
6ecb56bc-7769-587b-84b7-b44ac0b1a91d | textbox | B Phase to Neutral
54e6007f-ed42-5502-a209-9db3e0bbff5b | textbox | C Phase to Neutral
6ea09b75-d939-509d-9957-b9be8e75a1be | textbox | Phases to Earth
76fb78a0-099c-59a9-9fb6-ed8782fd0a95 | textbox | Neutral to Earth
8450ea03-7313-4823-be90-c47ccda57227 | checkpoint | Polarity Pass (tick)
9578d60c-1111-4c94-aa7b-4bfe834621fb | checkpoint | Correct Circuit Connections
c9348e44-b57a-48eb-833b-44b3e8ff164f | section | Holdpoint
ba80a7ea-8b57-4bcd-bf07-3b612f65bbf7 | checkpoint | Safe to Energise? (Initial)
db22dad5-0c96-4812-9958-3ebc1bc8afc4 | section | Energised Tests
0538f401-8750-4f0c-8248-e449b37ec016 | checkpoint | Attach any photos or documents
d0468ed7-a3dc-59e7-ac7b-7775db355edf | textbox | Voltage (v)
87280173-b97b-51ee-a087-648c887ce899 | textbox | Phase Sequence
95e6d834-17b4-5687-b68a-667e92d1c6d1 | textbox | Fault Loop Impedance
dfea5fa8-a88d-5a22-8803-8972efeb0666 | textbox | RCD Timed Test (mS) 30mA / 10mA - 0
9fb45569-967d-5a11-9965-63d05b48295d | textbox | RCD Timed Test (mS) 30mA / 10mA - 180
1d8c1726-d805-48e1-b2d6-96a1c768652b | checkpoint | Label Installed
31be6332-03b5-4318-8287-3457b699ffe8 | checkpoint | Signed Off
00aa8379-df5a-48f1-b663-03f935417910 | checkpoint | SDC Foreman Sign Off
625e63fe-82cf-4989-a797-69608373fb93 | signoff | Complete Sign Off
a3be90c4-b221-41f6-9099-fc5c496cd2b5 | checkpoint | Passive Fire Sealing
c7f9b0ac-79b0-4218-a15b-a97381acf18a | checklist | ITC-167.3 Earthing |  | ITC-167.3 Earthing
ab7d09d6-6dab-474d-96e7-749f46bc94f1 | checkpoint | Attach any photos or documents
70305f45-c830-5298-b06b-c33695f4b956 | textbox | Earth Point Origin
715805cd-cc6b-523c-812b-5bce24ecb0b4 | textbox | Destination
141e0b69-f287-5e58-8899-1f081fde6486 | textbox | Correct Location to Drawing
6ec6cef8-419f-53e1-9eed-44f4f347994e | textbox | Protective Earth Size
e7c7513f-2379-53dd-9049-b83370cdc93c | textbox | Earth Joint Secured
e0556443-e1e6-5865-8fc8-c5f34cc12ce3 | textbox | Continuity |  |  | Equipotential = <.5Ω, General Earthing = <1Ω
a94c6e3b-60ad-476c-83f6-bb9406c03321 | checkpoint | SDC Foreman Sign Off
ff41e0b2-3cca-4ee0-b6cd-5322e55ec58d | signoff | Complete Sign Off
da151e70-b532-4bd8-93cc-40940177b77c | checkpoint | Passive Fire Sealing
9f42502e-eee4-408b-98e1-d5e21168bae8 | checklist | ITC-168.1 Switchboard Delivery & Pre Energisation Inspections |  | ITC-168.1 Switchboard Delivery & Pre Energisation Inspections
18a2ae94-e9c4-488f-b51d-82da25b6b775 | section | Workshop pre delivery inspection
ee6cf967-ef04-437a-81d1-402ba67e6530 | checkpoint | Approved Drawing (#)
de43cbb7-4826-48c9-8cb5-6c0fa987e78c | checkpoint | Workshop Inspection FAT Complete
18900667-89ef-5694-9089-51497f2a1771 | textbox | Approx weight
5657958d-8f97-4f82-8787-b057f3aed4f7 | section | Site installation
30d80897-7403-4f60-b82c-c32d49479aea | checkpoint | Fixed Correcly into Position ¦ Fixing Type
7cb437db-7b48-5166-ab7d-38820467289e | textbox | Seismic Restrained
1696d88c-d907-5d9d-9b64-b19e71a53362 | textbox | Type
c4976412-35cf-4076-936f-090caf111d73 | checkpoint | Clearances
f8bfedcc-9dfc-4701-8ddd-d5753cd67a89 | section | Visual Checks
ecfd4be7-ef0e-4a15-9c4b-07e3aad2ff21 | checkpoint | Obvious Damage, Paint etc.
df22e726-fd33-4e5a-96b0-3bcdf9dc7706 | checkpoint | Internal Clean
ac1e4a52-80ba-482b-92ef-0179576d32c1 | checkpoint | Internal Fixtures, Meter's, CB's etc. Secure
d67ae223-ffe1-49a7-9010-435ef6c9ec9c | section | Tension Checks
6803e739-a866-484c-84d5-09f8082c21c3 | checkpoint | Main Switches
9b25197a-7412-4a81-b930-ebfacea7803c | checkpoint | Circuit Breakers
eb973979-9e97-45e9-8f3f-0d19dd63b51a | checkpoint | Controls
8ffde4a3-0e16-4381-915c-88c984dafe8a | section | Isolation Checks Completed
bfe47b05-d5e5-4ba0-9dae-a1529d477e9e | checkpoint | Main Switches
271f148c-8c2d-41e7-aa66-f98291c504c2 | checkpoint | Circuit Breakers
1e873b1c-57f1-4845-bcbb-322b1f5a8b08 | section | Check Trip Settings & Procective Device Ratings
604875f3-25c9-4e67-a306-8ad2f7f31616 | checkpoint | Fredon to issue Discrimination study report for review and approval
2090daf1-8ea5-41f2-b8ac-ec6748b2a5ae | section | Correct Labelling has been fixed
40fd9ab1-7d7c-4eab-ba51-647078c23630 | checkpoint | Review switchboard as built general arrangement and engineers reports
44f392b3-ff04-48b8-9efc-9f461fa92671 | section | Signage
23c124b6-47b5-42c3-abda-190f08b04d7b | checkpoint | External Doors, Trench Covers & Schedules
762f2dac-0606-44d4-be33-4f6de0109acb | section | Insulation & Continuity Test
078cc8d6-a460-4371-9192-b9fe48f0123d | checkpoint | Insulation & Continuity Test Completed
5076c45f-4d78-45b2-af71-07cc2f5bd2b6 | section | Reinstate All Cover / Panels
510988e0-ffa9-47bd-aa14-c68d0885ab9a | checkpoint | Switchboard Covers Secured
e1c19582-a6cf-4ef4-aa3c-e820335a9832 | checkpoint | SDC Foreman Sign Off
0ca47bac-95fc-4240-ae71-96735b80a0fb | signoff | Complete Sign Off
57011a9b-4c86-4424-b09a-37cc85f37b9c | checkpoint | Passive Fire Sealing
1cef89b8-265b-446b-bf9d-bc5ec7c925c8 | checklist | ITP 169 Mains & Sub Mains Installation |  | ITP 169 Mains & Sub Mains Installation
4f615875-fd8b-4300-ad9c-f327e108c978 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
9919b156-2907-5cb5-baa6-83592534c38f | note | For sub main installation information follow Fredon sub main installation check sheet. The check sheet will have all necessary information such as; cable size, origin and destination. This sheet is to be followed and filled out to verify correct installation. COMPLETE ITC 169.1
34cff115-52d8-44f2-9d7f-fe6a355b0d89 | checkpoint | All submains dressed in the formation specified on Fredon sub main installation check sheet.
8002e059-930d-5fc4-a4c9-f436467a73af | note | When using a winch, maximum cable pulling tensions are not to be exceeded, refer to cable manufacturer's technical data for maximum pulling tension
99676cd8-e131-4ba3-989e-3cbd09008082 | checkpoint | All parallel submains dressed on cable tray/ ladder have been spaced correctly to minimise derating and satisfy all standards specs and regulations NOTE: AS3008 Table 23 & Table 24
91b88223-f33f-40ad-bd96-f44ca2ed90ac | checkpoint | All fire rated submains have been dressed with steel cable ties NOTE: Essential Safety Services require their own Fire Rated Support and cable pathway
a7a9b976-1f52-43e4-83c5-a7571ff0d0e6 | checkpoint | Mechanical protection installed where required.
4fd886d3-b356-4640-9e8e-42258e4f63be | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
441e3950-82ff-490d-9fd7-99bc703d5cdb | checkpoint | All submains have been kept clear of sharp edges during installation to avoid damage to insulation.
ddccd516-f763-4160-8560-0be73afc0613 | checkpoint | Visual inspection of rough in carried out to ensure completion
f78b0a6b-1c0e-4f43-a0ca-692d43c04f9f | checkpoint | All relevant drawings checked to ensure that all services have been allowed for
4d4b2777-9134-4256-a4c8-57d39f6e4bea | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
f1f752be-b6cf-4ea0-8f6f-dce0ba3485c2 | checkpoint | Cross check and verify that the as built drawings are complete and correct
89b8d93c-690c-4c97-a362-f943e97a3037 | checkpoint | Verify all inspections are complete and collate records
97ab5876-bd78-4305-b7d1-28f518cdbeb6 | checkpoint | SDC Foreman Sign Off
f0f4d3ce-7836-41e4-9cf0-45cc8475346c | signoff | Complete Sign Off
7e7c45f6-56fa-46de-9995-e7637bf81d73 | checkpoint | Passive Fire Sealing
ccfb5e51-0dd8-4f32-9092-d8efc07cd88e | checklist | ITP 170 Cable Tray & Ladder |  | ITP 170 Cable Tray & Ladder
1aeff4f7-1dd3-45da-8779-3480ae34deb7 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
119454ed-3068-4842-af3c-4c1b792fbc21 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
ae4cbc99-982a-4c49-b8f1-dc1890d0158b | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
7391ad02-9b9a-4ec6-94b7-e378121848b6 | checkpoint | Correct fixings have been used for the installation of support rods e.g. HKDs, Drop In Anchors. Fixings have been knocked in correctly with appropriate punch tool.
93c7410e-1cd3-4403-be2c-be01cf90f8a3 | checkpoint | Load bearing capacity has been calculated and confirmed - PM to have cable support technical submission to confirm.
e026a9ba-4040-49a2-862d-d9f7f0da9dd7 | checkpoint | For any trays with a high expected load a pull test could be requested and witnessed by customer (if required)
0daa7bff-bdf4-49af-81d9-8574235a608a | checkpoint | Cable tray / ladder has been supported at intervals not exceeding manufacturer's specifications.
5f644317-613d-44b2-94d9-e48550aeb0e1 | checkpoint | Seismic restraints have been installed in accordance with engineered approvals.
b3538510-196f-54df-b8fc-4bbb4e165dfd | note | Has the Seismic consultant been engaged to inspect install and signoff against their design? Inspections to be complete inline with customer ceiling signoff and construction program.
f0db038d-49b5-48fa-ab89-c97cfd8f6669 | checkpoint | Cable tray / ladder has been installed at the correct height in order to coordinate with other services and ceiling heights.
2a2a7400-dba8-48c8-98ee-a3fe4b53f7a1 | checkpoint | Cable tray / ladder, which will be carrying fire rated submains, has had fire rated ladder and supports installed to manufacturer's specifications
07658b8b-9983-48c6-9e75-7c38e8553aa0 | checkpoint | All threaded rods have been cut to a maximum of 30 mm below the fixing nut on completion of installation
9353aa30-7b36-4ccf-bd91-df1648015b72 | checkpoint | All cuts to cable/tray ladder and supports have been galvanised to prevent corrosion
e62297b6-f9a6-49d4-b0a7-81b6b65d0c54 | checkpoint | Ensure the Cable tray has been bonded to earth securely
fc5f2f05-8413-4e06-b97a-fef4314e9104 | checkpoint | Visually inspect the cable tray/ladder run to ensure all above requirements have been fulfilled
6776fcb2-b07c-4b73-9d71-b41687554e20 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawings located in the site office. These drawings MUST be kept updated for use as as built drawings.
a4376eaa-eebf-4286-a182-fe33093d8345 | checkpoint | Cross check and verify that the As Built Drawings are complete and correct
8af4ec66-263e-4fb2-962f-d6dfe1206443 | checkpoint | Verify all inspections are complete and collate records
403729b6-c187-4d6b-9f4a-7ad5290e9b9a | checkpoint | SDC Foreman Sign Off
9a25fcfb-f51a-4da6-8f0a-635b4ef229db | signoff | Complete Sign Off
0f943778-b35a-4395-bfb9-f642c7d0f91f | checkpoint | Passive Fire Sealing
2cb9e0b9-ef8f-4c52-81e0-9ef983289882 | checklist | ITP 171 In Slab - Works |  | ITP 171 In Slab - Works
32507242-5828-4573-ba28-5da20fb7e3dc | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
652a8861-29ee-4d9a-8de2-1a14d053b081 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
487b1d83-419d-5117-b381-5de296d75c77 | note | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
e17f8c29-e94b-4ab9-9c5a-59f4adb72e33 | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
2640487a-11f1-4c82-932e-f2dcbe6202f7 | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
b2a49552-5925-4a8f-9b8d-7ab3e3696014 | checkpoint | Engage certified surveyor for critical set out works
8684bd13-1dda-4031-a868-f43bc009b4aa | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
989cd199-582e-4357-a284-9e0c96dc3db2 | checkpoint | Conduit to be measured and cut using correct tools
be7f5afb-0c1e-5685-af55-dfebb0d475a6 | note | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
cccf38cc-5628-5a83-90a7-a4ed62857e53 | note | All joins to be glued using PVC jointing cement
0d65c222-a4fa-5690-98d5-66421ec4a559 | note | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3way T, 4way
d1a71981-d002-53aa-816c-0b7914432652 | note | Do not use corrugated conduit in decks
53c17039-43dd-441a-876c-56e37b33bb3c | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
9bba34c3-945f-5e1b-a27b-3003b5ae2c43 | note | Conduit should be tied to bottom mat of steel
e1ec545c-0501-4937-967f-92caf3b20ffb | checkpoint | Ensure conduit installation is supported from deck over entire length
d23e9fc4-7fc5-569a-8b24-84100aeeda15 | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
70b52ebb-fa2e-474b-a79f-78c79f0d5aaf | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
5562785d-a677-4b7e-a484-22780dc8d2cd | checkpoint | Ensure sufficient concrete cover can be achieved
9b18a6f4-d982-4545-b14d-285180494ce1 | checkpoint | Complete as installed conduit drawing showing all conduits. Photograph area of works.
c4cd4c20-2884-4471-82bc-d1bb16bb404c | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
1ccb4434-f897-4c69-9f38-81b58fa49688 | checkpoint | Observe concrete pour with particular attention to critical area
d165bc7f-fcbb-4cfb-b9c0-ab72280bd765 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
7b4582cb-2d41-4c89-ae04-7278d3c861f4 | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
33c6ee3b-d67c-4a7b-ab71-5036a1f677f6 | checkpoint | SDC Foreman Sign Off
177040ec-19eb-441b-8af3-5587fababe1a | signoff | Complete Sign Off
4e875c03-0a07-4e88-ace2-989b0b3a8014 | checkpoint | Passive Fire Sealing
25460a31-5230-462e-b365-f11603a2db57 | checklist | ITP 172 Light & Power Rough-In |  | ITP 172 Light & Power Rough-In
46ba36d5-bd67-4e57-9600-b68399a26df0 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
34b513d5-3dc9-414c-8e52-81509234ae54 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
5da35605-b432-4cd1-8a41-01663e54ba5b | checkpoint | Ensure that the latest service drawings are being referenced
44710e88-63d0-45a5-b5e3-8a03fc744904 | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
1e79f5a6-1a91-4bcb-931b-eba9916008f8 | checkpoint | Cable locations marked on floors and walls, if required
92a750b6-d84e-435c-81a4-17c80e72ba91 | checkpoint | Cable locations marked on drawings for ease of locating where required
4c215130-cf16-42de-b7f1-7713b75511d7 | checkpoint | Surface conduit correct size to house required number and size of cables
785c76f1-ec46-4c9c-aa35-12b851e481fd | checkpoint | Surface conduit fixed correctly and all required draw boxes installed
bc14bfa0-76bf-40d0-9126-427c431e45b6 | checkpoint | Ensure that no PVC Conduit has been installed passing through fire rated walls, breaking the integrity of the fire rating.
b0c4b5ba-e399-4b6e-b4a7-9195c5b3041d | checkpoint | Ensure that steel conduit has been installed in areas where mechanical protection is required or where called for by the project documentation.
d756af4d-90f0-46c9-b497-7794cb7f20d4 | checkpoint | All surface conduit installed in a tradesman like manner.
0dcf6334-733f-40ec-9c40-8b894e24ba49 | checkpoint | All penetrations are sized correctly
de383bf6-54fb-4200-8596-73f5b2d350b9 | checkpoint | All penetrations are sprayed or painted with galvanising paint
0aa10326-93f3-493e-a577-bb2c5af9a047 | checkpoint | All penetrations are bushed to prevent damage to cables passing through them
644c6073-a2f2-40c5-b02c-735ea30d9dfc | checkpoint | All penetrations are sealed to prevent the ingress of insects or vermin
47e13bda-0f4a-42a2-a371-61c2b8c5b703 | checkpoint | All cable sizes selected correctly to suit the size of the supply required and to satisfy all standards, specs and regulations.
d947bc5f-ffd4-4434-b043-8f2b3266a860 | checkpoint | All cable sizes selected correctly to allow for Voltage Drop due to excessive cable run lengths to satisfy all standards, specs and regulations.
eb834bc2-f1ce-4c37-b821-7a6734c95b6c | checkpoint | All cables fixed or supported correctly to satisfy all standards, specs and regulations.
1dcc96d4-a2a9-4e60-95ed-abef19e512f3 | checkpoint | Mechanical protection installed where required and minimum segregation from other services maintained
a5a9a83f-8269-4266-9610-48fd83d47a0c | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
68f78b31-efb3-4b62-8bc5-c2b7b54232ef | checkpoint | All feeds are marked and checked from the drawings to ensure that none have been missed.
577a7a5b-16da-4519-bb2e-3a139907a933 | checkpoint | All cables are marked with their circuit identification numbers at each point.
7df94d34-6980-4799-8fad-180e98ab3f31 | checkpoint | All cables installed on cable ladder/tray are dressed and spaced correctly to minimise derating and satisfy all standards, specifications and regulations.
dc1e6997-9612-5d26-90ec-672a9a57eddf | note | Do not leave any cable ends exposed / bare. Fredon Policy TWIST-PREPARE-TAPE
82b3da9c-1d6f-435c-b3d7-2c27390d535c | checkpoint | Visual inspection of rough in carried out to ensure completion.
f346ad75-9213-4fa8-a7f3-3c96b8774b74 | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
db45de5e-39c8-4e5d-85b3-5d349476064a | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
920ffb5f-b963-4a35-a29b-fbb18aacf917 | checkpoint | Cross check and verify that the as built drawings are complete and correct.
5d975062-99a8-4ae1-bd1f-2181e0367796 | checkpoint | Verify all inspections are complete and collate records.
be0f41be-f4db-4387-a599-b064c032c9ff | checkpoint | SDC Foreman Sign Off
c4bcefae-ccca-49a9-9411-9b1c1de3d044 | signoff | Complete Sign Off
b7e4465a-4321-4292-9ccd-0f421f49b63f | checkpoint | Passive Fire Sealing
687f30d4-ffd8-4991-9e8c-996ccc7c341f | checklist | ITP 173 Fit Off Light Fittings |  | ITP 173 Fit Off Light Fittings
ade27e60-d244-4453-aa40-2c0c60b0e7ed | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
f066451c-9aa3-4f23-8d53-411b08df1777 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
0ea42a76-51d3-467f-8d1e-444dd313be36 | checkpoint | Ensure that the latest co-ordinated service drawings are being referenced
7ac33ca8-a51d-4731-8879-ec9c47b1106b | checkpoint | Ensure that the latest co-ordinated drawings are being referenced Not Required
e66badb7-f38c-51ff-a4d7-67fd774e1c6f | note | Understand physical characteristics of light fitting to be installed. Recessed fitting cut out dimensions. Lineal fitting lengths v fixings. Height of fittings. Architectural requirements - light spill direction
5ac8ff28-1e82-4237-a4ad-4c7072530b87 | checkpoint | Ensure the fitting is compliant with Australian Standards
854f77fa-7594-4bb0-959d-5740cad30dce | checkpoint | Install fittings as per manufacturer's recommendations
fdea0450-7a2f-4ab9-99c4-6c92bc6dd16c | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings
54eeb41f-33ba-4b85-80b3-619d27cf5444 | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
aa750693-ec51-4d80-b4b2-0225cad8434e | checkpoint | Ensure fittings are installed using the correct fixing type
b2e4150d-cced-4d2a-94b6-f7baf61786c7 | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
d1df3a9a-3c51-4637-89cf-b95c00379a77 | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
86f1ace2-ef0d-4ede-b4e2-c152810a5306 | checkpoint | Ensure that all terminations are correct including lighting control terminations and are as per manufacturer's requirements
9778cd09-7ce4-45be-a3c3-df3ae722253b | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
0cf52720-2bef-4b7b-b700-f551c76693f1 | checkpoint | Install fittings as per manufacturer's recommendations
813cbeac-7695-445d-9286-d59e21d7a6c1 | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings and visibility of escape lighting meets AS 2293. NOTE: Directional arrows show correct path of egress and the luminaire has the Emergency label attached
e15f41a8-c3ea-469e-b674-d72550886137 | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
5d400545-1c88-4d44-859b-2f0e699b9728 | checkpoint | Ensure fittings are installed using the correct fixing type
966baa13-9a70-4150-981c-1b0d66e92526 | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
d4bd8c54-9386-4f54-9f89-49e0670182ea | checkpoint | Ensure that all terminations are correct including monitoring terminations and are as per manufacturer's requirements
49b458b1-2b29-4ecf-8c81-c6f5ea3b0f97 | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
24cadd28-e0a1-4a46-836e-93c82e1ef339 | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
edb0e902-ff66-4b31-9c1b-3402449e0d86 | checkpoint | Ensure all emergency lighting information is kept on As Built information. Fitting number. Circuit suppling fitting. Fitting serial numbers etc.
700633b4-945d-4bc8-80fc-a51666bb62a6 | checkpoint | Ensure that the lighting control philosophy is understood. Cable requirements. Cable polarity. Cable connections.
4e5ef87f-636e-42d0-abb7-e5702fc8a00d | checkpoint | Ensure all fitting information is kept on as built information. Fitting number. Circuit supplying fitting. Fitting serial number etc.
34edade0-9678-4313-8e11-4291334ce735 | checkpoint | Visually inspect entire circuit for completeness Ensure fittings are protected if required Remove all rubbish - empty boxes etc.
1fac6c23-bf39-4dcf-8242-0a6a956e39c8 | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
1abd2b0b-fe5b-4988-8ac8-11e0bf2de93b | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
258f5de0-0d34-43e5-aaf6-d7464f996b31 | checkpoint | Verify all inspections are complete and collate records
44fcba38-3841-451b-9e58-bfc5fa96717c | checkpoint | SDC Foreman Sign Off
c6e7c540-ada0-471c-ab74-7105c1820e99 | signoff | Complete Sign Off
a8232eac-56da-43d9-9ac3-8e16a0b2c25e | checkpoint | Passive Fire Sealing
3758dc77-e4f3-42d1-a79e-5d1b089032f2 | checklist | ITP 174 Fit Off-Power, Switches & Accessories |  | ITP 174 Fit Off-Power, Switches & Accessories
fd9f944f-9a4c-4405-8817-481f2bed33f9 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
632cd9b3-e1e7-4c7b-8731-f44af0bc23da | checkpoint | The Updated / Superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced.
687c65aa-edd5-49b6-a845-c1a184ebadc6 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
21bd8fd3-915d-48c2-b85f-4738aa1283b9 | checkpoint | Ensure that the latest service drawings are being referenced
25123b85-99d7-4925-8f4c-c6b6e34cb2f7 | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
d9becd7b-a090-4103-8255-011a6b49d114 | checkpoint | Ensure all required distances are kept from other services as per AS3000, e.g. in damp situations
602d42e1-c1c2-4e43-9bbd-5429fc113ee1 | checkpoint | Ensure the fitting is compliant with Australian standards
b3c89fa9-ad3b-43e3-bd95-9f4e289dc9ba | checkpoint | Install GPOs / Switches as per manufacturer's recommendations
5338f43a-5b45-4f2d-9593-05ae204c1e01 | checkpoint | Ensure GPOS are installed using the correct fixings and brackets
de36bce6-ad79-417e-8260-8df91f3941f2 | checkpoint | Ensure the correct item is being installed at each location prior to fit off (Current rating and Phases required)
39e50f56-ef9a-49b1-ba65-7985173e6267 | checkpoint | Use fire boxes, acoustic boxes etc. where required - if in doubt check with the site manager
68375d9b-c2bc-4013-8805-d8dff4843df7 | checkpoint | Ensure correct weather proof fittings are used where required
6547a834-e4d0-43c2-922c-c323217e1e78 | checkpoint | All switches and GPOs are installed in a tradesman like manner, e.g. level
aac09d09-f4da-4e8f-90ff-e8c65a152ad4 | checkpoint | Ensure all Sensors and PE-Cells are terminated correctly and switch the approved lights. They should also be installed in a position that will not obstruct it's ability to function correctly.
4ea77fc9-57f7-4941-a70c-5b5ea7a5df55 | checkpoint | Ensure all ELV smart/programmable switches have been terminated with correct polarity and to manufacturer's recommendations
991529ad-8fe3-4d45-8ff2-114681369ec8 | checkpoint | Ensure that all penetrations through the steel structure have been properly bushed before fitting off item
ae37a3ea-8290-4def-a724-7ef726bf92e0 | checkpoint | Bushing installed is not able to fall off over time
4fc826cf-8f61-4e38-af61-c541204285dd | checkpoint | Penetration is sealed to prevent ingress of vermin before fit off where required.
f8c1ddc7-0352-476f-99af-bbc016c5ade5 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built Drawings.
84fe1a56-f778-4d67-a1b9-00346ab5fafe | checkpoint | Visually inspect entire circuit for completeness.
8e4ecde3-deb8-417c-91a8-35b8ffd922b5 | checkpoint | Ensure fittings are protected if required
39cf408f-a37b-450e-bc11-fcb2c916ba8a | checkpoint | Remove all rubbish - empty boxes etc.
0080f8d5-ca02-453e-90ad-a25c08e61c0c | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
5dec80a2-36eb-4e07-ac56-de6d68ecdff4 | checkpoint | Cross check and verify that the As built Drawings are Complete and Correct.
fa4ca507-5cfd-4abd-894a-e1af5c59792f | checkpoint | Verify all inspections are complete and collate records
caf6931b-ebef-4ef8-be64-8f63a5c66f16 | checkpoint | SDC Foreman Sign Off
e1dd6133-4c31-4bc2-9627-572a08f55a60 | signoff | Complete Sign Off
bcad97ee-2f88-4ef0-8ae1-3ee10f233e94 | checkpoint | Passive Fire Sealing
5b5f8cda-1599-4db1-bb15-cb4768e52237 | checklist | ITP 175 In Ground Works |  | ITP 175 In Ground Works
cb40078d-0fe3-4f1e-8e64-d2e0e6bae022 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
f7f33e2c-3bc6-42da-b7a7-dd6efcf1b9a7 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
7cb9f505-ab1e-5315-9615-861cfe58b701 | note | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
1079b17c-fe19-40a4-8017-c138844b288e | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
db918d33-7600-4098-9d87-bfc1abb91c61 | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
90399a29-c147-4f99-b1f6-c8c767867cd6 | checkpoint | Engage certified surveyor for critical set out works
8a7fa076-262c-478e-9075-fca7cf015942 | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
5268aaef-4c22-4bf9-968a-8d6bd53b2311 | checkpoint | Conduit to be measured and cut using correct tools
24828341-9eea-546b-8487-c72792ff7d11 | note | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
c7ab69e8-b254-5540-8e56-bdcb07d6e981 | note | All joins to be glued using PVC jointing cement
2b60f04e-20d2-58ad-9ccc-832bfcc6a9fe | note | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3way T, 4way
add6368e-44b5-5546-bcaa-1791492677e0 | note | Do not use corrugated conduit in decks
1ffb4319-08ef-4ee0-9149-06895884b9ff | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
f2742dbb-6d89-551b-a7ae-cbd5a1853e34 | note | Conduit should be tied to bottom mat of steel
9edbba28-b90b-4a02-a5b5-46ad31aa9033 | checkpoint | Ensure conduit installation is supported from deck over entire length
a801afee-275f-57d0-8aab-6aa89253712e | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
6f449c82-bc25-4874-aef7-30d06f19f455 | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
9627d2fc-6395-4f8e-b0cf-0c4a6027b61f | checkpoint | Ensure sufficient concrete cover can be achieved
e2a9a7f9-27e2-4b56-8a3c-f5e3eab7508e | checkpoint | Complete as installed conduit drawing showing all conduits. Photograph area of works.
c5a52ad5-a63c-46bb-bfa6-df75c0d85dc5 | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
1bce793b-9d24-4c6a-a0ca-fda859d55c9d | checkpoint | Observe concrete pour with particular attention to critical area
dfd88d43-2f50-4fdd-81c1-2a1314d15c07 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
611fb298-8c86-4beb-9d25-8a137e8abe56 | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
2a8361ca-31cc-4bb7-881c-f7e4c9eff6eb | checkpoint | SDC Foreman Sign Off
ddf16652-73f4-4085-9447-0f560b4c27f7 | signoff | Complete Sign Off
20724f8e-8ae3-4110-859d-cc3e3eab041d | checkpoint | Passive Fire Sealing
539e4dad-1e78-4143-952d-912092be7c95 | checklist | ITP 177 Horizontal Cabling |  | ITP 177 Horizontal Cabling
2e39061a-c908-4e7d-8882-c71f9e39ba0e | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
ee68f6c9-19ff-4eba-98a7-cd63056de8d5 | checkpoint | The Updated / Superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced
d0b48181-1787-4ddc-8966-a7d1d3cf9311 | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
0d591ccc-5df8-4d32-82a4-8f8888fdfa84 | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
5fd6119c-fd36-524a-8da3-5076aa3c679c | note | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
0177650e-58cc-4352-b128-e8051b245026 | checkpoint | Ensure that the latest services and co-ordinated drawings are being referenced
aacd344e-5a2d-4d9a-bc66-1dbf4f52cb12 | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
b8d7abe5-247e-4fd3-a466-d257e77de71a | checkpoint | Ensure the cable does need exceed manufacturer's bending radius and is segregated to other services as per AS S2009:2013
13f7f3cf-f2f3-451f-af0b-09593113509b | checkpoint | Ensure the cable has adequate support and the pathway is less than 90 m including service loops & goose necks before drops
05882822-e1ee-4c89-a18f-23d5f16ae6a1 | checkpoint | Visual inspection of rough in carried out to ensure completion.
3d83993b-fca1-4409-b481-6c0621465bc2 | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
bf0034b1-0aba-4f81-904b-653386578cf5 | checkpoint | Ensure Cabinet Layouts are installed to the latest drawing layouts with door swing and clearances considered
a1184d78-5306-4963-9662-fbe833482ae4 | checkpoint | Ensure cabinet is secured and and all accessories, panels and management installed correctly to latest RU Layout Drawings
9e628ab6-acfd-48a5-af27-8301ce4ed1a1 | checkpoint | Ensure all shielded equipment is earthed and the electrical contractor has supplied an earth with a maximum resistance of 0.5Ω
a46976bd-4630-4308-b39e-7240f20a2573 | checkpoint | Ensure that all Field End Cabling has been labelled, terminated and is level to other services
b9be355d-660a-4f75-867c-4a0323c5bf38 | checkpoint | Ensure that cables are bunched into their final looms and dressed throughout the communications room to individual patch panels
78fd58b3-e1fe-4a99-a507-da87abed041a | checkpoint | Ensure that all cabling is terminated according to communications rack lay out drawings
97614a61-a228-4930-a7ab-bd21918274b9 | checkpoint | Ensure that all cabling is terminated has been labelled
99d35590-9160-4c20-b7b6-61abe2491504 | checkpoint | Ensure that Fluke DSX Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their correct label on cabinet and latest revision drawings
21decd5e-3ad4-4fe4-9dde-f80dfc9d11fb | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
90da26d1-5276-4618-8296-b04787c160b1 | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
2e2f556a-1850-4ae8-a9ab-38ae69fad0d8 | checkpoint | Verify all testing are complete and collate records
33a1bcc3-e606-4156-80b0-27850791df81 | checkpoint | SDC Foreman Sign Off
8e9e097f-075e-40fc-8739-996a7b78bad8 | signoff | Complete Sign Off
f22e3151-c972-4aaf-84f4-94d390c69c50 | checkpoint | Passive Fire Sealing
2eddc9a4-eaef-4afb-9e2c-d3cae5283a42 | checklist | ITP 178 Lighting Control |  | ITP 178 Lighting Control
8d8e88c8-542e-44b9-9b0c-6ae0585c2e0d | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
2b2be054-9003-4e9b-b826-e4e5a2a18040 | checkpoint | Ensure that all installations have been coordinated with other services, both new and existing
cca3369e-e5d6-48b2-9334-d5eb50305705 | checkpoint | Ensure segregation is maintained pending cable insulation and shielding ratings
79f2bd36-dedc-489e-af03-7d7ee4266ca5 | checkpoint | Ensure cables can communicate the specific protocols over the distances installed
035f438f-863e-4989-8a29-192db50c474e | checkpoint | Ensure not exceed the maximuim number of devices per group
620d5327-bb8b-4212-86e6-b725eb59455a | checkpoint | Terminations have been performed according to the manufacturer's requirements
0ef6ed02-7f72-43cf-8d91-47b2fad8e5b6 | checkpoint | Test for voltage on the dali line
0cca8709-1bea-4134-8007-5050164c3259 | checkpoint | Test for Short Circuit on the dali line
9d14e667-3dcb-4c06-9f5e-c0fc62bf9ef1 | checkpoint | DALI flash each individual line to confirm all lights are communicating correctly
9e2d6c22-57bc-44c3-9b86-c2d8f4c8c1be | checkpoint | Test for voltage on the communication cabling
0251147e-46db-4495-97ca-cc43d8b9a3eb | checkpoint | Test for Short Circuit on the dali line
bd1c94ed-07a4-4b24-aec3-dd9c94690bce | checkpoint | Scan communication line and confirm all devices can be programmed
b732e17c-cfa7-46e3-9407-171b9e8c3062 | checkpoint | Address all DALI drivers/light fittings with their fitting ID number and update drawings
e9ece87f-e76d-4a6e-b008-8f40c7df9e4b | checkpoint | Address all devices/inputs with their device ID number and update drawings
a2c0a3d5-44c5-4cb4-b375-8c8dc79a2231 | checkpoint | Setup the the relationship between devices/ inputsand light drivers.
898267ca-dc80-45d8-a797-ddb93d2d0e67 | checkpoint | Program all Touchscreens using the approved graphical interface as per the clients requirements
59cf870b-4747-49ee-92c1-bca1b3417e5d | checkpoint | Confirm all lighting and switches functions as per the latest specification, technical submissions and drawings. This may include Dimming, Motion, Lux, timing parameters etc
cfbe1499-473e-4c9a-81b5-645e4215199c | checkpoint | Program Head End PC/ Control system and backup all information for future maintenance and rectification
5bbf0a35-3a1d-45c4-b36e-b93e5e095df2 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
8663192c-2d52-4012-b871-79c0a6a9d8a3 | checkpoint | Cross check and verify that the as built drawings are complete and correct.
899178be-5902-4aeb-8781-024e23f97000 | checkpoint | Verify all inspections are complete and collate records.
814a95bd-c0df-4900-bb8e-bb5dfcca7824 | checkpoint | SDC Foreman Sign Off
4dc3e23e-f5c7-4408-ab31-8eba52bf4b27 | signoff | Complete Sign Off
457d5b85-0bd0-45c6-ac29-9e5192571233 | checkpoint | Passive Fire Sealing
1786c2dc-0e43-48d2-bd80-dc91f6098fd3 | checklist | ITP 180 Control Cabling |  | ITP 180 Control Cabling
e02dad76-81d6-4716-bedf-9ea35c76f2b0 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
2abbae36-bbc8-4250-866c-a59940a02b9e | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
1ba00e46-7e8d-4018-8c9c-2dbb63c2d455 | checkpoint | Ensure all control circuits are designed to function under the necessary circumstances that they will be required to function under
5a3792e5-ff18-4cca-b50d-aaca6415493c | checkpoint | Ensure segregation is maintained pending cable insulation and shielding ratings
aec2c132-a2b0-4e97-a93a-e06164204182 | checkpoint | Ensure cables can communicate the specific protocols over the distances installed
c32e711f-37bc-4e25-af4d-9f5e5584f1d3 | checkpoint | Ensure the correct amount of cores have been supplied
d313ce64-a4c5-4408-b4c4-1530a4ac9f12 | checkpoint | Ensure the requirements of the system and if it requires to be normally open/ normally closed for the control/status that is required
149d9c86-181e-48f6-acd1-cebbc604cd20 | checkpoint | Ensure all spares are left in an open state and labelled accordingly
40e895fb-d916-41ce-a1cb-733c7371e602 | checkpoint | Ensure cable/cores can be easily identified for future works and maintenance
7930c414-574d-49bb-bb54-cf4f365a4a26 | checkpoint | Low Level Inputs - Point to Point test individual cores at both the origin and the destination
1e579568-629a-4245-b3c0-020c292ebacc | checkpoint | High Level Inputs - Confirm the software can be seen on the head end system
24682c68-3d3c-4088-a47f-84d08d29ff57 | checkpoint | Activate functional devices and programming and confirm that the control system functions correctly eg. Manually Pressing Emergency Stop - turns off designated equipment
422499eb-1af9-442c-89b7-20a46209d433 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
ad20a666-ced9-45a6-89bc-246682a671a4 | checkpoint | Cross check and verify that the as built drawings are complete and correct.
e184caf5-96ab-48e4-b0d3-7f21cdc789cb | checkpoint | Verify all inspections are complete and collate records.
c82ce7ab-ec36-4a81-9efa-c40c5d295c2a | checkpoint | SDC Foreman Sign Off
e7a84308-a7e5-4e0a-a268-32c5912e5aaa | signoff | Complete Sign Off
e54b8d4e-d08e-4425-9d32-b69dd79f1a94 | checkpoint | Passive Fire Sealing
4981da4c-9012-450e-9c4d-4c5b793298c7 | checklist | ITP 181 Fibre Optical Cabling |  | ITP 181 Fibre Optical Cabling
366d7e73-fd70-4c59-a54d-54b6efe657fa | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
13e6982c-e511-4792-b849-1da2eee19b38 | checkpoint | Ensure all test equipment including leads have been calibrated within the previous 12 months.
fd6fca14-8b5d-4314-9a93-10c0238e3fbb | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
a6f525bb-ab66-4d7d-9d94-ee43f679e97f | checkpoint | Ensure pit and underground piping are clear of obstructions and have the appropriate access and barricading
1693f631-6d84-4514-80b9-3675e3191c37 | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
82c5a78f-e1c0-4905-b76f-3b6c8497a5f1 | checkpoint | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
324a4f4f-83e7-4d13-85b2-a333225e5c98 | checkpoint | Ensure that the latest services and co-ordinated drawings are being referenced
03d5fd4a-bea5-4bee-8a5d-97420502e9c0 | checkpoint | Ensure the cable does need exceed manufacturer's bending radius and is segregated to other services as per AS S2009:2013
9d446b02-324c-4239-ad20-8fc5f1b49b01 | checkpoint | Ensure the cable pulling strength is not exceeded as per manufacturer's recomendations
210c16b5-ead4-4352-ab82-165cf50fe473 | checkpoint | Ensure the cable been loomed in neatly along cable pathway and has adequate service loop's at both origin and destination
5454e257-d37f-4c3f-b84c-79e932274ac7 | checkpoint | Ensure the area for splicing has the appropriate workstation and is in a dust free environment
9a330634-7abc-565e-91d8-27e169ed6899 | note | Cut the last 2 meters of the fibre and remove it to avoid any dirt, or damage from the hauling that may have taken place.
1f7d374c-2605-4ef7-9402-03361ffb309b | checkpoint | Ensure the cable is stripped using the specialised tools and remove all Gel using telstra wipes if applicable and secure kevlar rope
2b7d50ca-07b7-45e8-8ba1-1f1cf5ca5031 | checkpoint | Ensure all equipment (cleaver and splicer) has been visually inspected, self checked, cleaned and regular servicing has been maintained
52c1a5a6-abd4-44dd-afcf-5b510c74cd23 | checkpoint | Ensure all splicing follows the correct sequence and any cut off shards are accounted for and disposed of correctly
82734673-6e76-4f5a-9bfc-dfbb8196790d | checkpoint | Ensure fobot is securely placed inside enclosure and dust caps installed
30dcabd7-dbd9-4b6b-a0fa-454a18c91712 | checkpoint | Ensure that OTDR Testing is taken from both directions and at multiple wavelengths and all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
2246262c-f30d-4099-abde-cd4994189d96 | checkpoint | Ensure that Light Source Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
598fcbf7-ce9a-4d20-bc15-2b84eace4b84 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
6d204683-c316-44ff-a4f1-b9f0c82fce26 | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
a83bdcc9-1d67-4428-a85d-dddd826e7b12 | checkpoint | Verify all testing are complete and collate records
cf0ab8e8-8931-460d-bf70-8207e024c743 | checkpoint | SDC Foreman Sign Off
2ba90c3c-0d62-495c-96e7-5e8219d0a167 | signoff | Complete Sign Off
1c9d545a-64db-4947-9b41-57aaa66a4cb1 | checkpoint | Passive Fire Sealing
9cccf8bc-0247-4696-8785-8dd52782df8a | checklist | ITP 183 Lighting Protection |  | ITP 183 Lighting Protection
7f8a8f3e-26ed-4b88-9cc4-b349582bc1ed | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
476ffd97-08e5-41a5-bf32-a3bcd883188a | checkpoint | Ensure that all installations have been coordinated with other services, both new and existing underground
a03d4c2d-d35d-4cd5-bdaa-a4be5a2a7177 | checkpoint | Ensure the distance of 20m between Lightning electrodes is not exceeded and that all external corners of buildings are protected
abd2a372-22f6-4312-b11f-095e7626af25 | checkpoint | Ensure down conductor is installed in the most direct path practicably possible
e5577b05-13d1-46ff-9c65-fd6a532557b0 | checkpoint | Ensure all conductor sizes meets the minimum requirements as per AS 1768 Table 4.6
f5705eda-3e13-41b6-bf16-c5a375a6bd06 | checkpoint | Ensure each Down Conductor is fastened securely to the engineered attachment point
d3864ef7-6608-4ba5-b318-244726ad3a96 | checkpoint | Ensure pit is installed to correct RL's and not above other underground services
89830556-ba03-4f94-8661-6d50beb74971 | checkpoint | Ensure Buried earthing conductors meet the requirements of AS 1768 Table .6
e2558021-ed06-4309-804b-710e8b94a9da | checkpoint | Ensure the correct length earth stake is used
68b900b3-3918-43ef-a5a0-4e268f61ebef | checkpoint | Ensure all earth conductors are correctly lugged and Identified
98d3b34c-de0f-4894-bc16-3ec739afebec | checkpoint | Ensure all earth conductors and fastened/clamped to the down conductor securely
3f69b71a-b347-4a8f-80df-f7a8186ed014 | checkpoint | Down Conductor Testing - Project Specific Testing Requirement
ca0b8920-f0de-401c-96ef-513028f2e5a5 | checkpoint | Ground Resistivity Testing - Project Specific Testing Requirement
f3c64230-1697-40c2-ab45-271df18bb4f7 | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as built drawings.
ec335ab3-37c0-4f20-a214-4c245e8b8a2b | checkpoint | Cross check and verify that the as built drawings are complete and correct.
fdf50805-9c22-4cd8-b2a2-f1d8256ba7d7 | checkpoint | Verify all inspections are complete and collate records.
a52b2a58-7134-413a-b46e-717cdbe65475 | checkpoint | SDC Foreman Sign Off
5b62c0ed-09e0-498e-90b3-2d18aa47c6a9 | signoff | Complete Sign Off
6d94096b-9f8a-4607-bf89-aef602e1c415 | checkpoint | Passive Fire Sealing
6e8013d6-0fde-421f-ade7-09194c13fe2c | checklist | ITP 184 Lux Measurements |  | ITP 184 Lux Measurements
4e5f70de-20d6-42f3-99a0-c3e9ef282962 | checkpoint | Ensure that the lighting exceeds the minimum requirements and meets the design criteria
e2ad7d2e-f657-4d6d-9bd9-fdce0bb4ff42 | checkpoint | Appropriately set out the area in a grid
abd57b1f-0c03-4dd5-bcf6-0f4d367d6078 | checkpoint | Visually inspect the light meter and confirm the the calibration has not expired.
11849362-dfbe-47ef-ae8e-b8ce4df6f949 | checkpoint | Architectural requirements - light spill direction
58cd55ca-5093-4037-b3f9-8b93e70988c1 | checkpoint | Ensure the Light meter is pointed directly at either the light source or the viewpoint/camera in which the light levels need to be recorded
2639c5d9-42ec-4583-87ff-0b58d1085c29 | checkpoint | Ensure all readings are taken at a consistent height and at the relative intervals to the grid setout
386ae841-fe72-429c-bd56-f5159f1b88e2 | checkpoint | Ensure the Light meter is perfectly horizontal and no shadows from the technician are covering the meter
bc7a1f20-98d6-4a46-9d3e-d658c47edb49 | checkpoint | Ensure all readings are taken at a consistent height (Normally 1500mm) and at the relative intervals to the grid setout
0bee8779-0e10-4239-a25e-458f886dcf8c | checkpoint | Record all information & verify the Minimum and uniformity requirements
0b7e25e3-e650-4a3a-98df-dd1443f3175e | checkpoint | Verify all inspections are complete and collate records
287f714f-e14f-4db9-ab42-64895fa3d561 | checkpoint | SDC Foreman Sign Off
d2a7bbc8-854a-418c-961c-5d9e872ad166 | signoff | Complete Sign Off
3be4094d-4894-4eca-9e93-033ac62ed393 | checkpoint | Passive Fire Sealing
a6c85981-98a0-4101-8bff-928fa33b3ade | checklist | ITP-168 Switchboard Inspections |  | ITP-168 Switchboard Inspections
52d432c8-90d6-4d9d-8206-bb2f7ce42436 | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
9708c654-ecb2-424d-9dd9-f465e00152f5 | checkpoint | The updated / superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced
87e6a1f2-b721-49e1-a166-1527ce72446a | checkpoint | Ensure the switchboard drawings have been reviewed and approved by the consultant
72edb533-e8c5-4e06-aa2f-79d3924ed9fb | checkpoint | Ensure all new installations have been coordinated with other services, both new and existing.
4526a30a-4224-4ff7-a150-651a44feea69 | checkpoint | Location & Position of Switchboard
abe75b12-1f36-4ace-9145-8cde3cc08658 | checkpoint | Supply Authority Access Requirements
d5afc92e-ebe7-48fd-b8b9-3c2ec971c549 | checkpoint | Physical Clearances in & around switchboard area
fba2dde4-9337-43fe-95b3-c6b49bbdc0d2 | checkpoint | Ensure proposed switchboard location is secure
a9416cae-2210-5c90-86d3-6552c301c0a8 | note | Doors on rooms / cupboards etc.
c6fc324c-c411-4058-bf81-9026dec9e427 | checkpoint | Signage is installed
eb30c3a9-f93c-4fba-bd84-87683580b732 | checkpoint | Structural supports in place
33b6e2d8-d39c-47d7-bece-35c1645fddc5 | checkpoint | Carry out pre-delivery inspection at workshop
91ad48ab-3b6c-4101-8d0e-5fcd35853b19 | checkpoint | Inspect workmanship and take quality control photograph. Attach or take photo of weight & lifting information
52e24990-1455-4e6b-a2e3-2f3508d85971 | checkpoint | Confirm has the manufacturer supplied workshop QA & FAT documentation
b567f765-a23c-538e-8055-696f6cf8fbce | note | Fredon to issue switchboards FAT documentation for review
c70e88c4-d258-4637-bfb7-cad8b086461e | checkpoint | Check for obvious signs of damage DO NOT ACCEPT DELIVERY IF DAMAGED
c8a1eacc-c997-4acf-940e-8a090f385b53 | checkpoint | Check for delivery of quality control and quality checklist completed from factory DO NOT ACCEPT DELIVERY IF NO DOCUMENTS
a369fb8e-a2be-4191-8d58-9939a2aaceaf | checkpoint | Plan and resource installation task appropriately
68f1d899-82c8-4575-849a-e18d95f2379e | checkpoint | Use only proprietary lifting and rolling equipment
7f7c3e49-09fd-40eb-b79d-cc8e7de62848 | checkpoint | Clear route to switchboard installation location
47542b3f-e296-43f1-b381-eb0c86348f9f | checkpoint | Clear installation area completely of any obstacles, rubbish, personnel etc.
5c0fde3c-f3f1-463a-9fd2-c8ea8fa64afe | checkpoint | Switchboard mounted using correct fixings with additional structural support added where required
071968fa-87bd-43c1-9239-729fb7b954d5 | checkpoint | Switchboard mounted in a position to allow all correct clearances around the switchboard to satisfy all standards, specs and regulations
d14cbb6c-771b-4956-9711-640cceb1d806 | checkpoint | Remove all covers and inspection panels from board, carry out the following checks & inspections:
08343bad-c2e7-5fad-aa13-8c891fa7c368 | note | Visually inspect for damage
b739534d-de28-563a-b812-da2f2fde9920 | note | Visually inspect for cleanliness within boards
6ef30efb-c122-5da5-9776-24c6ce9ede53 | note | Visually inspect for loose cables & bars
1ed865b0-1ed7-53ae-9eae-86f81f7e6053 | note | Visually inspect for loose breakers, fuses and switches
ff3d27df-1ea2-59a4-a204-0560fd92a55a | note | Visually inspect all metering and control equipment
2d096422-cbfa-41e5-b64d-21afdcbdeda5 | checkpoint | Using appropriate tension tools and equipment, physically check tension of switchboard connections (switches, circuit breakers, control compontents etc.)
6283c118-70e4-5a55-abf0-c06fffc59a70 | note | NOTE: Switchboard connections may have come loose during transit
11795b15-4c35-4586-9c5d-84b4db1e919e | checkpoint | Using a calibrated tester physically confirm functionality of ALL isolation devices
90721352-b8a0-4b07-a382-ec180c1c8a24 | checkpoint | Confirm "OFF" is off (open state) by physical operation
0bad1cff-db68-492e-bd55-71aa3400332d | checkpoint | Confirm "ON" is on (closed state) by physical operation
06b1583b-5a15-426c-8706-80144408adfa | checkpoint | Review all protective device trip settings in accordance with engineers design, discrimination and cascade reports
9cc84f26-c741-4b30-8b30-37bd6b2a90bc | checkpoint | Fredon consultant to issue the discrimination study report for review and approval
c9bece6b-c401-4af4-9d84-a5988e8cd0ce | checkpoint | Review all metering, fuses and control equipment wiring
7ef51191-0270-4e9e-aa0a-31f7c602ecaa | checkpoint | Using as built / as constructed documentation confirm general arrangement, SLD and schematics are correct
8be73492-30e8-4dce-ad28-387559be6435 | checkpoint | Confirm signage and labels on board are correct
78f3322d-d462-4e2a-99d8-04d5221950cf | checkpoint | Confirm schedule is updated and inside board
0eaf8047-ae6f-4049-ac52-e5d47afe3aa4 | checkpoint | Carry out insulation resistance test to confirm integrity of switchboard insulation between all active conductors and all neutrals AND earths
8845432c-f4b6-4691-a356-a591c8ca80b0 | checkpoint | Reinstate ALL cover panels, close doors and lock etc.
2651a6f2-9d28-48de-8669-0051b8f3d224 | checkpoint | SDC Foreman Sign Off
a92ecde4-c841-4251-8070-be76b4388051 | signoff | Complete Sign Off
567cd124-d833-4560-afa5-9d706a685fba | checkpoint | Passive Fire Sealing
69d235c9-290c-4902-a902-ca1218a4e224 | checklist | SYS - Documents |  | SYS - Documents
6f5ea8ec-77ac-4b54-b52c-aa95f4abcf01 | checkpoint | Attach ITP / ITC
296dd308-70ac-4910-b62e-fa17d934470a | checklist | SYS - Drawings |  | SYS - Drawings
c916caf9-4320-44bb-973d-f24408604d02 | checkpoint | Attach Drawings
c31b197f-5fcc-4285-a670-fb2381103db2 | checklist | SYS - Fredon Compliance |  | SYS - Fredon Compliance
8b704297-2d47-435b-a0fb-3ba251abac4c | checkpoint | Fully compliant, site specific Safety Manual and SWMS have been submitted and accepted by the Principal Contractor.
91d5c165-17c8-4994-b8bb-3732eb718b9c | checkpoint | All Fredon electrical personnel undertaking these works have been trained and inducted in the Safety Manual and the relevant SWMS for these works.
60c4ae14-20eb-48a8-ab9b-1c6b61682845 | checkpoint | All Fredon electrical personnel undertaking these works are qualified to carry out these works, and are trained, and competent in the use of all equipment and plant required to carry out these works.
8d89afa6-a214-413d-bf8d-1b0a956b4d32 | checklist | Testing & Commissioning ITP 167 |  | Testing & Commissioning ITP 167
7c39cdea-df9f-4e72-8375-e5c5dde52b17 | section | Safety
7ca85f77-59cd-4412-b76c-e203d597915f | checkpoint | Project Risk identification and management register.
0b3a566a-6e66-5168-98bc-364c09424c58 | note | Identify / acknowledge and manage risks involved with this task.
3fb544c5-77fc-5401-87c3-79bec6802943 | note | Review the project risk register.
6df1471d-d82a-470a-bc84-c0424e201ce5 | checkpoint | SWMS
eaf91449-013b-546a-b489-360174128893 | note | Ensure that all workers have reviewed appropriate SWMS and have signed onto SWMS.
9898f1b8-e299-5fca-9f96-1e82aeb96c0a | note | Review
46b3de25-b672-40f9-a34b-38ff7ba286a1 | checkpoint | Project Specific HSEQ management plan.
4bde4618-20e6-5cd0-a013-aee223903306 | note | Review Project HSEQ management plan - these works must be fully compliant, site specific safety manual and SWMS have been submitted and accepted by the Principle Contractor.
413e0c97-4526-5da9-aad5-84cd3ce251a1 | note | Review
dbe2d6ee-dd43-46fc-9062-6ed9be011994 | checkpoint | Review Fredon Procedures
62fa9f92-efdd-55b2-be04-3298999cc7c3 | note | HSP-055 Testing an Electrical Installation
4d6da747-37df-5be6-b4b8-fae908fa3aab | note | HSP-037 Live Work Policy Witness VOC
f8b8ee98-f216-4f23-90cc-0a666a7ecc72 | checkpoint | NSW Electrical Safety Regulation 2013
6a6ae74a-cb6d-5724-a897-090518cf7ac5 | note | All Fredon Electrical personnel undertaking these works are qualified to carry out these works, and are trained, and competent in the use of all equipment and plant required to carry out these works.
7cb5d77a-29d7-5f59-af30-e7aa9ab5f3c7 | note | Fredon Electrical Testing and Fault Finding Training & VOC in previous 12 months
d5906f7d-bef0-4a4f-81fc-9c077c5fa823 | checkpoint | Ensure workers whom are performing 'energised' testing hold current CPR and switchboard rescue certificate.
e54c4a43-b618-5f1d-9069-0c775ca6875d | note | These are to be renewed annually.
d2d47ba4-e268-5948-a3a4-560cee27cf0f | note | Witness
fd08a26f-6eee-4186-b5ac-682e7c6ff951 | section | Project Specific Scope Requirements
5fdeef75-46ca-43eb-945d-2b173d50e27b | checkpoint | Insert project specific requirements here - specification ref, additional standard ref etc
d082fd9a-e3e8-5d91-95ff-6a5b1c0d3b05 | note | Review project specific documentation to ensure all relavent information is available any additional / supplementry testing requirements must be included within this ITP
d1fae888-e04d-5c2a-b7e6-3a94ae4e8e78 | note | ITCs for predecessor works complete
eed164e7-00ed-5e39-90ef-ef8d7c48ce01 | note | ITC - Switchboard pre-energisation
d25a9014-95d8-5f20-a64e-a2d781dc02da | note | ITC - Light & Power Fit off
b633b309-2e14-5fbd-804d-23baa89c9072 | note | As installed drawings complete
d59572f0-eed6-5d2a-b62c-a34d4002ea3c | note | Witness
d91b0c97-8917-4fba-aae7-59fe0c7f5c05 | section | Before Starting
62af6628-a07e-499e-8ddc-beb212366d70 | checkpoint | Correct test equipment to complete the task
15cd54c4-a611-54fc-a04a-cd18151bde6b | note | Insulation resistance tester - Ohmmeter;
edc8daf3-dba3-59d4-b829-0c90e498fcf7 | note | Voltage indicator (e.g. lamp, neon, LED device or meter);
af119dcc-5dd3-5fa4-9d1a-824e74a9742d | note | Suitable probes;
fe0edcee-6095-5817-a66a-8ed06f8e9fd6 | note | Trailing leads;
d212b52b-e128-51ef-b3f2-b65fe6bbde5c | note | A range of resistors of known values;
4afc56a3-b7a2-55f9-af14-724488e8c2c6 | note | A suitable instrument for measuring fault-loop impedance; and
a3a48721-7a68-5fca-93f7-369c7c471db8 | note | A suitable instrument or device for checking the operation of a RCD.
c8ef5fa6-edbb-52d4-ad79-426eb98117f2 | note | Phase rotation confirmation instrument Witness
2e552291-5cf1-4010-9006-4f2e3037ddc7 | checkpoint | Calibration
4cc244c4-c6a4-50a2-9c19-a1233ae9858d | note | The test equipment / multimeters etc must display current calibration information. Witness
b93924db-c71a-40e8-a2fc-228f40f10e7d | checkpoint | Operation of test equipment
1d74fea5-fb95-5db9-8ab5-238a706b5b3e | note | Ensure the electrician whom is to perform the works has been trained on correct operation of test equipment - multimeters. Witness VOC
ac985e34-ea55-43a5-9dc7-9ef7f1197b08 | checkpoint | Project specific - know the installation - be aware
c84a52b6-2b25-5323-90b7-462acb5bb925 | note | Ensure the electrician whom is perfroming the works is familiar with the installation - If required walk them through the proposed work zone. Discuss / Confirm
886e328c-fe09-4b02-b6a2-cbe8a34aa958 | checkpoint | AS Standards - reference documentation
a9058116-c933-5130-a279-5bbb0c38a41b | note | Each electrician whom shall be performing these works must be given access to AS 3017-2017 Discuss / Confirm
d25d3833-8001-4199-a1da-4bef953e1812 | checkpoint | Red Line Markups
b7f15db0-2305-5165-b2e7-228975fe4a66 | note | Ensure the electrician performing the works has the latest redline marks up available and can easily identify circuit arrangements
19dbfcee-c333-4efa-bc6d-675c9b556f18 | checkpoint | Complete ITC-167.1 / ITC-167.2
c6b6030e-5d76-5947-8fae-c05be4d74201 | note | Ensure the electrician whom is perfroming the works understands the requirement to complete the ITC [Inspection & Testing Checklist] associated with these works and that these works must be completed in accordance with Statutory requirements.
6a8cf140-95cf-5f3f-a823-014945025ce2 | note | The electrician must enter their personal electrical licence number and acknowledge compliance via signature on ITC as works are completed.
a8508ae4-dedc-57b8-a43f-75a4808b0c15 | note | Review ITC-167.1 / ITC-167.2
876633fa-d168-44ee-ae3e-0d296d657f84 | checkpoint | Electrical Certificate of Testing and Compliance
662dabb9-a057-5de0-9b11-41673c6e49b2 | note | It is the Project managers responsibility to review complete ITC,s and compile the project testing / commissioning dossier for final review.
08b79702-0202-53b6-b530-fb91a4633568 | note | The project manager shall then complete the certificate of electrical compliance and testing - This document must be presented to Fredon QTP [Qualified Technical Person] for project sign off.
38a85860-5ad5-5e1e-aac2-1a2ce43a65ce | note | Certificate of Compliance
18930e48-37de-43dc-8ae0-3935c0d3d1f1 | section | De-Energised Testing - Visual Inspection
492d4017-841c-4586-98da-f7d0250eff8f | checkpoint | A visual inspection shall be made when work on an electrical installation has been completed in order to verify that the work complies with the requirements of AS/NZS 3000.
d816e841-12cd-54d7-a0ef-ee8bb34bdecd | note | The visual inspection shall be carried out before, or in association with testing, and should where practicable be made before the relevant part of the electrical installation is placed in service.
abf9493f-12f1-59f0-837f-4c8241daaa49 | note | Where the visual inspection of a part of the electrical installation is not practicable at the completion of the work, e.g. not accessible due to enclosure in the building structure, consideration should be given to inspecting that part during the course of the installation.
72d9dd1e-bc79-5fe2-8736-c2eeb6130cae | note | Refer to AS 3017 section 2 for further detail.
b8785b79-bc1d-57e7-80ac-b8378268998f | note | Complete ITC-167.1 / ITC-167.2
c5b65764-5fc0-4d14-a13a-ca1ef27bc4ab | section | De-Energised Testing - Earth Continuity Resistance
23c467be-dcd2-4e30-b4ac-f1040848f019 | checkpoint | Earth continuity and resistance tests are necessary to ensure that the earthing system has been installed in an appropriate manner and the resistance of the protective earthing conductor is low enough to permit the passage of sufficient current to cause circuit protective devices to operate if there is a fault between live parts and exposed conductive parts.
79260149-6077-523a-9145-65c3bfe0ed41 | note | NOTE: This may include cable tray, Stainless kitchens etc
85b1072e-ba87-5235-8c29-c3089e85bc76 | note | Refer to AS 3017 section 3.1 for further detail.
649b4f4a-dc1c-5097-b56f-3eb337db260e | note | Complete ITC-167.3
f7ae9e55-4de1-4e54-b10c-800b6145393e | checkpoint | Earth continuity and resistance tests are required for Communications Cabinets with shielded and sensitive equipment requires to have a clean direct earth.
df2918b2-abe7-5cc9-9313-9c5d35918c9e | note | Refer to AS S009 Pass Less than .5Ω
f9759d32-88dc-5a56-960b-39b423ef8637 | note | Complete ITC-167.3
bce7f189-2f32-40f3-9380-5a3f3e27f652 | checkpoint | Note: The continuity of protective earthing conductors may also be verified by measuring the earth fault-loop impedance of the circuit.
0aad2841-2394-5cd2-a111-2bc1e9869c04 | note | See 3.6.4.2 refer table 3.2 for values Complete ITC-167.1 / ITC-167.2
0a992b3c-78f7-4f36-9f24-4e840715d70c | checkpoint | The insulation resistance tester used shall be able to maintain its terminal voltage within +20% and -10% of the nominal open-circuit terminal voltage, when measuring a resistance of 1 MΩ on the 500 V range or 10 MΩ on the1000 V range.
df7cb230-80ee-5697-b307-6b146a13b08b | note | When applying the insulation resistance test to electronic equipment or surge protection devices, care should be taken to prevent damage to the devices.
b0f82bdd-d305-4118-a764-e5c2f2e57c1b | checkpoint | Results The resistance of protective earthing conductors shall be
4601a737-25f9-5a4c-8607-02aec1c68e57 | note | (a) low enough to permit the passage of current necessary to operate the overcurrent protective device; and
3c1a8de7-e006-5161-99b7-0f043cd69968 | note | (b) consistent with the length, cross-sectional area and type of conductor material. The resistance of the main earthing conductor or any equipotential bonding conductor shall be not more than 0.5
90900985-3a45-5b18-9f4f-f404f16517fc | note | NOTES: 1 Under the subsequent tests for earth fault-loop impedance, the maximum allowable resistance of the protective earthing conductor associated with any particular circuit depends on the type and rating of the protective device and the impedance of the live conductors that comprise the circuit.
87eef55c-6f61-5c28-9b91-8860189802f7 | note | 2 Resistance values (Re) for earthing conductors are given in Table 8.2 as a function of the rating of the associated overcurrent protective device. These values may be used when testing for earth continuity.
e058f04a-33b1-4ecb-b730-097a59443d7a | section | De-Energised Testing - Insulation Resistance
c958b411-e2e6-4ef1-a2cd-5e52f1c1b9b4 | checkpoint | Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation. This is to prevent:
9599e05f-88bb-58c2-bea6-3d35a7782735 | note | (a) Electric shock hazards from inadvertent contact;
d9384f66-dd6f-54c4-8b93-9aae711a8f79 | note | (b) Fire hazards from short-circuits; and
f8992054-8647-5fc0-ab08-9b3475229290 | note | (c) Equipment damage.
e5cdf59e-f3b0-51d7-84f6-e07258685c5c | note | In addition, insulation resistance tests between all conductors are necessary for consumers mains and submains to minimise potential for insulation breakdown, injury or property damage due to failure of such conductors. The integrity of the insulation is stressed by applying a direct current at 500 V, or 167 V for equipment described in 3.2.4(e) which cannot be isolated. The insulation resistance between:
ff0ed00e-37f4-5282-a250-7f20d9371b22 | note | (a) the conductors of consumers mains and submains; &
f72ef866-d4e2-5440-a41a-8f4087659d97 | note | (b) live and earthed parts of an electrical installation, or parts thereof, including consumers mains and submains shall be not less than 1 MΩ.
eed8620a-4f6a-5076-ad85-ffef8b8d0d4e | note | Refer to AS3017 section 3.2 for further detail
1433e3d4-2e5b-5eee-aad2-70183389dd72 | note | Complete ITC-167.1 / ITC-167.2
677aa97a-9da0-57f3-8030-93a57b0b53b4 | note | Note - If luminaires have been installed - all switching devices should be 'on' - Test only between 'live' conductors and earth.
bf8a2be3-ef1b-56e4-8fdf-73901737a8b8 | note | Note - If luminaires have not been installed - all switching devices should be 'on' - Test between all conductors and earth.
3d737b9d-76da-4c44-bc4e-9db768b1b5f6 | section | De-Energised Testing - Polarity
2c584f8b-61de-48c5-8942-6e57e0a11487 | checkpoint | Polarity testing is necessary to ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors. This testing is to ensure:
24343b00-b249-5427-ac77-65ca34c69bb1 | note | (a) Active and neutral conductors of the consumers mains or submains are not transposed resulting in the electrical installation earthing system becoming energised;
a7e20b94-bef7-5d6b-a1b4-8ed2d95542e1 | note | (b) There are no combinations of incorrect active, neutral and earthing conductor connections resulting in the exposed conductive parts of the electrical installation becoming energised; and
79ad8a20-4e2b-5643-9204-d203be6ec9c8 | note | (c) Switches do not operate in neutral conductors, resulting in parts of appliances, such as heating elements and lampholders, remaining energised when the switches are in the ‘OFF’ position.
f2cb32f6-8f77-4acd-a0df-01858273fd77 | checkpoint | Requirements
6b7442ea-5cf4-51d3-abd1-73502ef44608 | note | (a) Every single-pole switch or protective device shall operate in the active conductor of the circuit in which it is connected;
a7cee0d1-bbf1-5211-9645-72195fa5c39e | note | (b) A switch or protective device of a multi-phase circuit, other than some types of motor overload protective devices, shall operate in all active conductors of the circuit in which it is connected;
c6504652-315e-5064-a72b-dac3ee8be1ea | note | (c) RCDs required to switch all live conductors shall switch the active and neutral conductors of the circuit;
b4f32b92-1d49-50ff-b439-bc243e50e077 | note | (d) Where multi-phase socket-outlets of the same type form part of an electrical installation the phase sequence of the socket-outlets shall be the same (see 3.5);
5f8bfafa-1efb-5940-aeab-b9298eca178a | note | (e) Socket-outlets which accommodate flat-pin plugs shall be connected so that, when viewed from the front of the socket-outlet, the order of connection commencing from the slot on the radial line shall be earth, active and neutral in a clockwise direction;
8ec3f6ac-795f-5843-8c8c-8c097d451043 | note | (f) All neutral conductors shall be connected to the neutral bar of the switchboard; and
2c466e61-c3e6-5d5f-8e75-7987ef91a22f | note | (g) The consumers mains neutral shall be connected to the neutral bar of the main switchboard.
ac5ce141-17c3-5d43-9de5-24b496e1ec01 | note | Refer to AS3017 section 3.3 for further detail.
b1e0e980-0e0e-511b-ae8b-538e5f3e691d | note | Complete ITC-167.1 / ITC-167.2
b0ea4bb2-8653-4e47-b783-4622eaefe14b | section | De-Energised Testing - Correct Circuit Connections
ef20fa07-3aa1-4d98-a4e8-85c0b953a227 | checkpoint | Tests for correct circuit connections are necessary to ensure the following:
5e03b02f-130a-5b22-b33f-fbe1a86d8d92 | note | (a) Protective earthing conductors do not carry current in non-fault conditions; and
f655e9b4-8274-5b04-a5ba-a9f261ee0abf | note | (b) No short-circuit exists, because a short-circuit current flowing between live conductors and through part of the earthing system can cause considerable fire damage or personal injury, particularly in high current locations.
1f9fab88-cb90-52de-b96a-b2776709d1fa | note | Refer to AS3017 section 3.4 for further detail.
37896d16-639b-586f-ae7e-55341104ad3b | note | Complete ITC-167.1 / ITC-167.2
4d987e89-8365-4f4e-8656-4a8bdbd7b5a2 | section | De-Energised Testing - Earth Faultloop Impedance
a32c87ce-413d-4214-ab49-1920d80844b4 | checkpoint | 3.6.3.2 Supply not connected
c67b63e5-4372-5cad-9aea-71012bec60ce | note | When tested in accordance with 3.6.4.2, the total resistance (Rphe) of the active and protective earthing conductors of an individual circuit which forms part of the earth fault-loop shall not exceed the values shown in table 8.2.
aeb0499f-380e-586c-9ed6-90a509de42c1 | note | NOTE: The values calculated must be accumulative of submains etc.
8b1e8fdb-5e89-44f5-9cba-b701171e9012 | checkpoint | The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
27ec159b-102e-5c5f-8eb9-755b4b02f5d9 | note | Refer to AS3017 section 3.6 for further detail.
deee592b-fb74-5f84-a037-50fc133f6458 | note | Complete ITC-167.1 / ITC-167.2
a54b61a0-1dd4-41a0-88fa-c961b14bcc4b | checkpoint | Dead testing complete
9765fecc-583b-5a0a-9b46-1ae104bebdc2 | note | Upon completion of 'dead' testing present all documentation to Site supervisor for approval
eb2e04d4-8a1b-49bd-8c47-e66f6859fe89 | checkpoint | Submit test results for review with site management
510fbf8a-5732-54b8-9dec-d46282c2bad4 | note | Site supevisor reviews ITC for completeness.
e8e6f403-2abb-5ab5-bb31-5cd2d7625c8f | note | Note: Fredon supervisor is not responsible for test result accuracy.
7c61a2ec-046a-519a-9a9f-f6dbaec21d37 | note | Review / issue permit energisation Permit (HSF-091)
f4a5cba0-827e-4400-b5e9-813456377917 | section | Energised Tests - Tests for Voltage
73629a53-3086-43a9-8f81-199f914e8f64 | checkpoint | Using test lamps / voltmeter
d8051c2e-003b-58a4-b5ab-33ac2f7a2fae | note | Main switch off
170f1bf6-fdd1-5dcd-87ed-e96000d53ad0 | note | ○ Confirm supply is present at Line side of main switch.
c7410f3f-ec9c-598d-a305-03ab8c5da5b4 | note | ○ Confirm supply is not present at Load side of main switch.
04d90a52-da3c-523b-ae3a-460e8533925f | note | Main switch on - sub circuit (CBs) off
38e8075c-df2c-5276-96c6-e379aaf2a1df | note | ○ Confirm supply is present at Load side of main switch.
4ab7df78-c5b9-5660-8c7c-481f49d2b8de | note | ○ Confirm supply is present to line side of relative distribution circuit breakers. Complete ITC-167.1 / ITC-167.2
b2cae5f9-b7e7-4167-93a1-70538c2b8c3a | section | Energised Tests - Phase Rotation
873f44e7-cdaa-41ec-9b41-32984e36589f | checkpoint | Using test phase rotation meter.
0f3b12e2-f032-5ffd-9f10-6d8822673100 | note | Confirm phase rotation sequence.
ebeb5199-c903-5ff4-adab-bf5a3697c0a6 | note | Complete ITC-167.1 / ITC-167.2
397637f3-9910-4b19-829c-016fb6344889 | section | Energised Tests - Earth Fault Loop Impedance
6461956e-5178-4f4e-83e9-dda884f53df5 | checkpoint | 3.6.4.1 Supply connected
d4fbe468-e6fb-5100-b761-c9c6e1061152 | note | The earth fault-loop impedance should be measured using an instrument that has a facility for measuring and indicating low values of impedance.
4baca61f-004d-583e-8ff6-d2f609ab5c69 | note | NOTE:
09b0ed6d-9168-5d92-916a-2ef60a72e472 | note | (2) Earth continuity and resistance tests should be carried out on protective earthing conductors in accordance with 3.1 before measuring the earth fault-loop impedance.
a07e5728-b220-5701-abe5-2ac1325e09df | note | (3) It is preferable to measure the earth fault-loop impedance using the permanent network supply rather than a temporary supply.
d45c15f1-7584-53b6-8210-927e56fcd471 | note | (4) The measuring circuit includes the impedance of the flexible test lead, which must be as supplied with the meter. If the meter leads are fused, the fuse resistance must be taken into account. The MEN connection is to be left intact.
e6b15eb0-8f91-47be-b003-dff2793b88ed | checkpoint | Maximum values of earth fault-loop impedance shall not exceed the values shown in table 3.1 or the value of Ia for the protective device being used in accordance with the manufacturer’s data.
83ca9ebd-21df-5f9e-826b-2312b2316441 | note | Refer to AS3017 section 3.6 for further detail. Complete ITC-167.1 / ITC-167.2
50dc4acf-a768-50c2-8f05-e9eb68064158 | note | Note: If an RCD operates during the earth fault-loop impedance test, the test result is considered satisfactory.
1cd9a98b-ddd0-47c3-8b71-45843c4e7faf | section | Energised Tests - Operation of Residual Current Devices
3b0dde2c-889c-468c-aa14-e7319b781c79 | checkpoint | Testing of an RCD is carried out to ensure that the RCD operates and disconnects the designated circuit. The function of the RCD is verified by the operation of the integral test device, or by the use of special test equipment
db520dea-55dc-492f-98aa-5efdcbb22cd4 | checkpoint | Operation of the integral test device shall cause the RCD to trip and disconnect the designated circuit.
e40aa1d4-8a2c-5063-83b8-35413cfd1800 | note | NOTE:
3be254d7-4f78-58ae-b099-5d415077efc6 | note | (1) Tripping the RCD by means of the integral test device establishes:
c7e168c6-7952-5084-a2c2-4d95e8da8b77 | note | (a) That the RCD is functioning correctly; and
12f65dbf-5cd7-564c-834e-ef9716104744 | note | (b) The integrity of the electrical and mechanical elements of the tripping device.
a16bc8d8-a964-5d0b-9508-edd21805608f | note | (2) Operation of the integral test device does not provide a means of checking:
79ce7867-7701-52fb-829c-a5bcff634853 | note | (a) The continuity of the main earthing conductor or the associated circuit protective earthing conductors;
5a27f5a4-3866-5c84-821a-d2d2ebc54a38 | note | (b) Any earth electrode or other means of earthing; or
4a200032-d3d4-5ce6-9177-7be317886a54 | note | (c) Any other part of the associated electrical installation earthing.
79a05826-c123-5702-b897-094c009585f2 | note | (3) Tripping the RCD by means of the integral test device, or by special test equipment such as a test plug with a resistor between the active and earth pins, may be used to verify that the circuits required to be protected by the RCD are protected.
45c8c197-23b4-4787-91d7-55cf1062c2af | checkpoint | RCD is to be tested using functional trip test and trip times must be recorded. Complete ITC-167.1 / ITC-167.2
cfb2ae80-0a7e-46ad-845f-34f87afa16cd | section | Energised Tests - Final Inspections & Safety Checks
54a3e490-9248-44e1-b0f0-0cfb3e84954e | checkpoint | Final Inspections: At works completion confirm all circuit schedules are complete & correct.
9b3a0802-2df3-409e-801a-7f324ccb1b7c | checkpoint | All circuit descriptions are clear & worded to be easily understood.
9c0ed3d1-23c0-46c0-83fe-3c33ed6853c9 | checkpoint | Any circuits not tested remain disconnectd from circuit breaker & terminated in BP connected.
ac62130c-da51-496e-b468-afc6f54582e5 | checkpoint | All equipment has been labelled in accordance with project requirements, and labelling aligns with as built drawings.
987f16ee-e101-4f3d-8f28-97e210dcb791 | checkpoint | Ensure that any changes made during testing which effect as built documentation are captured via RED pen mark up on drawings.
16ea6f24-c62e-4c98-8732-907124df02a2 | checkpoint | Compile list of any incomplete works or defects which require rework.
524d6fd0-660b-42c0-bafa-de35b8631a48 | checkpoint | Re-instate all switch board covers, doors and panels. LOCK THE SWITCH BOARD DOOR & CHECK ALL OF THE ABOVE
249cfbb5-e002-4390-b1cb-7cf9cfff69dd | section | Energised Tests - Completion
1ae631dc-8cda-4969-9a2a-d41ce0548311 | checkpoint | Documentation - Once complete:
93b01727-db1c-5123-a53c-6972e548348a | note | 1. Review documentation for correctness.
e79f0ba6-b4ef-5b42-91b3-16110ec28ea0 | note | 2. Submit documentation to site supervisor immediately.
b75c42cd-5b2b-5676-9ee9-4bea895f85f3 | note | 3. ITC-167 complete & signed
670bd9df-5035-57f1-bc60-44a4447a926f | note | 4. RED pen mark up of zone drawing for as built information.
de317fc5-bf11-5b1a-a6f3-a97109cb4c62 | note | 5. DB schedule information.
96409bb9-32f9-5d43-8d97-b6233bc2867c | note | 6. Concise list of incomplete or defective works. (DO NOT LEAVE ON SITE)
356b7d93-b1e9-5e25-b583-79c730582c8a | note | 7. Submit
035265fc-2d95-458a-9b89-2319fb1b8a8b | checkpoint | Fredon site supervisor shall review all documentation
c5b6af6a-9af9-568f-ab09-f7a322020eb5 | note | Note Fredon supervisor is not responsible for test result accuracy
4577cf44-a58a-5407-959f-80db95c635b0 | note | Review
d4f68046-8f6e-48ab-93bf-f3fc4a445e27 | checkpoint | Fredon Project Manager to provide certificate of testing and compliance Certificate of Compliance
837f87c6-82b0-4c3f-929c-568d247353d3 | checkpoint | SDC Foreman Sign Off
acb81183-a0b4-4102-a2fa-ab19a941c849 | signoff | Complete Sign Off
185a5735-0c58-47de-8f36-6db5f4c24c15 | checkpoint | Passive Fire Sealing