## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Document Upload |  |  |  |  | Yes | Document Upload | 11881eff-c8bb-4cc1-b01f-11940cf94c3f
checkpoint-status |  |  | checkpoint | Upload Drawing, docket, etc.- pass once complete
checklist-flat |  |  | checklist | ITP-001 - In Slab Conduit Installation Checklist |  |  |  |  | Yes | ITP-001 - In Slab Conduit Installation Checklist | 24e26a2f-26e1-41e6-9283-b4d1eeecaaf1
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 8ce05556-3db3-5cf8-863c-b264661cf7fc |  | textbox | Drawing Ref No. & Revision
text | 5b164201-0c9a-5b22-a593-50d9db243d89 |  | textbox | ID
text | dc981d0d-54cd-535b-a5fe-9732f8f26560 |  | textbox | Origin
text | d79e7e5a-b2e9-51c7-8952-65e2d31fd96f |  | textbox | Destination
text | 9061fdbd-3f20-51c2-b64f-54a54effcd5b |  | textbox | No of conduits
text | 024af932-d5f2-57c5-af98-8b50bd10ef3d |  | textbox | Size
checkpoint-status |  |  | checkpoint | Check for existing services, location & approval
boolean | 6ff52c21-9fba-541d-ad84-d4d4ac1d8f17 |  | tickbox | Exist
boolean | 9247dd15-52fc-599f-8054-04af0ba4668a |  | tickbox | Locate
boolean | 84426970-5552-58e2-ab21-24695c7393b9 |  | tickbox | Permit
checkpoint-status |  |  | checkpoint | Correct depth
checkpoint-status |  |  | checkpoint | Tied and joins glued
checkpoint-status |  |  | checkpoint | Ends sealed
checkpoint-status |  |  | checkpoint | Draw string
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | OK to pour concrete
checkpoint-status |  |  | checkpoint | Signature - installer sign off attached below
checklist-flat |  |  | checklist | ITP-010 - Subcircuit & Submain Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-010 - Subcircuit & Submain Installation - Inspection & Test Plan | 40c2d63a-4259-41cc-8c05-f8498dea38a6
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 60d6632e-4261-5030-8d02-c1560a4e57bd |  | textbox | Drawing Ref No. & Revision
text | 1589be27-d0a1-571a-b4ca-e139f4347eaa |  | textbox | ID
text | e1282537-2108-5db8-a568-f687130ac834 |  | textbox | Wired from (Origin)
text | 8193d8d1-71d5-5d8c-b30d-0c78f1d914d1 |  | textbox | Wired to (destination)
select | 6a7f1a53-4d27-5b0b-b24b-fdb5330a0d96 |  | dropdown | Cable size | 1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm
checkpoint-status |  |  | checkpoint | Lighting or Power - N/A if not applicable
select | 81d5efc8-747e-578b-ae6c-45af43480b98 |  | dropdown | select if applicable | Light,Power
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | cable labelled both ends
checkpoint-status |  |  | checkpoint | Visual inspection for damage
checkpoint-status |  |  | checkpoint | Insulation Resistance Test complete
checkpoint-status |  |  | checkpoint | Continuity test complete
checkpoint-status |  |  | checkpoint | Polarity & switching test complete
checkpoint-status |  |  | checkpoint | Test result
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-003 - Wall Conduit Installation Checklist |  |  |  |  | Yes | ITP-003 - Wall Conduit Installation Checklist | 428de98e-0787-4c68-871e-07670e4fd1f7
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 17920113-3f2c-5917-86ce-7eb2bef0e451 |  | textbox | Drawing Ref No. & Revision
text | b31c6a09-3e3a-570e-9d7f-87d95eabf69c |  | textbox | ID
text | 1613d639-5b0c-5e33-92e4-17ff042041c3 |  | textbox | Origin
text | 2d01c962-b591-5b4b-b60d-53afbc8869ea |  | textbox | Destination
text | 2b67da07-a097-5781-8f02-cd6328951ff7 |  | textbox | No of conduits
text | fcee5b16-7040-5579-8075-b42255824dbd |  | textbox | Size
checkpoint-status |  |  | checkpoint | Check for existing services, location & approval
boolean | 758c49f7-b7a5-5c91-98e9-c601ab231117 |  | tickbox | Exist
boolean | c8bde6e5-ac56-52b8-a08d-415b8b47c7e1 |  | tickbox | Locate
boolean | 9adff9bd-4777-50b0-9cca-6af7f71f889b |  | tickbox | Permit
checkpoint-status |  |  | checkpoint | Wall boxes fixed
checkpoint-status |  |  | checkpoint | Wall boxes flush
checkpoint-status |  |  | checkpoint | Conduit secured correctly
checkpoint-status |  |  | checkpoint | PVC conduit glued
checkpoint-status |  |  | checkpoint | Straight & level
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman sign off attached below
checklist-flat |  |  | checklist | RCD Commissioning - Switchboard Details |  |  |  |  | Yes | RCD Commissioning - Switchboard Details | 4c8c6f9a-a4b9-4c1f-a9b3-00d00ce94450
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | a3be1865-517c-52e9-82b6-0e83b3170316 |  | textbox | Drawing Ref No. & Revision
text | f9c3283b-7162-5171-abf8-f7d8b1cba89d |  | textbox | Switchboard ID
checklist-sectioned |  |  | checklist | Dry Fire Fit Off Devices |  |  |  |  | Yes | Dry Fire Fit Off Devices | 5292340c-50dc-4f48-8f79-af1b92a87a96
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | d513bb3f-1d84-5eca-a358-c78c0f858bac |  | textbox | Project Name
text | 18d949fd-c0dc-5433-81fd-f550442ad113 |  | textbox | Project Number
text | f0a372b3-b54a-5066-96a8-10215a12929d |  | textbox | Name
text | 8205d42e-00ae-5667-9657-c9fb631aecf9 |  | textbox | Date
text | b08753ec-c073-57cf-a4af-7ec0e94667f0 |  | textbox | Location
checkpoint-group |  |  | section | Detectors
checkpoint-status |  |  | checkpoint | Detector type appropriate
checkpoint-status |  |  | checkpoint | Detector addressed for correct location
checkpoint-status |  |  | checkpoint | Detector terminated correctly
checkpoint-status |  |  | checkpoint | Detector clear from walls / beams 400mm
checkpoint-status |  |  | checkpoint | Detector clear from air register 500mm
checkpoint-status |  |  | checkpoint | Detector located in accordance with RCP
checkpoint-group |  |  | section | Duct Probes
checkpoint-status |  |  | checkpoint | Probe installed on correct duct
checkpoint-status |  |  | checkpoint | Probe covers 70% of duct width
checkpoint-status |  |  | checkpoint | Detectors type - photo optical
checkpoint-status |  |  | checkpoint | Appropriate cable terminated in probe
checkpoint-status |  |  | checkpoint | Duct probes cover accessible
checkpoint-status |  |  | checkpoint | Detector indicator visible
checkpoint-group |  |  | section | Remote Indicators
checkpoint-status |  |  | checkpoint | Remote Indicator labelled correctly
checkpoint-status |  |  | checkpoint | Remote Indicator located below C/S detector
checkpoint-status |  |  | checkpoint | Remote Indicator located outside cupboard/room
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | 1f425613-b086-52da-b0e0-9669ec1dafb8 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checklist-flat |  |  | checklist | Dry Fire FIP SFIP Final |  |  |  |  | Yes | Dry Fire FIP SFIP Final | 5955fbb4-1988-4095-9b6b-0ee8a534a993
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 3ece533d-ba62-5b33-94f1-b67ad808c529 |  | textbox | Project Name
text | 26403490-523d-5870-bc9a-3a9592642198 |  | textbox | Project Number
text | 0ddc97b3-bf3c-5bb8-982b-1dbc6e196dc9 |  | textbox | Name
text | 2bf26ea0-0f7f-509f-9571-a7cc259aaa5b |  | textbox | Date
text | 05b34243-47a3-59c7-983a-162f4236a2e7 |  | textbox | Location
checkpoint-status |  |  | checkpoint | Location clearance 500mm either side, 1.5M at front
checkpoint-status |  |  | checkpoint | M.C.P. fitted adjacent or on F.I.P
checkpoint-status |  |  | checkpoint | Height 1850mm max to top of switches or indicators
checkpoint-status |  |  | checkpoint | F.I.P.’s securely fixed to wall
checkpoint-status |  |  | checkpoint | Cable entry holes de-burred and bushed
checkpoint-status |  |  | checkpoint | F.I.P. cleaned of all swarf and dirt
checkpoint-status |  |  | checkpoint | 240 V segregated from all other conductors
checkpoint-status |  |  | checkpoint | 240V Connected in accordance with AS3000
checkpoint-status |  |  | checkpoint | Fire line connected. (Phone/Radio/GSM)
checkpoint-status |  |  | checkpoint | Insulation test been carried out
checkpoint-status |  |  | checkpoint | Location/mimic diagram installed
checkpoint-status |  |  | checkpoint | Panel/Ancillary labels installed
boolean | d2c2c009-01a3-58b5-bfdb-4003e57fceec |  | tickbox | After hours label on the panel
boolean | 7104a35d-7880-520d-99f9-2270f6016580 |  | tickbox | Batteries dated
checkpoint-status |  |  | checkpoint | Block plan / As installed drawings in the panel
checkpoint-status |  |  | checkpoint | Log book in the panel
checkpoint-status |  |  | checkpoint | 100% test been carried out
checkpoint-status |  |  | checkpoint | A/C and 1668 controls tested
checkpoint-status |  |  | checkpoint | Evacuation system tested
checkpoint-status |  |  | checkpoint | Fire brigade connection been tested
checkpoint-status |  |  | checkpoint | Panel keys been handed to client
checkpoint-status |  |  | checkpoint | Client has been instructed on panel operation
checkpoint-status |  |  | checkpoint | Spares been provided
checkpoint-status |  |  | checkpoint | Panel been cleaned inside and outside
checkpoint-status |  |  | checkpoint | Sign-Off Test completed to specification/drawings & Area left clean/tidy
checklist-flat |  |  | checklist | ITP-005 - Underground Pit Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-005 - Underground Pit Installation - Inspection & Test Plan | 650fb48c-d55b-4ef6-8de4-011b3abdda96
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | cbea2e92-e023-5129-a409-6b0578d006a6 |  | textbox | Drawing Ref No. & Revision
text | c39cddf3-8b89-56a3-8f8b-fc918ef7fbf7 |  | textbox | ID
text | 0c863558-0ba4-5e60-8668-edfeef9f6e20 |  | textbox | Pit type
text | 795a3685-55db-5dba-8c00-fbb925d962cf |  | textbox | Pit location
text | a264959a-2dde-58d6-aec4-9e56301e9138 |  | textbox | Pit size
checkpoint-status |  |  | checkpoint | Excavation correct
checkpoint-status |  |  | checkpoint | Pit correctly bedded
checkpoint-status |  |  | checkpoint | Drainage installed
checkpoint-status |  |  | checkpoint | Concrete surround
checkpoint-status |  |  | checkpoint | Pit penetrations sealed
checkpoint-status |  |  | checkpoint | Lid square & pit cleaned
checkpoint-status |  |  | checkpoint | Pit lid labels installed
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-016 - Sub-circuit Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-016 - Sub-circuit Commissioning - Inspection & Test Plan | 7e5972db-62ba-43d9-a1fc-56277990a77e
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | b2e17b31-d97c-56ef-a036-bf1733d7d647 |  | textbox | Drawing Ref No. & Revision
text | c8971a72-5511-547f-838a-ccdd939089d4 |  | textbox | Switchboard ID
text | c942ceee-9626-561b-8915-396f9f24966f |  | textbox | Protection Device Number
text | b8b0bc9c-575f-5956-9a73-01236984dda2 |  | textbox | Protection Device Size (Amps)
select | 07466f75-0a5c-5f62-85a9-3d6ac2ab3ca3 |  | dropdown | Cable size | 1.5mm,2.5mm,4mm,6mm,10mm,16mm,25mm,35mm,50mm
boolean | ed74a47f-a980-57c2-8c69-13d8b1721834 |  | tickbox | Light circuit
boolean | 73c5fd8f-547b-5149-a01c-19e25412ded3 |  | tickbox | Power circuit
checkpoint-status |  |  | checkpoint | Earth resistance test result
checkpoint-status |  |  | checkpoint | Insulation resistance test result
checkpoint-status |  |  | checkpoint | Polarity test result
checkpoint-status |  |  | checkpoint | Short circuit test result
checkpoint-status |  |  | checkpoint | RCD test result
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
text | 402f5ec2-7954-502e-81ab-49c5673f43d0 |  | textbox | A' Grade Number
text | c7ddfbec-7e08-5019-bd06-6b11d183563c |  | textbox | A' Grade Name
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-019 - Lighting Control Installation/Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-019 - Lighting Control Installation/Commissioning - Inspection & Test Plan | 866e85f6-b02f-4fe3-b1f0-71fb76b5ac02
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 042a746f-e64f-5bf0-84ce-826ac273a9ff |  | textbox | Drawing Ref No. & Revision
text | 46dcee90-4fd5-5830-a04f-04faab41c190 |  | textbox | Channel Number
text | 3076efa9-ad41-5564-842c-595bcebed0bc |  | textbox | Protection Device Number
text | 69c50194-3aa8-5db5-8861-8825f3448281 |  | textbox | Number of Light Fittings
select | e605529f-ce21-562f-9c4a-56dcc1f51ac9 |  | dropdown | Type of Dimming Control | DALI,DSI,Power
checkpoint-status |  |  | checkpoint | Switching Function
checkpoint-status |  |  | checkpoint | Dimming Function
checkpoint-status |  |  | checkpoint | Scheduling/Scene Function
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-002 - Underground Conduit Installation Checklist |  |  |  |  | Yes | ITP-002 - Underground Conduit Installation Checklist | 871e5559-24a0-48a8-ba56-679ad34aa415
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | b327b862-22e3-5390-9ef9-3cd3237e9282 |  | textbox | Drawing Ref No. & Revision
text | f27d56ec-5b69-531e-9ff4-ac86ba894a55 |  | textbox | ID
text | e122e683-3a2b-5bc3-a539-19bef4a2b6e1 |  | textbox | Origin
text | 4bc6a9b1-c848-587e-945e-d32189383b95 |  | textbox | Destination
text | decd1b65-9083-51cc-b4e7-1c1f9d69c339 |  | textbox | No of conduits
text | 6c6f57f7-bf49-5fc8-b63a-2d011631423c |  | textbox | Size
checkpoint-status |  |  | checkpoint | Check for existing services, location & approval
boolean | 99f0147e-c244-539c-8541-de1ee3b34ce7 |  | tickbox | Exist
boolean | 661257c2-b991-5721-8706-f45878e1f004 |  | tickbox | Locate
boolean | 86aec1fe-7ccf-5147-8939-089b506f1c1f |  | tickbox | Permit
checkpoint-status |  |  | checkpoint | Correct depth
checkpoint-status |  |  | checkpoint | Marker tape
checkpoint-status |  |  | checkpoint | Compaction
checkpoint-status |  |  | checkpoint | Draw string
checkpoint-status |  |  | checkpoint | Sealed ends
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman sign off attached below
checklist-flat |  |  | checklist | RCD Test Results |  |  |  |  | Yes | RCD Test Results | 96e5c201-b484-43e6-a164-cc1dfa8ea73c
checkpoint-status |  |  | checkpoint | RCD Details
select | 2219774c-6545-5217-b18c-68712271ff7b |  | dropdown | RCD type | 10mA,30mA,100mA
text | e1e7501f-ccc1-5737-af61-d926c472a334 |  | textbox | Protection Device Number
button | 63cf19d7-835b-5c2b-8033-d16dd640edb2 |  | button | RCD test button working | Yes,No
label | 47868b47-5cfe-5d74-b146-417d0b6c4867 |  | note | 1/2 Rated Trip 0° - ∞
label | 5f41f209-bce8-5560-9a39-6edf2c43f422 |  | note | 1/2 Rated Trip 180° - ∞
text | 55e2c777-9b7c-521a-8819-7918333b4be9 |  | textbox | Rated Trip 0°
text | 31ae8a13-6795-5342-8a95-c4aa82a362b8 |  | textbox | Rated Trip 180°
text | 047faa70-912d-5a42-8a27-e9fe43a9a717 |  | textbox | 5x Times Rated Trip 0°
text | 0265ee37-aa46-5fa5-9642-d3ed6fa268a1 |  | textbox | 5x Times Rated Trip 180°
text | e17b70a3-b105-528d-a29c-d50c42d4d548 |  | textbox | Tag Number
checkpoint-status |  |  | checkpoint | Test result
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-021 - UPS Installation/Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-021 - UPS Installation/Commissioning - Inspection & Test Plan | ad7023a0-8514-40c0-930e-d3f7428b473d
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | b139ef18-da33-5d6f-bd06-81768423c5a2 |  | textbox | Drawing Ref No. & Revision
text | 6dbeb845-b152-597f-ab98-1c7359a5848e |  | textbox | UPS Make
text | ea9bf974-b6bf-5b76-a57c-d02ffe88cf3e |  | textbox | UPS Model
text | 1d47d7b9-8526-5b8d-b897-7b82fa63a625 |  | textbox | UPS serial number
text | 06ab868a-4db1-508c-826f-b204ec774508 |  | textbox | UPS Capacity
text | c3ee871f-05cf-560f-919d-b489ce5adbe9 |  | textbox | UPS Autonomy Rate
checkpoint-status |  |  | checkpoint | UPS level and mounted securely
checkpoint-status |  |  | checkpoint | UPS rating and Model correct against Spec
checkpoint-status |  |  | checkpoint | Door and escutcheons secure
checkpoint-status |  |  | checkpoint | Check all nuts and bolts for tight
checkpoint-status |  |  | checkpoint | segregation and clearances acceptable
checkpoint-status |  |  | checkpoint | Neutral and earth connections are correct
checkpoint-status |  |  | checkpoint | Cable supports acceptable
checkpoint-status |  |  | checkpoint | Components are correct type and rating
checkpoint-status |  |  | checkpoint | Battery details, Type-
checkpoint-status |  |  | checkpoint | Battery details, Number of Batteries-
checkpoint-status |  |  | checkpoint | Battery details, Total Volts-
checkpoint-status |  |  | checkpoint | Battery installed correctly
checkpoint-status |  |  | checkpoint | Battery isolator installed correctly (if applicable)
checkpoint-status |  |  | checkpoint | Cable access and protection adequate and correct
checkpoint-status |  |  | checkpoint | Operating instructions, labelling and signage installed correct
checkpoint-status |  |  | checkpoint | Load testing completed and battery autonomy correct
checkpoint-status |  |  | checkpoint | Electrical works completed
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | Penetration # |  |  |  |  | Yes | Penetration # | b72a2f9a-d2d6-42d8-af88-e9ad0e71c15b
checkpoint-status |  |  | checkpoint | Penetration Details
text | d9eddd7d-3174-5b3c-a654-eb90c2665f84 |  | textbox | Project Name
text | 4ef05003-a427-56d9-ad68-9ded04759d02 |  | textbox | Project Number
text | 91e61973-f53f-5af4-9e5c-015298059eed |  | textbox | Name
text | e79b80b6-3fbf-5c27-9662-b4e68f2d883d |  | textbox | Test Date
text | f5359ff6-1f7d-5588-b998-f170cfe557af |  | textbox | Penetration Location
checkpoint-status |  |  | checkpoint | Penetration completed and photograph of label taken
select | 7e7d81bd-0c0d-5101-8447-d93d281c7423 |  | dropdown | Orientation: | Ceiling,Floor,Mid Floor,Roof,Wall
select | eaca8879-a342-5302-9710-8fd3964be462 |  | dropdown | Rating of the seal (FRR): | 30 / 30,60 / 60,90 / 90,120 / 120,240 / 240,SM / SM
select | e3bc604a-2423-5d53-ba70-0f4e31c424eb |  | dropdown | Substrate: | Concrete,Masonry/Brick,Plasterboard,Timber,PLT
select | e3f4325d-a721-5f6e-bec8-2f29ba2f0e90 |  | dropdown | Penetration Type: | Cable,Cable bundle,Cable tray,Conduits,Flush Box,Gap seal,Hole,Metal pipe,Paircoils,Plastic pipe,Steel angles/beams
text | b47d2c22-269a-57cd-b537-4662ee9785b5 |  | textbox | Service
text | 9c9ed0c4-910a-51fc-b32a-3bb09935de2b |  | textbox | Thickness of Substrate (mm):
text | 8387e7e1-f5c1-562f-aaa9-b20d078407f0 |  | textbox | Penetration Size (mm):
select | 943d705d-4331-5a1a-baa6-6a2ec8dd80ce |  | dropdown | Product 1 used: | CAFCO,Promaseal A-Acrylic Sealant,Promaseal Conduit Collar,Promaseal Pillow,Promaseal Retrofit Collar,Promaseal Wall Collar,Promaseal Waste Collar,Promaseal wrap,Promastop Unicollar,Promat AG,Sealant,Promat Bulkhead batt,Promat Grafitex paste,Other (specify below)
select | 0b913f87-df3e-5f9e-b5b3-4f7cde0b1b44 | DataPoint is missing 'select' values | dropdown | Specify other product used
select | c55bef84-e244-5e25-8fde-fe0789a4df41 |  | dropdown | Product 2 used: | CAFCO,Promaseal A-Acrylic Sealant,Promaseal Conduit Collar,Promaseal Pillow,Promaseal Retrofit Collar,Promaseal Wall Collar,Promaseal Waste Collar,Promaseal wrap,Promastop Unicollar,Promat AG,Sealant,Promat Bulkhead batt,Promat Grafitex paste,Other (specify below)
select | 7932df6e-7058-5a82-9059-b1ec456385b0 | DataPoint is missing 'select' values | dropdown | Specify other product used
select | 97d5ffb0-8c61-59af-97fb-d21d56a00b70 |  | dropdown | Product 3 used: | CAFCO,Promaseal A-Acrylic Sealant,Promaseal Conduit Collar,Promaseal Pillow,Promaseal Retrofit Collar,Promaseal Wall Collar,Promaseal Waste Collar,Promaseal wrap,Promastop Unicollar,Promat AG,Sealant,Promat Bulkhead batt,Promat Grafitex paste,Other (specify below)
select | 620943e4-0c28-5247-b47f-d471096d6bd7 | DataPoint is missing 'select' values | dropdown | Specify other product used
select | c339583f-4d6a-5567-8f03-5ad122cd372b |  | dropdown | Product 4 used: | CAFCO,Promaseal A-Acrylic Sealant,Promaseal Conduit Collar,Promaseal Pillow,Promaseal Retrofit Collar,Promaseal Wall Collar,Promaseal Waste Collar,Promaseal wrap,Promastop Unicollar,Promat AG,Sealant,Promat Bulkhead batt,Promat Grafitex paste,Other (specify below)
select | 4962a670-ab80-53c1-8e6e-9dccdc16b7c3 | DataPoint is missing 'select' values | dropdown | Specify other product used
select | a7dd4480-7766-5065-8e84-ed494fed6831 |  | dropdown | Product 5 used: | CAFCO,Promaseal A-Acrylic Sealant,Promaseal Conduit Collar,Promaseal Pillow,Promaseal Retrofit Collar,Promaseal Wall Collar,Promaseal Waste Collar,Promaseal wrap,Promastop Unicollar,Promat AG,Sealant,Promat Bulkhead batt,Promat Grafitex paste,Other (specify below)
checklist-flat |  |  | checklist | ITP-020 - Energy Meter Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-020 - Energy Meter Commissioning - Inspection & Test Plan | b8b3f464-7ef1-46fd-be40-12df657d9d6c
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 3e9f5ba5-2f89-57e1-8e3f-460cd8611286 |  | textbox | Project Name
text | e12cbe47-fa9a-5e4d-93a6-963e33f52765 |  | textbox | Project Number
text | b4daa673-d039-5d32-862a-acd44096d6c7 |  | textbox | A' Grade Name
text | de750f4b-057c-54d7-9ce6-876891a34b3c |  | textbox | A' Grade Number
text | 84ba94c4-90c9-572c-af85-3fb8357eb620 |  | textbox | Test Date
text | dee01a09-3f12-5b84-a4bc-793c159768ef |  | textbox | Due Test Date
text | 4448b521-354b-5e0c-a8ba-bcddb6919f3c |  | textbox | Switchboard ID
text | f01d3f0b-c239-5a88-811f-0603070e83dc |  | textbox | Energy Meter Make
text | e965939c-86d5-5771-a593-f37bede979fd |  | textbox | Energy Meter Model
text | 82f321b3-3867-51a5-8b65-e6383ecdc4e8 |  | textbox | Energy Meter Serial Number
checkpoint-status |  |  | checkpoint | Energy Meter installed correctly
checkpoint-status |  |  | checkpoint | Energy Meter Labelled Correctly
checkpoint-status |  |  | checkpoint | All connections correct and secure
checkpoint-status |  |  | checkpoint | All fuse or protection devices installed
checkpoint-status |  |  | checkpoint | Display operating correctly
checkpoint-status |  |  | checkpoint | Voltages displayed correctly
checkpoint-status |  |  | checkpoint | Line Amps displayed correctly
checkpoint-status |  |  | checkpoint | Kilowatts displayed correctly
checkpoint-status |  |  | checkpoint | Interface between BAS connected if applicable
checkpoint-status |  |  | checkpoint | Interface between BAS operating correctly
checkpoint-status |  |  | checkpoint | CT Ratio (of the installed CTs)
text | 9faf77f4-a905-510f-bd61-3faac73dff21 |  | textbox | CT Ratio
checkpoint-status |  |  | checkpoint | Where multipliers are applied to a meter reading after output:
button | 53318905-09fa-573d-bdde-862baa88faf2 |  | button | Does the meter face reading need to be multiplied to calculate the true consumption? | Yes,No
text | 18b054e1-955f-543a-9151-786592bf5f8b |  | textbox | If so, confirm the multiplication factor to be applied to account for the CT Ratio:
checkpoint-status |  |  | checkpoint | Where multipliers are applied to a meter reading prior to output:
button | 652cf43e-6334-547d-9369-3deb44cc7595 |  | button | Can the meter multiplier be interrogated on the meter face? | Yes,No
text | bdf97e5b-ca30-54dd-af7d-dd5cb26afb84 |  | textbox | If so, record the meter multiplier and attach photographic evidence
label | 2c72e1f2-6920-5d90-9f2a-48a2cfaef66a |  | note | If not, use tong-testing or a hand-held meter to compare measured current and meter face current per phase
text | 45fd8cd4-13f2-5b30-ac94-670a7c589c07 |  | textbox | Sub-meter current per phase
text | 5b37a95f-557c-5eeb-8402-d9855c7b8915 |  | textbox | Comparison meter current per phase
checkpoint-status |  |  | checkpoint | Validation test between display and physical test completed
checkpoint-status |  |  | checkpoint | Meter - Current per Phase (Visual reading "Amps") - pass once completed all 3 below
text | 682aaeb7-f5c2-5a55-915a-753137abb17d |  | textbox | Red Phase
text | 6ab24b9e-985c-5ccd-837e-78322a5cdb9c |  | textbox | White Phase
text | f4ea8d4a-0d9f-52d9-876c-a6acf165c343 |  | textbox | Blue Phase
checkpoint-status |  |  | checkpoint | Meter - Current per Phase (Clamp meter reading "Amps") - pass once completed all 3 below
text | a2bb51cb-e92f-55c4-bd39-7f6f8cecceaf |  | textbox | Red Phase
text | e5c17acb-9c8b-5a4a-8132-b68aff57a9de |  | textbox | White Phase
text | 622012aa-78b8-519c-bea6-3baee79f3dac |  | textbox | Blue Phase
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-006 - Communication UTP Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-006 - Communication UTP Installation - Inspection & Test Plan | bf7cebc0-b560-41a4-9e5a-f463e4082173
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 78c88e0e-639b-5506-8a9f-2144e2239a5c |  | textbox | Drawing Ref No. & Revision
text | 27f86e83-5e0a-5010-9def-2ed6b31b9539 |  | textbox | ID
text | 2846432c-1319-58fa-9820-f0ca8d9bc3bc |  | textbox | Cable type
text | e1806398-0930-525f-897f-5d3386dbe769 |  | textbox | Number of cables
checkpoint-status |  |  | checkpoint | Segregation & separation
checkpoint-status |  |  | checkpoint | Correct fixings & supports
checkpoint-status |  |  | checkpoint | Cables labelled at both ends
checkpoint-status |  |  | checkpoint | Patch panel or frame labelled
checkpoint-status |  |  | checkpoint | Test equipment Calibration
checkpoint-status |  |  | checkpoint | Tested to correct standard
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-013 - DSB Installation/Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-013 - DSB Installation/Commissioning - Inspection & Test Plan | c133f510-c946-4c70-81c7-214c6fe6ac36
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 35592f53-e0b6-50ca-ae2b-cb7ac18cba6a |  | textbox | Drawing Ref No. & Revision
text | bb94e63e-aa7b-5a75-9d54-e0126b566caa |  | textbox | Switchboard ID
text | be961562-6f5f-5f14-b635-24738abdfdad |  | textbox | Switchboard location
checkpoint-status |  |  | checkpoint | (Isolate) Supply cables terminated & checked for tight
checkpoint-status |  |  | checkpoint | Sub-circuit cables terminated & checked for tight
checkpoint-status |  |  | checkpoint | Main earth connected & checked for tight
checkpoint-status |  |  | checkpoint | Switchboard vacuum & cleaned
checkpoint-status |  |  | checkpoint | Insulation resistance test on switchboard chassis phase-phase
checkpoint-status |  |  | checkpoint | Insulation resistance test on switchboard chassis phase-earth
checkpoint-status |  |  | checkpoint | Controls operation check (if applicable)
checkpoint-status |  |  | checkpoint | Overload settings checked & correct (if applicable)
checkpoint-status |  |  | checkpoint | Operation of main switch/isolator
checkpoint-status |  |  | checkpoint | Operation of sub-circuit protection device(s)
checkpoint-status |  |  | checkpoint | Labels installed
checkpoint-status |  |  | checkpoint | All terminations tightened & checked
checkpoint-status |  |  | checkpoint | RCD's tested
checkpoint-status |  |  | checkpoint | Switchboard schedule completed and installed
checkpoint-status |  |  | checkpoint | Visual inspection of all sub-circuits to confirm all cables are terminated
checkpoint-status |  |  | checkpoint | Visual inspection of cables coiled up ceiling and junction boxed
checkpoint-status |  |  | checkpoint | BMS Interface connection terminated (if applicable)
checkpoint-status |  |  | checkpoint | Test result
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
text | 6575c063-93f6-5ea4-be08-c832839f2756 |  | textbox | A' Grade Number
text | 0c6f95b4-a2e8-5264-be4c-8696d9a26c09 |  | textbox | A' Grade Name
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | RCD Test - Switchboard Details |  |  |  |  | Yes | RCD Test - Switchboard Details | c1c5b258-98cf-4243-be8a-ff8e290eb12e
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | cf8987bb-9152-5fc9-aff5-628c536a6e0f |  | textbox | Project Name
text | 171203f8-7c48-53d7-bcab-4a5cad4be0da |  | textbox | Project Number
text | ba68ccf9-c227-593e-95c1-042c565facc7 |  | textbox | A' Grade Name
text | d46520d8-83a3-5a98-b3c2-e0d7606e780d |  | textbox | A' Grade Number
text | 05f628a5-9ea4-54f5-859e-04a8d9e13f83 |  | textbox | Test Date
text | 751b8ae3-5267-5016-96e8-17bdc864fc54 |  | textbox | Due Test Date
text | e745da5c-ec81-59c0-a9e7-8651e15024e6 |  | textbox | Switchboard ID
checklist-flat |  |  | checklist | ITP-018 - Lighting Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-018 - Lighting Installation - Inspection & Test Plan | c3de036d-0d13-4ede-b982-1f4d68a719be
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 7a34cca2-dd31-5365-8579-23b8fad4ade8 |  | textbox | Drawing Ref No. & Revision
text | fec2442c-5f69-5ba0-b728-3dfbfee84266 |  | textbox | Location/Area
checkpoint-status |  |  | checkpoint | Correct size and type
checkpoint-status |  |  | checkpoint | Any Damage
checkpoint-status |  |  | checkpoint | Correct Light Temperature - select from below
select | 684d3ecc-6e0d-5fb6-9a1b-f1f5b7c82271 |  | dropdown | Select light temperature | Warm White: 2600K to 3200K,Cool White: >3200K to 4500K,Daylight: >4500K
checkpoint-status |  |  | checkpoint | Correct diffuser/reflector
checkpoint-status |  |  | checkpoint | Correct operation
checkpoint-status |  |  | checkpoint | Correct circuit/ DB designation
checkpoint-status |  |  | checkpoint | Correct Labelling
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-014 - Sub-Main Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-014 - Sub-Main Commissioning - Inspection & Test Plan | c653bdd0-7ecb-4867-ac18-bb7ff76c49c7
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | c8ad5373-1e40-5361-993f-241b93fc1c01 |  | textbox | Drawing Ref No. & Revision
text | 5ef9f5c9-4d33-5152-9237-5c8a04d338a9 |  | textbox | Submain from (Origin)
text | dd26859d-4b25-5528-a02b-944cce6fcef6 |  | textbox | Submain to (destination)
select | 791e0cc2-1314-5c71-8e12-cadb8822bcbe |  | dropdown | Conductor type | Copper,Aluminium
select | 7cb75a81-7955-5f3c-bb7b-7d6af428b1e7 |  | dropdown | Conductor size | 16mm,25mm,35mm,50mm,70mm,95mm,120mm,150mm,185mm,240mm,300mm,400mm,500mm,630mm
select | f9d245ab-b9c7-5e9b-82f7-096836d5c6ea |  | dropdown | Number of cables pre phase | 1,2,3,4
boolean | b6b7c7af-4d1b-5fd3-b6f4-dcce4921480e |  | tickbox | All terminations complete & checked for tight
boolean | 454231e8-1543-5bfe-8d6f-7a4869a9f45f |  | tickbox | All cables labelled
boolean | 783f88a9-3827-58da-b4d7-56c837facd75 |  | tickbox | Phase rotation correct
boolean | b966276f-175a-5277-8909-6f0f0dcd406b |  | tickbox | Polarity test correct
boolean | b9d4c581-1054-58d8-ab08-7df83f26efe3 |  | tickbox | Insulation resistance tests
boolean | 2ef7e24c-4e45-54a9-9bf9-a30ade55084b |  | tickbox | Red & White
boolean | 66618e66-ac7e-545a-935f-857bae1f3e22 |  | tickbox | Red & Blue
boolean | ee6d0e55-1cd3-5952-9cf0-45f193ace53e |  | tickbox | Blue & White
boolean | 5aa6339b-6069-5d8c-8d95-630b6092344f |  | tickbox | Red to Neutral
boolean | bca7572a-5cf0-56d0-b0fc-3ef949e1ecb2 |  | tickbox | White to Neutral
boolean | 4c930b72-da7d-5f93-823e-621f36c0273e |  | tickbox | Blue to Neutral
boolean | fe4c3950-ee4b-52f3-9bd7-f33f03e0eaa7 |  | tickbox | Red to Earth
boolean | 4813b010-9a41-5b6c-b82b-7e6ec394c074 |  | tickbox | White to Earth
boolean | 0d2c7a92-8e33-5101-a434-ba3ea73cb6ee |  | tickbox | Blue to Earth
boolean | 6451eda6-ec02-55c7-bc6b-f2110eea2549 |  | tickbox | Neutral to Earth
boolean | d7885a4d-4bb0-5a14-b11c-56e573fa87a0 |  | tickbox | Earth Continuity
boolean | 168c7032-367f-5d3c-8ce0-6c369a22c270 |  | tickbox | Visual Inspection
checkpoint-status |  |  | checkpoint | Test result
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
text | 1862f121-91b4-57f8-83cd-ff1dbb433c49 |  | textbox | A' Grade Number
text | f879192c-4631-5fd3-89ba-f220c7020714 |  | textbox | A' Grade Name
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | Appliance Test & Tag |  |  |  |  | Yes | Appliance Test & Tag | ca8e08dc-b674-4f50-bf2a-f1ce50b73893
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 9f35f925-5460-5fed-8d70-aba39f462537 |  | textbox | Project Name
text | e3c9f8f2-26f3-57b3-8702-4cb8c9adff40 |  | textbox | Project Number
text | 0f9a4e6e-4acb-5e8b-b64a-f9747b2940e3 |  | textbox | Company Name Tagging for
text | b5b38c61-d44d-59ed-aee9-7ba729f249da |  | textbox | A' Grade Name
text | 93fba166-a87c-54d8-9ef3-f84e7b35b207 |  | textbox | A' Grade Number
text | c985f540-d3c3-5211-a4ec-8a79ff2b0a0f |  | textbox | Test Date
text | ae065e66-db70-5bc1-a427-4bb92e023d19 |  | textbox | Due Test Date
select | e8ba8e3b-4e14-58cc-80ab-05d619377356 |  | dropdown | Tag Colour | Dec - Feb = Red,Mar - May = Green,June - Aug = Blue,Sept - Nov = Yellow
text | bc4bde27-f58f-5ce5-a142-8e94344958b9 |  | textbox | Tag number
text | d4d69ca1-d044-5ae8-b6b6-97735148021b |  | textbox | Equipment
checkpoint-status |  |  | checkpoint | Test result
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-025 - Generator Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-025 - Generator Commissioning - Inspection & Test Plan | ceb3f6ed-095b-4149-9a04-981f5d8e3253
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | dbd7a0c2-a646-5aa0-bfe4-3bd81b9ab126 |  | textbox | Drawing Ref No. & Revision
text | 2968e431-1d5d-50a9-8e52-ee733b600bba |  | textbox | Switchboard Name with Generator connection
checkpoint-status |  |  | checkpoint | Advise Client of disruption to permanent power and approximate outage times.
checkpoint-status |  |  | checkpoint | Approval received from Client to proceed with Black Start
checkpoint-status |  |  | checkpoint | Check Generator Fuels Levels
checkpoint-status |  |  | checkpoint | Final Check of all Electrical Connections at Generator and Automatic Transfer Switch
checkpoint-status |  |  | checkpoint | Obtain latest Run On Time settings for Generator required for project - Check programmed settings reflect
checkpoint-status |  |  | checkpoint | Simulate Loss of Permanent Power via Phase Fail and ATS Logic Controller
checkpoint-status |  |  | checkpoint | Observe operation of ATS
checkpoint-status |  |  | checkpoint | Confirm Run Status OK - ie Zero warnings, Fault Conditions etc.
checkpoint-status |  |  | checkpoint | Confirm Generator Supply to all Essential Services.
checkpoint-status |  |  | checkpoint | Reinstate permanent power - Confirm Time for Generator Run On is correct and record below
text | 185e989d-1152-5e11-b467-9c695255bef1 |  | textbox | Generator run on time
checkpoint-status |  |  | checkpoint | Check reinstatement of permanent power.
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-017 - RCD Commissioning - Inspection & Test Plan |  |  |  |  | Yes | ITP-017 - RCD Commissioning - Inspection & Test Plan | dd37e516-8bf7-4eb6-aea7-ae3462050657
checkpoint-status |  |  | checkpoint | RCD Details
select | bb1efc47-9250-57e0-96d4-fd31599d1fa2 |  | dropdown | RCD type | 10mA,30mA,100mA
text | fb563bc3-1967-5946-bcc8-4ae01ec5623e |  | textbox | Protection Device Number
button | 3cdaf213-79b7-5d50-a658-2641fac7aecb |  | button | RCD test button working | Yes, No
label | d821752e-b95f-5507-92f7-64d313b91186 |  | note | 1/2 Rated Trip 0° - ∞
label | 438f507b-dbe1-5306-910e-7d217acf6f0c |  | note | 1/2 Rated Trip 180° - ∞
text | ff53fc72-820f-5d67-9bb5-bba182e40fba |  | textbox | Rated Trip 0°
text | 80ee08ce-8fcd-55ef-8221-397f081cf72c |  | textbox | Rated Trip 180°
text | 17be0417-a86d-56ca-893a-8f04eaa831e8 |  | textbox | 5x Times Rated Trip 0°
text | 533b2f1b-be94-543e-8ceb-1dbc83e66c60 |  | textbox | 5x Times Rated Trip 180°
checkpoint-status |  |  | checkpoint | Test result
text | 66ede362-a606-5d77-aba1-8219d4bbaece |  | textbox | A' Grade Number
text | 821d218d-8acf-5e57-bed9-5a0f6e25d882 |  | textbox | A' Grade Name
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-007 - Communication Fibre Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-007 - Communication Fibre Installation - Inspection & Test Plan | e3830b6f-3e7a-4cd0-bbae-95d47740a6d2
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 1fc4b196-980b-538c-84e5-7951691c0f03 |  | textbox | Drawing Ref No. & Revision
text | 00dadb0e-d97e-5efd-8973-6dd385db800c |  | textbox | ID
text | b2161829-84b7-5d34-be57-41df71f0622c |  | textbox | Cable type
text | 86aad6ac-fc43-5b6b-bd3a-57d98b8de5de |  | textbox | Number of cables
checkpoint-status |  |  | checkpoint | Segregation & separation
checkpoint-status |  |  | checkpoint | Correct fixings & supports
checkpoint-status |  |  | checkpoint | Cable is labelled at both ends
checkpoint-status |  |  | checkpoint | Correct Fibre connections installed
checkpoint-status |  |  | checkpoint | Fibre terminated & labelled
checkpoint-status |  |  | checkpoint | Test equipment Calibration
checkpoint-status |  |  | checkpoint | Tested to correct standard
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-004 - Cable Tray Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-004 - Cable Tray Installation - Inspection & Test Plan | f0bbedf2-20c7-4ea3-a152-3acccb7961b1
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | c8ab0c7b-9852-5614-872b-f8b41651eef4 |  | textbox | Drawing Ref No. & Revision
text | 8d3aa57e-efd3-528f-9c99-479e80061b3f |  | textbox | ID
text | 233d46d9-9b85-5adc-94e9-72cd5bc6dfd4 |  | textbox | Origin
text | 5f445eeb-dca5-5a27-ba61-e68d95936862 |  | textbox | Destination
text | 69d88cf8-ddd8-5cd2-bde3-5f019eff9ed2 |  | textbox | Number of cable trays and size
checkpoint-status |  |  | checkpoint | Support & spacing correct
checkpoint-status |  |  | checkpoint | Supports & fixings tight
checkpoint-status |  |  | checkpoint | Tray level
checkpoint-status |  |  | checkpoint | Tray earthed where required
checkpoint-status |  |  | checkpoint | Tray penetrations fire or smoke sealed
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-flat |  |  | checklist | ITP-008 - Communications Cabinet(s) Installation - Inspection & Test Plan |  |  |  |  | Yes | ITP-008 - Communications Cabinet(s) Installation - Inspection & Test Plan | f58c4b3d-162f-465d-8377-a17c4f81d2a7
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | 73ab22ea-0236-531a-9810-ee9b56686410 |  | textbox | Drawing Ref No. & Revision
text | cf942a00-29ba-5f77-b22d-e1894a496d78 |  | textbox | ID
text | 11941170-7a4a-5951-badb-39de5024a1e7 |  | textbox | Cabinet model and size
text | 8c87e1ba-5a81-5d63-b328-580298fb9939 |  | textbox | Number of cabinets
checkpoint-status |  |  | checkpoint | Position and location correct
checkpoint-status |  |  | checkpoint | Level and fixed into position
checkpoint-status |  |  | checkpoint | Earthing correct
checkpoint-status |  |  | checkpoint | All accessories provided and installed
checkpoint-status |  |  | checkpoint | Cabinet ID labels installed
checkpoint-status |  |  | checkpoint | All cabinets bolted together where applicable
checkpoint-status |  |  | checkpoint | Power rails installed and plugged in
checkpoint-status |  |  | checkpoint | Tested to correct standard
checkpoint-status |  |  | checkpoint | Area clean & safe
checkpoint-status |  |  | checkpoint | Mark up on drawings
checkpoint-status |  |  | checkpoint | Signature - Foreman/Installer sign off attached below
checklist-sectioned |  |  | checklist | Dry Fire Wiring Installation |  |  |  |  | Yes | Dry Fire Wiring Installation | fcce33ae-dc85-4098-8e64-762f57637531
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details - pass once entered below
text | f4324855-4a90-586e-b3bf-a47064ed6f00 |  | textbox | Project Name
text | 867099a5-629e-57bd-85ae-ac9dfd069b9d |  | textbox | Project Number
text | 2743e667-7176-5642-9c34-2fc00a9eaef5 |  | textbox | Name
text | 798a3c1b-a92e-567e-b38b-3b40e2dd2fc2 |  | textbox | Date
text | 4e2cb2af-6ba3-5273-be7f-3df5b0ffb26f |  | textbox | Location
checkpoint-group |  |  | section | Cables
checkpoint-status |  |  | checkpoint | Appropriate cable ties / fixings used
checkpoint-status |  |  | checkpoint | Adequate length on cable drops
checkpoint-status |  |  | checkpoint | Segregation of minimum 50mm from LV
checkpoint-status |  |  | checkpoint | All cables to be per approved vendor list
checkpoint-status |  |  | checkpoint | All cables shall be minimum size of 0.75mm
checkpoint-status |  |  | checkpoint | Detection cabling twisted pair
checkpoint-status |  |  | checkpoint | EWIS / BOWS cabling flat pair
checkpoint-group |  |  | section | Conduits
checkpoint-status |  |  | checkpoint | Conduit as specified (e.g. HD/MD/COMMS)
checkpoint-status |  |  | checkpoint | Adequately saddled/supported
checkpoint-status |  |  | checkpoint | Galvanised conduit deburred
checkpoint-status |  |  | checkpoint | All fixtures fitted with lids and screws
checkpoint-status |  |  | checkpoint | Sets and/or bends neat and free from kinks
checkpoint-status |  |  | checkpoint | Expansion joints as required
checkpoint-group |  |  | section | Catenary Wire
checkpoint-status |  |  | checkpoint | Clear of other services
checkpoint-status |  |  | checkpoint | Secured at suitable intervals
checkpoint-status |  |  | checkpoint | Adequate tension in wire
checkpoint-group |  |  | section | Tray/Duct
checkpoint-status |  |  | checkpoint | Fixings supports suitable
checkpoint-status |  |  | checkpoint | Cuts deburred
checkpoint-status |  |  | checkpoint | Fittings correct type
checkpoint-status |  |  | checkpoint | Duct lids fitted
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | 28d7ae06-544e-5c25-af17-b755ee5642c4 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)