## Resources
type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist | Gas Pipe Line Test Sheet |  |  |  |  | Yes | Gas Pipe Line Checklist | 0228c9cf-96da-4179-8fdd-9ffeaa986625
section | Job Details
checkpoint | Job details complete
textbox | Job:
textbox | Gasfitter:
textbox | Date:
textbox | Site Address:
dropdown | Gas Installation "Safe To Use" | No,Yes
textbox | Risk Classification
textbox | Part/Whole Installation
textbox | Gas Type
textbox | Certifying Gasfitter
dropdown | Work done in accordance with means of compliance (AS/NZS 5601.1:2010 part 1) | No,Yes
section | Test Details
textbox | Work undertaken:
textbox | Test location:
checkpoint | Test procedure AS/NZS 5601.1:2010 Appendix E
textbox | Date:
checkpoint | Leakage test of Existing installation E6
textbox | Test Pressure: |  |  | kPa
textbox | Duration:
textbox | Drop/raise
checkpoint | Final Connection Test E7
textbox | Test Pressure: |  |  | kPa
textbox | Duration:
textbox | Drop/raise
textbox | Working Pressure |  |  | kPa
checklist | 1st Fix - LPG |  |  |  |  | Yes | 1st Fix - LPG QA Sheet | 0940e520-1a50-4c2c-97d9-69bcb99f098e
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check that the correct pipe sizing is complete to each fixture
checkpoint | Check that the wingbatts are installed at the correct height
checkpoint | Check that seismic restraints are installed
checkpoint | Check that the fixing's are installed at correct height
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Check the pipe labels are on
checklist | Water Quality Testing |  |  |  |  | Yes | Checklist - Water Quality Testing | 10091958-9aff-4d28-861d-5c80a3722149
checkpoint
textbox | Date
textbox | Test point Location
checkpoint | Lab results confirmed and attached
checkpoint | QA Complete
checkpoint | Final Sign Off
checklist | Pipework Pressure Test Sheet - Water: |  |  |  |  | Yes | Test Sheet - Pipework Pressure - Water | 10156f40-5f6e-4bd2-a2d9-be6e49eee604
checkpoint | Details Complete
textbox | Consent Number: ABA
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
checkpoint | Testing
note | Required Test Pressure: Static Water Test
note | Required Test Time: 1/2 hour (as per NZBC and ASNZ 3500)
textbox | Date:
textbox | Start Pressure: |  |  | (kPa)
textbox | Finish Pressure: |  |  | (kPa)
checkpoint | Signoff
checklist | Flushing Valves |  |  |  |  | Yes | Checklist - Flushing Valves | 16cf727f-f1c5-4dfc-9473-4c9749121a69
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Confirm Operation
checkpoint | GPF Flow Ring Installed (colour)
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | Programmed Maintenance Checklist |  |  |  |  | Yes | Programmed Maintenance Checklist | 1dacc987-363b-40c5-af15-694d6af17279
checkpoint | Details
textbox | Maintenance Number:
button |  | Area -
checkpoint | Having recieved approval to carry out the maintenance, ask the department heads if there have been any problems with the plumbing systems
checkpoint | coordinate with the electrical trade to carry out the maintenance at the same time
checkpoint | Inspect the integrity of the portaboe hot and cold pipework
checkpoint | Inspect the integrity of the waste water pipe work
checkpoint | Inspect the integrity of the HWC for leaks
checkpoint | Inspect the integrity of the HWC valves
checkpoint | Inspect the integrity of the TMV temperatures
checkpoint | Inspect the integrity of the toilet flush
checkpoint | Inspect the integrity of the pumps
checkpoint | Inspect the integrity of the trap primers
checkpoint | Inspect the integrity of the suction pipework
checkpoint | Inspect the integrity of the LPG pipework and valving
checkpoint | Inspect the integrity of the basins and sinks
checkpoint | Inspect the integrity of the suction pipe work
checkpoint | Inspect the integrity of the plaster traps
checkpoint | Inspect the integrity of the foul sewer and water systems
checklist | Sanitary drainage below slab - water and waste pipe work |  |  |  |  | Yes | Sanitary drainage below slab - water and waste pipe work QA Sheet | 1ea5a277-69f1-4310-a047-82806aeada2e
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check pipe brackets conform to PS1 design
checkpoint | Check maximum spacing of brackets not exceded.
checkpoint | Drains installed at correct grades/fall ratios
checkpoint | Check that risers are in the correct location and secure
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | DCC inspection complete
checklist | Sanitary Drainage Below Slab: |  |  |  |  | Yes | Checklist - Sanitary Drainage | 2a04f69d-9afe-41b8-9643-1e6e26b63827
section | Details
checkpoint | Details Complete
textbox | Consent Number: ABA
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
section | Water and Waste Pipe Work QA
checkpoint | Area tidy and ready to start
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Confirm Pipe bedding at least 75mm compacted thickness
checkpoint | Confirm pipe bedding material AP20
checkpoint | Pipe work layed to invert and grades as per approved shop drawings.
checkpoint | Check that risers are in the correct location and secure
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | DCC inspection complete
checkpoint | Trenches backfilled and compacted AP65. Marking tape installed
checkpoint | QA sheet completed and loaded in system
checklist | Backflow Preventer |  |  |  |  | Yes | Checklist - Backflow Preventer | 2d984892-872f-4e83-8c96-289a2e5497d6
checkpoint
textbox | Date
textbox | Valve Number
textbox | Location
checkpoint | Result (confirm passed)
checkpoint | Service label attached to RPZ
checkpoint | IQP certificate filed
checkpoint | Final Sign Off
checklist | 1st Fix - RO Water pipe work |  |  |  |  | Yes | 1st Fix - RO Water pipe work QA Sheet | 393756dc-e1c1-4771-8c96-182bb8197265
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check that the correct water and pipe sizing is complete to each fixture
checkpoint | Check that the wingbatts are installed at the correct height
checkpoint | Check that seismic restraints are installed
checkpoint | Check that the waste pipe is the correct location
checkpoint | Check that the fixing's are installed at correct height
checkpoint | Check that the pipe insulation is installed
checkpoint | Check that the acoustic insulation is installed
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | Check the pipe labels are on
checklist | 1st Fix - Water pipe work |  |  |  |  | Yes | 1st Fix - water pipe work QA Sheet | 3ac2da9e-209e-4f20-b8ff-cb64d8cbf30a
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check that the correct water and pipe sizing is complete to each fixture
checkpoint | Check that the wingbatts are installed at the correct height
checkpoint | Check that seismic restraints are installed
checkpoint | Check that the waste pipe is the correct location
checkpoint | Check that the fixing's are installed at correct height
checkpoint | Check that the pipe insulation is installed
checkpoint | Check that the acoustic insulation is installed
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | Check the pipe labels are on
checklist | Trap Primer |  |  |  |  | Yes | Checklist - Trap Primer | 47c7ef5a-1e74-4c35-bb27-725348b4b059
checkpoint
textbox | Date
textbox | Trap Primer Number
textbox | Location
checkpoint | Water system complete and charged
checkpoint | Electrical supply commissioned
checkpoint | On/Off times set.(tick)
checkpoint | "Test button" Press confirm operation.
checkpoint | QA Complete
checkpoint | Final Sign Off
checklist | LPG Meters |  |  |  |  | Yes | Checklist - LPG Meters | 49f2a513-727b-4989-8283-44718709a4f7
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Confirm operation with BMS
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | 1st Fix - RO Water pipe work |  |  |  |  | Yes | QA Sheet - 1st Fix - RO Water pipe work | 5a89a564-26e3-48fc-ae40-0664da136e10
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check that the correct water and pipe sizing is complete to each fixture
checkpoint | Check that the wingbatts are installed at the correct height
checkpoint | Check that seismic restraints are installed
checkpoint | Check that the waste pipe is the correct location
checkpoint | Check that the fixing's are installed at correct height
checkpoint | Check that the pipe insulation is installed
checkpoint | Check that the acoustic insulation is installed
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | Check the pipe labels are on
checklist | LPG system |  |  |  |  | Yes | Checklist - LPG System | 5e7e6873-f98f-4010-9f4d-33626a750f67
checkpoint
textbox | Date
textbox | Location
checkpoint | Test certificate filed
checkpoint | Pressures set. Record below
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | Sanitary drainage/SuctionTest Sheet - |  |  |  |  | Yes | (Dental School) Add Sanitary drainage/Suction Test Sheet | 6bb65c56-81ca-44c5-b3fb-5757957d7ef5
checkpoint | Details Complete
textbox | Consent Number: ABA
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
checkpoint | Testing
note | Required Test Pressure: Static Head
note | Required Test Time: 10 min (min) (as per NZBC G12 and ASNZ 3500)
textbox | Date:
textbox | Water Level Check 1
textbox | Water Level Check 2 |  |  | (kPa)
checkpoint | Signoff
checklist | Sanitary drainage below slab - water and waste pipe work |  |  |  |  | Yes | QA Sheet - Sanitary drainage below slab - water and waste pipe work | 6d389d02-3611-4956-ad05-d076516d8183
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check pipe brackets conform to PS1 design
checkpoint | Check maximum spacing of brackets not exceded.
checkpoint | Drains installed at correct grades/fall ratios
checkpoint | Check that risers are in the correct location and secure
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | DCC inspection complete
checklist | Water Strainers |  |  |  |  | Yes | Checklist - Water Strainers | 736b0fe7-6266-490f-aeba-1229403e8b89
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Size (Micron's)
checkpoint | Strainer mesh replaced
checkpoint | QA Complete
checkpoint | Final Sign Off
checklist | Hot Water Clorafiers |  |  |  |  | Yes | Checklist - Hot Water Clorafiers | 77564cfd-69e0-4ec1-bfc1-fb74436dc73f
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Temperature entering
textbox
checkpoint | Temperature leaving
textbox
checkpoint
textbox | Check time
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | Basin Sensor Taps |  |  |  |  | Yes | Checklist - Second Fit QA | 81d1dfad-4d59-4c78-a393-be0b3f24f995
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Confirm Operation
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | [5 empty] | Yes | Add Folder | 8509b27e-52e3-4407-8328-3805c8421ff0
checklist | Final Sign Off Slab Grids |  |  |  |  | Yes | Add Final Sign Off Slab Grids Checklist | 86bdf911-63e7-4773-b65f-ffdb7777b83d
section | Slab Grids QA
checkpoint | Steel clips ready for mesh tie down
checkpoint | Pipe penetrations lagged to slab height
checkpoint | Checked for damage at slab level all ok
checkpoint | Water test holding
section | Sign Off
checkpoint | Foleys Signoff
checklist | Hot Water Return Pumps |  |  |  |  | Yes | Checklist - Hot Water Return Pumps | 8e447c4e-47be-442a-bda2-68301e42e32c
checkpoint
textbox | Date
textbox | Pump Number
textbox | Location
checkpoint | Electrical Complete
checkpoint | Water Heating operating
checkpoint | System Balanced
checkpoint
textbox | Pressure diffrence across pump
textbox | Final Flow Rate
checkpoint | QA Complete
checkpoint | Final Sign Off
checklist | Water Meters |  |  |  |  | Yes | Checklist - Water Meters | 997031c3-f399-4538-a5a8-25d97d12713e
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Confirm operation with BMS
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | Hot Water Clorafiers |  |  |  |  | Yes | Checklist - Hot Water Clorafiers | a63d937c-1552-4054-b36c-2bf96e028725
checkpoint
textbox | Date
textbox | Item
textbox | Location
checkpoint | Temperature entering
textbox
checkpoint | Temperature leaving
textbox
checkpoint
textbox | Check time
checkpoint | QA complete
checkpoint | Final Sign Off
checklist | 1st Fix - LPG |  |  |  |  | Yes | QA Sheet - 1st Fix - LPG | ab28d90e-07e8-4593-b55a-07ada6fd85dd
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check that the correct pipe sizing is complete to each fixture
checkpoint | Check that the wingbatts are installed at the correct height
checkpoint | Check that seismic restraints are installed
checkpoint | Check that the fixing's are installed at correct height
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Check the pipe labels are on
checklist | Sanitary Drainage Below Slab: |  |  |  |  | Yes | Add Sanitary Drainage Checklist | ac5a6f32-07f0-46ec-baef-1eb335832b98
section | Details
checkpoint | Details Complete
textbox | Consent Number: ABA
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
section | Water and Waste Pipe Work QA
checkpoint | Area tidy and ready to start
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Confirm Pipe bedding at least 75mm compacted thickness
checkpoint | Confirm pipe bedding material AP20
checkpoint | Pipe work layed to invert and grades as per approved shop drawings.
checkpoint | Check that risers are in the correct location and secure
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | DCC inspection complete
checkpoint | Trenches backfilled and compacted AP65. Marking tape installed
checkpoint | QA sheet completed and loaded in system
checklist | Pipework Pressure Test Sheet - |  |  |  |  | Yes | (Dental School) Add Pipework Pressure Test Sheet - Water/LPG | b8efc79d-673a-4fa1-9b2c-ebe442bca291
checkpoint | Details Complete
textbox | Consent Number: ABA
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
checkpoint | Testing
note | Required Test Pressure: 1500kpa (min)
note | Required Test Time: 15 min (min) (as per NZBC G12 and ASNZ 3500)
textbox | Date:
textbox | Start Pressure: |  |  | (kPa)
textbox | Finish Pressure: |  |  | (kPa)
checkpoint | Signoff
checklist | Pipework Pressure Test Sheet - Water: |  |  |  |  | Yes | Add Pipework Pressure Test Sheet - Water | bd7e1b2a-938a-4519-9ef2-d4869ae8b162
checkpoint | Details Complete
textbox | Consent Number: ABA
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
checkpoint | Testing
note | Required Test Pressure: Static Water Test
note | Required Test Time: 1/2 hour (as per NZBC and ASNZ 3500)
textbox | Date:
textbox | Start Pressure: |  |  | (kPa)
textbox | Finish Pressure: |  |  | (kPa)
checkpoint | Signoff
checklist | Hot Water Balancing Valves |  |  |  |  | Yes | Checklist - Hot Water Balancing Valves | c85c1340-2f49-4e68-a162-fc3a4babb2fe
checkpoint
textbox | Date
textbox | Location
textbox | Valve Number
checkpoint | Hot Water Circulating
checkpoint | Balanced Temperature
checkpoint | QA Complete
checkpoint | Final Sign Off
checklist | Pressure Limiting Valves |  |  |  |  | Yes | Checklist - Pressure Limiting Valves | cd27064b-3d5f-45b1-a6c0-dcb3122fd23a
checkpoint
textbox | Date
textbox | Valve Number
textbox | Location
checkpoint | Pressure Set
checkpoint | Set Pressure (KPA)
textbox
checkpoint | QA Complete
checkpoint | Final Sign Off
checklist | Sanitary drainage - waste pipe work |  |  |  |  | Yes | QA Sheet - Sanitary drainage - waste pipe work | ce6fd15a-540e-440a-94d9-0445f910b60a
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check pipe brackets conform to PS1 design
checkpoint | Check maximum spacing of brackets not exceded.
checkpoint | Drains installed at correct grades/fall ratios
checkpoint | Check that risers are in the correct location and secure
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | DCC inspection complete
checklist | Sanitary drainage/SuctionTest Sheet - |  |  |  |  | Yes | Test Sheet - Sanitary drainage/Suction | d51c1d2d-5b14-4fb3-bc30-ce245ac726af
checkpoint | Details Complete
textbox | Consent Number:
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
checkpoint | Testing
note | Required Test Pressure: Static Head
note | Required Test Time: 10 min (min) (as per NZBC G12 and ASNZ 3500)
textbox | Date:
textbox | Water Level Check 1
textbox | Water Level Check 2 |  |  | (kPa)
checkpoint | Signoff
checklist | Room - |  |  |  |  | Yes | Checklist - Demolition Fixtures | d5bd0a5c-837c-448f-bcb4-8f0cae443f54
checkpoint | Details Completed
textbox | Location:
textbox | Drawing:
textbox | Plumber:
note | What area within space that can be demoed
tickbox | Ceiling Space
tickbox | Room area
checkpoint | Cold water services have been isolated and capped
checkpoint | Hot water services have been isolated and capped
checkpoint | Trap's have been removed and desposed of
checkpoint | Waste pipes have been capped
checkpoint | LPG services have been isolated, purged and capped
checkpoint | Compressed Air services have been purged and isolated
checkpoint | All services have been isolated and all fixtures are now safe to be removed
checklist | Room - |  |  |  |  | Yes | Add Demolition Fixtures Checklist | e0e6963c-d756-403f-a806-6a07e04ab5c7
checkpoint | Details Completed
textbox | Location:
textbox | Drawing:
textbox | Plumber:
note | What area within space that can be demoed
tickbox | Ceiling Space
tickbox | Room area
checkpoint | Cold water services have been isolated and capped
checkpoint | Hot water services have been isolated and capped
checkpoint | Trap's have been removed and desposed of
checkpoint | Waste pipes have been capped
checkpoint | LPG services have been isolated, purged and capped
checkpoint | Compressed Air services have been purged and isolated
checkpoint | All services have been isolated and all fixtures are now safe to be removed
checklist | Pipework Pressure Test Sheet - |  |  |  |  | Yes | Test Sheet - Pipework Pressure - Water/LPG | e9a281d5-44fb-4f65-a4d3-fb85b22813e3
checkpoint | Details Complete
textbox | Consent Number: ABA 2016-513
textbox | Location:
textbox | Drawing:
textbox | Plumber:
textbox | Date:
checkpoint | Testing
note | Required Test Pressure: 1500kpa (min)
note | Required Test Time: 15 min (min) (as per NZBC G12 and ASNZ 3500)
textbox | Date:
textbox | Start Pressure: |  |  | (kPa)
textbox | Finish Pressure: |  |  | (kPa)
checkpoint | Signoff
checklist | Gas Pipe Line Test Sheet |  |  |  |  | Yes | Gas Pipe Line Checklist | ed6b8ff4-510b-43fb-8680-328240b788b1
section | Job Details
checkpoint | Job details complete
textbox | Job:
textbox | Gasfitter:
textbox | Date:
textbox | Site Address:
dropdown | Gas Installation "Safe To Use" | No,Yes
textbox | Risk Classification
textbox | Part/Whole Installation
textbox | Gas Type
textbox | Certifying Gasfitter
dropdown | Work done in accordance with means of compliance (AS/NZS 5601.1:2010 part 1) | No,Yes
section | Test Details
textbox | Work undertaken:
textbox | Test location:
checkpoint | Test procedure AS/NZS 5601.1:2010 Appendix E
textbox | Date:
checkpoint | Leakage test of Existing installation E6
textbox | Test Pressure: |  |  | kPa
textbox | Duration:
textbox | Drop/raise
checkpoint | Final Connection Test E7
textbox | Test Pressure: |  |  | kPa
textbox | Duration:
textbox | Drop/raise
textbox | Working Pressure |  |  | kPa
checklist | Sanitary drainage - waste pipe work |  |  |  |  | Yes | Sanitary drainage - waste pipe work QA Sheet | f24a4b05-6e5d-4545-95f3-d6c3650b7192
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check pipe brackets conform to PS1 design
checkpoint | Check maximum spacing of brackets not exceded.
checkpoint | Drains installed at correct grades/fall ratios
checkpoint | Check that risers are in the correct location and secure
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | DCC inspection complete
checklist | 1st Fix - Water pipe work |  |  |  |  | Yes | QA Sheet - 1st Fix - water pipe work | fa7ea125-6a62-499e-a6c0-48dce6c76ee2
checkpoint | Check pipework is installed as per listed drawings
checkpoint | Check that the correct water and pipe sizing is complete to each fixture
checkpoint | Check that the wingbatts are installed at the correct height
checkpoint | Check that seismic restraints are installed
checkpoint | Check that the waste pipe is the correct location
checkpoint | Check that the fixing's are installed at correct height
checkpoint | Check that the pipe insulation is installed
checkpoint | Check that the acoustic insulation is installed
checkpoint | Check that the pressure test is complete
checkpoint | Check that the test sheet is filled out
checkpoint | Council inspection complete
checkpoint | Check the pipe labels are on
checklist | Thermal Mixing Valves |  |  |  |  | Yes | Checklist - Thermal Mixing Valves | fb16baec-ce33-4be2-915d-76738b72f13b
checkpoint
textbox | Date
textbox | Valve Number
textbox | Location
checkpoint | Set Temperature. °C
checkpoint | Lock cap fitted
checkpoint | QA complete
checkpoint | Final Sign Off