## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITR 002 Sewer Drainage |  |  |  |  | Yes | ITR 002 Sewer Drainage | 0d3670d7-61bf-4444-8cf2-39f40a6c85e4
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | Notify HP Management for inspection of drainage prior to backfill.
checkpoint-status |  |  | checkpoint | Book inspection with VBA for in-ground drainage. HP can sign off if inspector does not attend.
checkpoint-status |  |  | checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | ITR 011 Hot & Cold Rough In |  |  |  |  | Yes | ITR 011 Hot & Cold Rough In | 0fc91c20-8d60-4144-a67d-03df119e4b38
checkpoint-status |  |  | checkpoint | All works to be set our as per approved IFC drawings and penetrations to be installed to - IFC Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 & in accordance with specifications and requirements . Ensure isolation from authority main, fixtures, tapware and appliances while undertaking testing
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | Document |  |  |  |  | Yes | Document | 131f1c95-bdd5-47f4-b495-819e413e1b75
checkpoint-status |  |  | checkpoint | Attach document
checklist-flat |  |  | checklist | ITR 013 Water Meter |  |  |  |  | Yes | ITR 013 Water Meter | 230590a4-5164-4e87-9f86-2acbd0b981f3
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All meter work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | Ensure that all pipework to meters has been sealed and jointed, all capping adequately installed for testing.
checkpoint-status |  |  | checkpoint | Ensure all meters are sufficient supported and installed in correct location
checkpoint-status |  |  | checkpoint | Pass an amount of water in a container of known volume (bucket) and confirm the volume of water and meter reading are the same or within the required tolerances
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist-flat |  |  | checklist | ITR 007 Suspended Storm Drainage |  |  |  |  | Yes | ITR 007 Suspended Storm Drainage | 29dabbd9-2ef2-4269-bc3d-8b1188e2de2e
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
checkpoint-status |  |  | checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | ITR 009 Domestic Cold Water In Ground |  |  |  |  | Yes | ITR 009 Domestic Cold Water In Ground | 34191f19-1c6b-4972-8014-4ffd7cadd824
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC Drawings No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 & in accordance with specifications and requirements . Ensure isolation from authority main, fixtures, tapware and appliances while undertaking testing.
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist-flat |  |  | checklist | ITR 017 Thermostatic Mixing Valve Test Report |  |  |  |  | Yes | ITR 017 Thermostatic Mixing Valve Test Report | 3a0eb40b-8764-4951-9c09-d323f4332079
checkpoint-status |  |  | checkpoint | Thermostatic Mixing Valve Test
text | a5611f02-ea12-5d53-98ca-dc0891b079b3 |  | textbox | Licence No.
text | 6cba9033-7624-5009-8420-14c6d650a075 |  | textbox | Test kit serial No.
text | 2d6b332d-8c17-5a61-9e5e-252f2d95559b |  | textbox | Date test kit last certified:
text | 3b32788a-d5f3-5b7a-a2e4-6d2260e16ff6 |  | textbox | Place of certification
text | eed31752-d735-5887-a4ab-abfc8c2741af |  | textbox | Make
text | 973f66b9-b542-5540-b39f-8d275d8d721b |  | textbox | Model
text | 49b8ebca-b758-556c-9f1c-3ff3038c3acc |  | textbox | Location of valve
checkpoint-status |  |  | checkpoint | Shut down test
checkpoint-status |  |  | checkpoint | Flush / Clean filters
checkpoint-status |  |  | checkpoint | Static Test
boolean | 592843c7-c2af-58cc-8c27-fc98294e48c2 |  | tickbox | One outlet in use
text | 96b4108f-8886-576d-8c00-521a37529aa8 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Temp of warm water
text | 757f1857-315d-5ed2-816e-eb46c47e1616 |  | textbox | Fixture
text | d56e447b-4666-575d-8025-ff80256138fd |  | textbox | Pre Set Temp
checkpoint-status |  |  | checkpoint | Described Maintenance - Add comments / photos
text | 73d0facb-00bf-5022-881c-1b6d9d5a4977 |  | textbox | Parts & Materials Used
checkpoint-status |  |  | checkpoint | Testing signed off
checklist-flat |  |  | checklist | Non Conformance Report |  |  |  |  | Yes | Non Conformance Report | 7158861e-0ca5-4875-8526-d4ef680cdc75
checkpoint-status |  |  | checkpoint | Report completed
text | fb894c08-08c3-59df-acda-ba9ea5d3c48e |  | textbox | Short description
text | 1b163efe-c911-55a8-bd67-8f7572abc101 |  | textbox | NCN NO:
text | 4727f3ee-409f-5dfb-af29-c73cde02ba7b |  | textbox | Level / Area
text | 1234843e-c00f-50b4-9318-cebbfbd6c19e |  | textbox | Grid Coord
text | 54615f0a-ff84-5eaa-8060-7674914d39a0 |  | textbox | Responsibility
text | 1bcabcfd-6750-511d-9885-90cdeb4ab5c5 |  | textbox | Non Conformance Details
checkpoint-status |  |  | checkpoint | Method of disposition
text | b1d98aeb-4803-513e-9904-bce488cbe789 |  | textbox | Approval required from
checkpoint-status |  |  | checkpoint | Repair / Use as is
text | e821035a-c221-579e-baf8-6480ba9004f2 |  | textbox | Customer
checkpoint-status |  |  | checkpoint | Rework / Replace
text | 6c59e49e-0222-54be-acbc-dbb2336ebaa8 |  | textbox | Project Manager
checkpoint-status |  |  | checkpoint | Signed off by Highbury Plumbing Supervisor
checkpoint-status |  |  | checkpoint | Signed off by Scentre Group
checklist-flat |  |  | checklist | ITR 014 Sanitary Fit Off |  |  |  |  | Yes | ITR 014 Sanitary Fit Off | 72b7f30c-bf75-4029-907c-79e20da108de
checkpoint-status |  |  | checkpoint | All works to be set our as per approved Architectural Drawing No.
checkpoint-status |  |  | checkpoint | Inspect for product defects.
checkpoint-status |  |  | checkpoint | Install as per manufacturer's recommendations and requirements
checkpoint-status |  |  | checkpoint | All sanitary items to be tested in accordance to specifications and manufacturers requirements
checkpoint-status |  |  | checkpoint | Check for leaks
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist-flat |  |  | checklist | ITR 008 Suspended Greasy Drainage |  |  |  |  | Yes | ITR 008 Suspended Greasy Drainage | 82129726-6c52-4d64-a9c1-f07939e42432
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
checkpoint-status |  |  | checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | Internal Audit Checklist |  |  |  |  | Yes | Internal Audit Checklist | aa761ad2-feea-40c9-86b0-6946d34375b1
checkpoint-status |  |  | checkpoint | Drawing Register Current
checkpoint-status |  |  | checkpoint | Drawings as per Register
checkpoint-status |  |  | checkpoint | ITP Records
checkpoint-status |  |  | checkpoint | Material Specification
checkpoint-status |  |  | checkpoint | Sanitary Specification
checkpoint-status |  |  | checkpoint | Calibration records
checkpoint-status |  |  | checkpoint | Sample Register
text | 04586f43-fb90-5324-82a2-aba6f3f7546e |  | textbox | Comments
text | 0f6a327a-7373-5dde-8f97-68a3133f2a9a |  | textbox | Items of concern
text | b1336d76-dbed-553a-9733-008e200b3871 |  | textbox | Action required
text | b1c6b71c-49ae-589d-8005-61b9a7575436 |  | textbox | Future recommendations
checkpoint-status |  |  | checkpoint | Signed off by Highbury Plumbing Supervisor
checklist-flat |  |  | checklist | ITR 004 Greasy Drainage In Ground |  |  |  |  | Yes | ITR 004 Greasy Drainage In Ground | ab23276e-d74b-4d91-883b-9240d67a590c
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | ITR 012 Hot Water Service |  |  |  |  | Yes | ITR 012 Hot Water Service | af6317b7-52b9-4118-ac90-2166972636ec
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework to be tested in accordance to specifications and requirements namely 1500 kPA for 30 minutes
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist-flat |  |  | checklist | ITR 006 Suspended Sewer Drainage |  |  |  |  | Yes | ITR 006 Suspended Sewer Drainage | b6edf396-33db-40c7-a9ec-4efccc7a214c
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
checkpoint-status |  |  | checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | ITR 005 Fire Service |  |  |  |  | Yes | ITR 005 Fire Service | b8d3ffe8-6f48-4fe6-beaf-38356fd0dfaf
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & Standards or alternatively approved by CFA/MFB.
checkpoint-status |  |  | checkpoint | All pipework to be tested TO 1700 kPA in accordance to specifications &
checkpoint-status |  |  | checkpoint | requirements as per AS 2419 Hydrants & AS 2441 Hose Reels
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checkpoint-status |  |  | checkpoint | Prior to handover system must be inspected & certified in accordance to drawings, code, specification, dispensation, 129 report and FER
checklist-flat |  |  | checklist | ITR 016 Tempering Valve Test Report |  |  |  |  | Yes | ITR 016 Tempering Valve Test Report | c4193339-1689-4905-9996-54754f29c5ee
checkpoint-status |  |  | checkpoint | Tempering Valve Test
text | 142e855e-a5e8-521c-90a4-482db3875bc9 |  | textbox | Licence No.
text | 71f7c6b9-b995-5455-b96a-7638653f87ba |  | textbox | Test kit serial No.
text | 8e73a82f-befe-52a3-9e2e-492441bc2aea |  | textbox | Date test kit last certified:
text | d1d2d59a-8207-5616-885f-c943516887af |  | textbox | Place of certification
text | cf6f9be4-0172-52bf-a679-f265e46346a5 |  | textbox | Make
text | 21e74f2a-0617-55db-b0ef-d3438fc7be8a |  | textbox | Model
text | 4161c2bc-7970-5c69-befb-e3ee4574c80c |  | textbox | Location of valve
checkpoint-status |  |  | checkpoint | Flush / Clean filters
checkpoint-status |  |  | checkpoint | One outlet in use
text | 2fcf4b7a-cf2c-5519-a555-14882d65cd29 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Temp of warm water
text | 76472a04-c138-5a10-ba62-ef2eb5186bd1 |  | textbox | Fixture
text | 37573caf-2f68-51c7-aadb-a5d40324272e |  | textbox | Pre Set Temp
checkpoint-status |  |  | checkpoint | Described Maintenance - Add comments / photos
text | 86578768-aa3a-59d2-a76a-833f6880ec49 |  | textbox | Parts & Materials Used
checkpoint-status |  |  | checkpoint | Testing signed off
checklist-flat |  |  | checklist | ITR 015 Backflow Test Report |  |  |  |  | Yes | ITR 015 Backflow Test Report | cc0e8787-8c5c-480d-85f1-bddd2fa9cee2
checkpoint-status |  |  | checkpoint | Backflow Test Report Completed
text | 54137c33-e5e5-579e-b3df-ad0af1145c1e |  | textbox | Date of test
text | b499d820-47b5-5dca-bead-fe458ef56bce |  | textbox | Location of test
text | af284c44-ba85-5b38-aea4-ca233a3ecd41 |  | textbox | Licence No.
text | d476d340-a4ea-558f-85b7-274cfafb84dc |  | textbox | Test Kit Serial No.
text | ed1ed08d-e9d5-59bb-a8dd-41c69b4a46eb |  | textbox | Date test kit last certified
text | 9735c7c0-9e77-5293-97f4-524e229d037a |  | textbox | Place of certification
text | d8fc7e07-75e4-5a75-a53d-c92ac3a61cfa |  | textbox | Make of device
text | aa4ed4a5-8920-5c60-9221-e60888bea9e4 |  | textbox | Size (mm)
text | 54cf0de7-698d-5e69-a261-8918172f7f13 |  | textbox | Model
text | 054a7899-5c7f-5e1e-9cb7-75f49f5eab2f |  | textbox | Serial No.
label | 52f21cc1-040a-59a4-a50f-baac3bf4d910 |  | note | Initial Test Before Maintenance
checkpoint-status |  |  | checkpoint | Permission to shut of water
boolean | a9a649cb-5d76-5f0a-a9f1-ee0fb319482c |  | tickbox | Reduced Pressure Zone Device
boolean | 94d5029a-6a1a-5ea5-9e5b-b9268da9aff3 |  | tickbox | Double Check Valve (Columns 1 & 2)
boolean | 204f5a00-5f19-5a15-8758-a4d58a30977c |  | tickbox | Pressure Type
checkpoint-status |  |  | checkpoint | Check Valve No 1
boolean | 4f6a5fe7-9f49-51d9-8efd-936857e73138 |  | tickbox | Closed Tight
boolean | b0e222d6-0984-5510-994b-588be3c3e073 |  | tickbox | Leaked
text | f84f9556-0e0a-5581-bbb9-afee9e651f9e |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Check Valve No 2
boolean | 31d2e918-af6b-5311-9122-fb7e2350243b |  | tickbox | Closed Tight
boolean | 48e097dc-c936-5fe2-8da4-9a495342e843 |  | tickbox | Leaked
text | 432b4b0f-9a5f-52e0-a98a-ebe26f1f0206 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Relief Valve
boolean | cbbe27f0-c362-576f-9659-0b626c37dd08 |  | tickbox | Opened At
boolean | 4f72005d-6f20-5436-b533-851cf4f245a7 |  | tickbox | Not Opened
text | 2e59d3ea-4009-5267-8b00-628bb2ebba87 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Check Valve
boolean | 7cbc9f55-729b-5e3e-84c7-c1182e7233a3 |  | tickbox | Closed Tight
boolean | f5e0d4e3-88e0-5b06-8202-1b1c59084a6f |  | tickbox | Leaked
text | d59d7d0b-3902-5dda-9bc2-37cdb766efd7 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Air Inlet
boolean | dc3d7889-8d1a-5c3c-9851-44924ef8c0ad |  | tickbox | Opened At
boolean | c60c6efe-08db-5583-9307-ade49231aedc |  | tickbox | Not Opened
text | e1404bdb-176b-505a-8b44-8f2655656aa8 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Downstream Isolation Valve
boolean | d6a9bc36-dec3-56f2-9b38-5883cc67a853 |  | tickbox | Closed Tight
boolean | 0d94e64e-b27c-504e-a5b0-8b2d1272409f |  | tickbox | Leaked
text | b853fcf7-671e-5c1d-8e6e-9d5b9e2b7aea |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Comment / Take photos of any reasons for failure (NA if not required)
label | bd037dff-c23f-5ef9-b215-158e131cd5cc |  | note | Re-Test After
checkpoint-status |  |  | checkpoint | Permission to shut of water
boolean | b7c5ebaa-fe37-5085-83dd-0d27d00bc478 |  | tickbox | Reduced Pressure Zone Device
boolean | 6ceb1544-dba0-5ed8-a881-9d1444f152ac |  | tickbox | Double Check Valve (Columns 1 & 2)
boolean | 60f20cb5-333c-5ff8-9d29-f89640f3a183 |  | tickbox | Pressure Type
checkpoint-status |  |  | checkpoint | Check Valve No 1
boolean | 4322c734-6a3a-5419-8974-527deaed4dcc |  | tickbox | Closed Tight
boolean | 709e4e40-f7aa-55c9-b644-952c5ec958fb |  | tickbox | Leaked
text | 5a4b6bfd-5314-5ff0-8d1a-5da48e8023e8 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Check Valve No 2
boolean | ee9a3d1b-97c0-50d8-9c8a-128d1e7beba9 |  | tickbox | Closed Tight
boolean | e859600b-56a0-523b-ac1b-3ca3cd90a1fb |  | tickbox | Leaked
text | bcc91c1f-0991-5ad7-b687-608d50827a20 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Relief Valve
boolean | e2cdb4f6-07ee-5bea-89e1-1967772e9cea |  | tickbox | Opened At
boolean | d69a04dd-6999-5eeb-8bde-98d7ab52d37f |  | tickbox | Not Opened
text | 57ba55b7-5c10-5eab-97f3-a56a5f7aba4e |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Check Valve
boolean | 116b51f2-11c9-5c95-b391-ed3284ea369b |  | tickbox | Closed Tight
boolean | 48b7f998-2b25-5c90-a1f6-477377234668 |  | tickbox | Leaked
text | 7e076ba2-be6c-5d45-a00f-8fa7018e6053 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Air Inlet
boolean | febe789c-e7fd-56d9-bb16-45744cdcd9d8 |  | tickbox | Opened At
boolean | 243aaf86-206c-5b5d-9095-8d57cc9f431e |  | tickbox | Not Opened
text | 06a50b59-846f-53fc-bdb5-f1fb42ddbc9e |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Downstream Isolation Valve
boolean | 7f3eac16-08cf-5e98-a80a-603222f6a58c |  | tickbox | Closed Tight
boolean | a15de90b-3cb3-5785-8984-0fb75105e946 |  | tickbox | Leaked
text | 0ad31dcc-3a33-548d-917d-feba3670fd48 |  | textbox | kPa
checkpoint-status |  |  | checkpoint | Described Maintenance - Add comments / photos
text | 550599ba-7598-5eab-9df5-5536ff8f8ae9 |  | textbox | Parts & Materials Used
text | 93d83e47-3094-505b-b525-a6c61f224d02 |  | textbox | Water Meter Number
checkpoint-status |  |  | checkpoint | Testing signed off
checklist-flat |  |  | checklist | ITR 001 Set Out Penetrations |  |  |  |  | Yes | ITR 001 Set Out Penetrations | ddba49bd-13ae-4702-a257-485b79babd63
checkpoint-status |  |  | checkpoint | All works to be set our as per approved IFC drawings. Works set out to IFC Drawing No.
checkpoint-status |  |  | checkpoint | All penetrations and fire collars to be as per specifications or alternatively approved
checkpoint-status |  |  | checkpoint | Ensure fire collars are installed as per manufacturer’s instructions.
checkpoint-status |  |  | checkpoint | Tabs on cast in collar to be exposed.
checkpoint-status |  |  | checkpoint | Photos of collar end labelling referencing fire matrix if required
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist-flat |  |  | checklist | ITR 010 Gas Service |  |  |  |  | Yes | ITR 010 Gas Service | e9859ac0-88c1-4cd1-826d-c32847827fe4
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC Drawings No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS5601.1 or alternatively approved including rod sizes and clipping configurations and methods
checkpoint-status |  |  | checkpoint | All pipework to be tested in accordance with specifications and requirements & AS5601.1
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checkpoint-status |  |  | checkpoint | Prior to gas being turned on ESV must inspect and approved installation if required, including all builders work requirements IE signage, access panels, ventilation, riser shafts etc..
checkpoint-status |  |  | checkpoint | Must notify HP management on completion of works.
checklist-flat |  |  | checklist | ITR 003 Stormwater Drainage In Ground |  |  |  |  | Yes | ITR 003 Stormwater Drainage In Ground | f76729ec-0c7d-43b6-b278-38e232bd56e3
checkpoint-status |  |  | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint-status |  |  | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint-status |  |  | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint-status |  |  | checkpoint | All pits to be checked for correct invert levels & finished floor levels in accordance to specifications & requirements & IFC drawings.
checkpoint-status |  |  | checkpoint | Ensure correct locations of pits.
checkpoint-status |  |  | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications & requirements
checkpoint-status |  |  | checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
checkpoint-status |  |  | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.